## Therm118
Windmill Logger - THERMAL2.IMS
File opened at 00:00:01 Sun 12 Mar 2006
File closed at 00:00:01 Mon 13 Mar 2006
Date | Time | Boiler_Gas | Gas_MeterT | Boiler_Elec | Boiler_Flow | Boiler_Heat | Boiler_FlowT | Rads_In | Rads_Out | Boiler_Retur | Flue_Gas | Kitchen | Outside | Rain_Gauge | DHW_Coil_Hea | DHW_Coil_In | DHW_Cylinder | DHW_Coil_Out | DHW_Ambient | DHW_Flow | DHW_Heat | DHW_Out | DHW_In | OT min | t OT min | OT max | t OT max | T swing | Wtd._Meter_T | Delta T | Time Interval | T.H. Plus | W.H.L + | Total Heat | Water Ht. | Gain + | Gain + %
Days | Secs | cubic_feet | Celsius | kWh | litres | kWh | Celsius | Celsius | Celsius | Celsius | Celsius | Celsius | Celsius | events | kWh | Celsius | Celsius | Celsius | Celsius | litres | kWh | Celsius | Celsius | Celsius | hh:mm:ss | Celsius | hh:mm:ss | Kelvin | Celsius |  | Minutes | kW | kW | kW | kW | kW | %
2006-03-12 | 0:00 | 0 | 16.154 | 0 | 5 | 0 | 58.778 | 59.36 | 46.132 | 46.407 | 38.746 | 25.99 | -1.023 | 1 | 0 | 58.397 | 54.525 | 47.67 | 18.057 | 0 | 0 | 49.757 | 33.06 | [5 empty] | 0 | 12.371 | 0 | 6.8943 | 6.4782 | 0.34037 | 0 | 6.4782 | 93.9641
2006-03-12 | 0:01 | 0 | 16.119 | 0 | 5 | 0 | 58.746 | 59.397 | 46.214 | 46.445 | 38.526 | 25.906 | -1.159 | 1 | 0 | 58.274 | 54.492 | 47.658 | 18.047 | 0 | 0 | 49.724 | 32.979 | [5 empty] | 0 | 12.301 | 1 | 6.9339 | 6.5158 | 20.342 | 20 | -13.4842 | -194.4676
2006-03-12 | 0:02 | 0 | 16.094 | 0 | 4 | 1 | 58.701 | 59.306 | 46.055 | 46.466 | 38.478 | 25.931 | -1.11 | 1 | 0 | 58.297 | 54.448 | 47.658 | 18.022 | 0 | 0 | 49.677 | 32.979 | [5 empty] | 0 | 12.235 | 2 | 6.9196 | 6.5022 | 20.3414 | 20 | -13.4978 | -195.0646
2006-03-12 | 0:03 | 1 | 16.119 | 0 | 5 | 0 | 58.701 | 59.306 | 46.099 | 46.536 | 37.586 | 25.955 | -1.059 | 1 | 0 | 58.32 | 54.471 | 47.658 | 18.047 | 0 | 0 | 49.677 | 32.955 | [5 empty] | 16.119 | 12.165 | 0 | 6.9048 | 6.4881 | 20.3408 | 20 | -13.5119 | -195.6886
2006-03-12 | 0:04 | 0 | 16.094 | 0 | 4 | 0 | 58.632 | 59.306 | 46.032 | 46.603 | 37.985 | 26.002 | -1.11 | 1 | 0 | 58.32 | 54.492 | 47.591 | 18.047 | 0 | 0 | 49.701 | 33.027 | [5 empty] | 0 | 12.029 | 1 | 6.9196 | 6.5022 | 4.6271 | 4.2857 | 2.2165 | 32.0325
2006-03-12 | 0:05 | 0 | 16.119 | 1 | 5 | 0 | 58.589 | 59.262 | 46.146 | 46.582 | 37.727 | 25.98 | -1.059 | 1 | 0 | 58.32 | 54.492 | 47.591 | 18.047 | 0 | 0 | 49.701 | 32.979 | [5 empty] | 0 | 12.007 | 2 | 6.9048 | 6.4881 | 4.6265 | 4.2857 | 2.2024 | 31.897
2006-03-12 | 0:06 | 0 | 16.041 | 0 | 5 | 0 | 58.612 | 59.351 | 46.146 | 46.627 | 38.055 | 25.906 | -1.033 | 1 | 0 | 58.274 | 54.425 | 47.658 | 17.997 | 0 | 0 | 49.701 | 33.027 | [5 empty] | 0 | 11.985 | 3 | 6.8972 | 6.4809 | 4.6262 | 4.2857 | 2.1952 | 31.8277
2006-03-12 | 0:07 | 1 | 16.071 | 0 | 4 | 0 | 58.589 | 59.262 | 46.123 | 46.582 | 37.469 | 25.882 | -1.007 | 1 | 0 | 58.297 | 54.448 | 47.728 | 18.07 | 0 | 0 | 49.701 | 33.027 | [5 empty] | 16.071 | 12.007 | 4 | 6.8896 | 6.4737 | 4.6259 | 4.2857 | 2.188 | 31.7582
2006-03-12 | 0:08 | 0 | 16.094 | 0 | 5 | 0 | 58.612 | 59.194 | 46.123 | 46.627 | 37.373 | 25.835 | -0.981 | 1 | 0 | 58.297 | 54.448 | 47.658 | 18.07 | 0 | 0 | 49.701 | 33.027 | [5 empty] | 0 | 11.985 | 5 | 6.8821 | 6.4665 | 4.6256 | 4.2857 | 2.1808 | 31.6885
2006-03-12 | 0:09 | 0 | 16.119 | 0 | 4 | 0 | 58.589 | 59.262 | 46.214 | 46.582 | 37.49 | 25.86 | -0.958 | 1 | 0 | 58.32 | 54.425 | 47.658 | 18.047 | 0 | 0 | 49.701 | 33.003 | [5 empty] | 0 | 12.007 | 6 | 6.8754 | 6.4602 | 4.6253 | 4.2857 | 2.1745 | 31.6268
2006-03-12 | 0:10 | 0 | 16.041 | 0 | 5 | 0 | 58.584 | 59.189 | 46.141 | 46.575 | 37.885 | 25.853 | -1.038 | 1 | 0 | 58.247 | 54.373 | 47.609 | 18.017 | 0 | 0 | 49.649 | 32.998 | [5 empty] | 0 | 12.009 | 7 | 6.8987 | 6.4823 | 4.6263 | 4.2857 | 2.1966 | 31.841
2006-03-12 | 0:11 | 1 | 16.089 | 0 | 4 | 0 | 58.605 | 59.235 | 46.095 | 46.599 | 37.626 | 25.926 | -0.989 | 1 | 0 | 58.224 | 54.397 | 47.609 | 18.04 | 0 | 0 | 49.649 | 32.998 | [5 empty] | 16.089 | 12.006 | 8 | 6.8844 | 6.4688 | 4.6257 | 4.2857 | 2.183 | 31.71
2006-03-12 | 0:12 | 0 | 16.094 | 0 | 5 | 0 | 58.632 | 59.171 | 46.214 | 46.603 | 37.961 | 26.051 | -0.981 | 1 | 0 | 58.251 | 54.425 | 47.682 | 18.047 | 0 | 0 | 49.677 | 33.12 | [5 empty] | 0 | 12.029 | 9 | 6.8821 | 6.4665 | 4.6256 | 4.2857 | 2.1808 | 31.6885
2006-03-12 | 0:13 | 0 | 16.064 | 0 | 5 | 0 | 58.584 | 59.143 | 46.048 | 46.554 | 37.909 | 25.951 | -1.038 | 0 | 0 | 58.224 | 54.397 | 47.677 | 18.017 | 0 | 0 | 49.649 | 32.998 | [5 empty] | 0 | 12.03 | 10 | 6.8987 | 6.4823 | 4.6263 | 4.2857 | 2.1966 | 31.841
2006-03-12 | 0:14 | 0 | 16.064 | 0 | 4 | 0 | 58.584 | 59.212 | 46.071 | 46.622 | 38.26 | 26.117 | -1.012 | 2 | 0 | 58.269 | 54.397 | 47.563 | 17.992 | 0 | 0 | 49.649 | 32.95 | [5 empty] | 0 | 11.962 | 11 | 6.8911 | 6.4751 | 4.626 | 4.2857 | 2.1894 | 31.7715
2006-03-12 | 0:15 | 1 | 16.041 | 1 | 5 | 0 | 58.628 | 59.189 | 46.027 | 46.692 | 37.485 | 25.997 | -0.938 | 0 | 0 | 58.224 | 54.373 | 47.677 | 18.017 | 0 | 0 | 49.649 | 32.974 | [5 empty] | 16.041 | 11.936 | 12 | 6.8695 | 6.4546 | 4.6251 | 4.2857 | 2.1689 | 31.573
2006-03-12 | 0:16 | 0 | 16.064 | 0 | 5 | 1 | 58.584 | 59.189 | 46.186 | 46.599 | 37.885 | 26.117 | -0.912 | 1 | 0 | 58.247 | 54.373 | 47.586 | 18.017 | 0 | 0 | 49.626 | 32.95 | [5 empty] | 0 | 11.985 | 13 | 6.862 | 6.4474 | 4.6248 | 4.2857 | 2.1617 | 31.503
2006-03-12 | 0:17 | 0 | 16.089 | 0 | 4 | 0 | 58.584 | 59.235 | 46.186 | 46.622 | 37.626 | 26.191 | -0.938 | 1 | 0 | 58.269 | 54.397 | 47.609 | 18.04 | 0 | 0 | 49.649 | 32.974 | [5 empty] | 0 | 11.962 | 0 | 6.8695 | 6.4546 | 4.6251 | 4.2857 | 2.1689 | 31.573
2006-03-12 | 0:18 | 1 | 16.126 | 0 | 5 | 0 | 58.639 | 59.223 | 45.945 | 46.725 | 37.591 | 26.034 | -0.95 | 1 | 0 | 58.235 | 54.362 | 47.735 | 18.03 | 0 | 0 | 49.614 | 33.007 | [5 empty] | 16.126 | 11.914 | 1 | 6.873 | 6.458 | 4.6252 | 4.2857 | 2.1722 | 31.6053
2006-03-12 | 0:19 | 0 | 16.069 | 0 | 4 | 0 | 58.543 | 59.171 | 46.076 | 46.65 | 37.397 | 26.002 | -1.01 | 1 | 0 | 58.251 | 54.378 | 47.544 | 18.045 | 0 | 0 | 49.631 | 32.976 | [5 empty] | 0 | 11.893 | 2 | 6.8905 | 6.4746 | 4.6259 | 4.2857 | 2.1889 | 31.7662
2006-03-12 | 0:20 | 0 | 16.069 | 0 | 5 | 0 | 58.566 | 59.194 | 46.029 | 46.627 | 37.655 | 26.002 | -0.958 | 1 | 0 | 58.206 | 54.308 | 47.705 | 18.02 | 0 | 0 | 49.607 | 32.976 | [5 empty] | 0 | 11.939 | 3 | 6.8754 | 6.4602 | 4.6253 | 4.2857 | 2.1745 | 31.6268
2006-03-12 | 0:21 | 0 | 16.044 | 0 | 5 | 0 | 58.566 | 59.171 | 46.076 | 46.627 | 37.724 | 26.076 | -0.984 | 1 | 0 | 58.162 | 54.308 | 47.612 | 18.02 | 0 | 0 | 49.584 | 32.976 | [5 empty] | 0 | 11.939 | 4 | 6.8829 | 6.4674 | 4.6256 | 4.2857 | 2.1817 | 31.6966
2006-03-12 | 0:22 | 1 | 16.069 | 0 | 4 | 0 | 58.543 | 59.171 | 46.144 | 46.627 | 37.49 | 26.098 | -0.832 | 1 | 0 | 58.185 | 54.331 | 47.682 | 18.045 | 0 | 0 | 49.584 | 32.907 | [5 empty] | 16.069 | 11.916 | 5 | 6.8387 | 6.4253 | 4.6238 | 4.2857 | 2.1396 | 31.2865
2006-03-12 | 0:23 | 0 | 16.094 | 0 | 5 | 0 | 58.566 | 59.237 | 46.19 | 46.65 | 37.091 | 26.027 | -0.832 | 1 | 0 | 58.206 | 54.308 | 47.567 | 17.997 | 0 | 0 | 49.607 | 32.976 | [5 empty] | 0 | 11.916 | 6 | 6.8387 | 6.4253 | 4.6238 | 4.2857 | 2.1396 | 31.2865
2006-03-12 | 0:24 | 0 | 16.101 | 1 | 5 | 0 | 58.573 | 59.244 | 46.174 | 46.657 | 37.311 | 26.058 | -0.698 | 1 | 0 | 58.258 | 54.338 | 47.619 | 18.052 | 0 | 0 | 49.638 | 33.031 | [5 empty] | 0 | 11.916 | 7 | 6.7997 | 6.3882 | 4.6223 | 4.2857 | 2.1025 | 30.9206
2006-03-12 | 0:25 | 0 | 16.044 | 0 | 4 | 0 | 58.566 | 59.171 | 46.123 | 46.671 | 37.325 | 25.978 | -0.806 | 1 | 0 | 58.162 | 54.331 | 47.567 | 17.997 | 0 | 0 | 49.607 | 32.976 | [5 empty] | 0 | 11.895 | 8 | 6.8311 | 6.4181 | 4.6235 | 4.2857 | 2.1324 | 31.2158
2006-03-12 | 0:26 | 1 | 16.094 | 0 | 5 | 0 | 58.721 | 59.214 | 46.214 | 46.741 | 37.397 | 26.027 | -0.806 | 1 | 0 | 58.206 | 54.308 | 47.588 | 18.02 | 0 | 0 | 49.607 | 33.024 | [5 empty] | 16.094 | 11.98 | 9 | 6.8311 | 6.4181 | 4.6235 | 4.2857 | 2.1324 | 31.2158
2006-03-12 | 0:27 | 0 | 16.069 | 0 | 5 | 0 | 58.744 | 59.26 | 46.167 | 46.718 | 37.82 | 26.122 | -0.806 | 1 | 0 | 58.185 | 54.308 | 47.635 | 17.997 | 0 | 0 | 49.584 | 32.955 | [5 empty] | 0 | 12.026 | 10 | 6.8311 | 6.4181 | 4.6235 | 4.2857 | 2.1324 | 31.2158
2006-03-12 | 0:28 | 0 | 16.069 | 0 | 4 | 0 | 58.79 | 59.417 | 46.123 | 46.832 | 37.724 | 25.953 | -0.806 | 1 | 0 | 58.185 | 54.355 | 47.588 | 18.02 | 0 | 0 | 49.584 | 32.955 | [5 empty] | 0 | 11.958 | 11 | 6.8311 | 6.4181 | 4.6235 | 4.2857 | 2.1324 | 31.2158
2006-03-12 | 0:29 | 0 | 16.069 | 0 | 5 | 0 | 58.79 | 59.372 | 46.237 | 46.694 | 38.5 | 25.931 | -0.731 | 1 | 0 | 58.139 | 54.264 | 47.635 | 18.02 | 0 | 0 | 49.561 | 32.955 | [5 empty] | 0 | 12.096 | 12 | 6.8093 | 6.3973 | 4.6226 | 4.2857 | 2.1116 | 31.0111
2006-03-12 | 0:30 | 1 | 16.044 | 0 | 5 | 1 | 58.79 | 59.417 | 46.237 | 46.671 | 40.028 | 25.906 | -0.68 | 0 | 0 | 58.162 | 54.308 | 47.612 | 18.045 | 0 | 0 | 49.584 | 32.976 | [5 empty] | 16.044 | 12.119 | 13 | 6.7944 | 6.3832 | 4.622 | 4.2857 | 2.0975 | 30.8711
2006-03-12 | 0:31 | 0 | 16.038 | 0 | 4 | 0 | 58.74 | 59.367 | 46.162 | 46.736 | 39.624 | 25.924 | -0.737 | 1 | 0 | 58.135 | 54.236 | 47.63 | 18.04 | 0 | 0 | 49.579 | 32.926 | [5 empty] | 0 | 12.004 | 0 | 6.811 | 6.399 | 4.6227 | 4.2857 | 2.1133 | 31.0275
2006-03-12 | 0:32 | 0 | 16.094 | 0 | 5 | 0 | 58.79 | 59.44 | 46.305 | 46.764 | 39.37 | 25.953 | -0.706 | 1 | 0 | 58.228 | 54.264 | 47.567 | 17.997 | 0 | 0 | 49.631 | 32.976 | [5 empty] | 0 | 12.026 | 1 | 6.802 | 6.3904 | 4.6223 | 4.2857 | 2.1047 | 30.9425
2006-03-12 | 0:33 | 0 | 16.044 | 1 | 5 | 0 | 58.79 | 59.463 | 46.214 | 46.902 | 39.322 | 25.953 | -0.603 | 1 | 0 | 58.162 | 54.308 | 47.588 | 18.045 | 0 | 0 | 49.584 | 32.955 | [5 empty] | 0 | 11.888 | 2 | 6.772 | 6.3619 | 4.6211 | 4.2857 | 2.0762 | 30.6586
2006-03-12 | 0:34 | 1 | 16.044 | 0 | 4 | 0 | 58.856 | 59.395 | 46.281 | 46.879 | 39.418 | 25.953 | -0.603 | 1 | 0 | 58.162 | 54.287 | 47.588 | 18.07 | 0 | 0 | 49.607 | 32.976 | [5 empty] | 16.044 | 11.977 | 3 | 6.772 | 6.3619 | 4.6211 | 4.2857 | 2.0762 | 30.6586
2006-03-12 | 0:35 | 0 | 16.038 | 0 | 5 | 0 | 58.717 | 59.321 | 46.438 | 46.851 | 39.318 | 25.997 | -0.585 | 1 | 0 | 58.135 | 54.259 | 47.539 | 18.014 | 0 | 0 | 49.556 | 32.926 | [5 empty] | 0 | 11.866 | 4 | 6.7668 | 6.3569 | 4.6209 | 4.2857 | 2.0712 | 30.6087
2006-03-12 | 0:36 | 0 | 16.069 | 0 | 5 | 0 | 58.721 | 59.395 | 46.442 | 46.947 | 38.665 | 25.953 | -0.603 | 1 | 0 | 58.162 | 54.287 | 47.567 | 18.095 | 0 | 0 | 49.584 | 32.907 | [5 empty] | 0 | 11.774 | 5 | 6.772 | 6.3619 | 4.6211 | 4.2857 | 2.0762 | 30.6586
2006-03-12 | 0:37 | 1 | 16.013 | 0 | 4 | 0 | 58.717 | 59.39 | 46.277 | 47.012 | 38.777 | 25.877 | -0.659 | 1 | 0 | 58.112 | 54.259 | 47.516 | 18.014 | 0 | 0 | 49.556 | 32.902 | [5 empty] | 16.013 | 11.705 | 6 | 6.7883 | 6.3774 | 4.6218 | 4.2857 | 2.0917 | 30.8133
2006-03-12 | 0:38 | 0 | 16.013 | 0 | 5 | 0 | 58.714 | 59.321 | 46.298 | 46.942 | 38.705 | 25.973 | -0.634 | 1 | 0 | 58.133 | 54.257 | 47.537 | 18.04 | 0 | 0 | 49.533 | 32.878 | [5 empty] | 0 | 11.772 | 7 | 6.781 | 6.3705 | 4.6215 | 4.2857 | 2.0848 | 30.7443
2006-03-12 | 0:39 | 0 | 16.049 | 0 | 5 | 0 | 58.815 | 59.374 | 46.377 | 46.928 | 39.021 | 26.103 | -0.549 | 1 | 0 | 58.187 | 54.266 | 47.546 | 18.1 | 0 | 0 | 49.589 | 32.933 | [5 empty] | 0 | 11.887 | 8 | 6.7563 | 6.347 | 4.6205 | 4.2857 | 2.0612 | 30.5087
2006-03-12 | 0:40 | 0 | 16.013 | 0 | 4 | 0 | 58.714 | 59.342 | 46.277 | 47.147 | 38.705 | 25.997 | -0.585 | 1 | 0 | 58.133 | 54.187 | 47.56 | 17.989 | 0 | 0 | 49.577 | 32.9 | [5 empty] | 0 | 11.567 | 9 | 6.7668 | 6.3569 | 4.6209 | 4.2857 | 2.0712 | 30.6087
2006-03-12 | 0:41 | 1 | 16.013 | 0 | 5 | 0 | 58.692 | 59.342 | 46.253 | 46.849 | 38.636 | 25.997 | -0.507 | 1 | 0 | 58.133 | 54.21 | 47.605 | 18.065 | 0 | 0 | 49.556 | 32.924 | [5 empty] | 16.013 | 11.843 | 10 | 6.744 | 6.3353 | 4.62 | 4.2857 | 2.0496 | 30.3916
2006-03-12 | 0:42 | 0 | 16.038 | 1 | 5 | 0 | 58.692 | 59.41 | 46.435 | 47.077 | 39.858 | 26.117 | -0.507 | 1 | 0 | 58.11 | 54.163 | 47.651 | 17.989 | 0 | 0 | 49.533 | 32.878 | [5 empty] | 0 | 11.615 | 11 | 6.744 | 6.3353 | 4.62 | 4.2857 | 2.0496 | 30.3916
2006-03-12 | 0:43 | 0 | 16.038 | 0 | 4 | 0 | 58.714 | 59.365 | 46.277 | 46.849 | 39.621 | 26.068 | -0.659 | 1 | 0 | 58.133 | 54.187 | 47.537 | 18.014 | 0 | 0 | 49.556 | 32.854 | [5 empty] | 0 | 11.865 | 12 | 6.7883 | 6.3774 | 4.6218 | 4.2857 | 2.0917 | 30.8133
2006-03-12 | 0:44 | 0 | 15.991 | 0 | 5 | 1 | 58.737 | 59.365 | 46.321 | 46.757 | 40.116 | 25.899 | -0.608 | 1 | 0 | 58.087 | 54.163 | 47.537 | 18.04 | 0 | 0 | 49.556 | 32.878 | [5 empty] | 0 | 11.98 | 13 | 6.7734 | 6.3633 | 4.6212 | 4.2857 | 2.0776 | 30.6724
2006-03-12 | 0:45 | 1 | 16.038 | 0 | 5 | 0 | 58.895 | 59.388 | 46.253 | 46.757 | 39.246 | 25.877 | -0.634 | 0 | 0 | 58.087 | 54.142 | 47.584 | 18.04 | 0 | 0 | 49.533 | 32.878 | [5 empty] | 16.038 | 12.138 | 0 | 6.781 | 6.3705 | 4.6215 | 4.2857 | 2.0848 | 30.7443
2006-03-12 | 0:46 | 0 | 16.008 | 0 | 4 | 0 | 58.913 | 59.449 | 46.225 | 46.753 | 39.971 | 25.848 | -0.664 | 1 | 0 | 58.06 | 54.114 | 47.486 | 18.009 | 0 | 0 | 49.528 | 32.802 | [5 empty] | 0 | 12.16 | 1 | 6.7898 | 6.3788 | 4.9515 | 4.6154 | 1.7634 | 25.9716
2006-03-12 | 0:47 | 0 | 15.983 | 0 | 5 | 0 | 58.822 | 59.518 | 46.064 | 46.797 | 39.712 | 25.943 | -0.664 | 1 | 0 | 58.06 | 54.159 | 47.532 | 17.984 | 0 | 0 | 49.505 | 32.802 | [5 empty] | 0 | 12.025 | 2 | 6.7898 | 6.3788 | 4.9515 | 4.6154 | 1.7634 | 25.9716
2006-03-12 | 0:48 | 0 | 16.038 | 0 | 5 | 0 | 58.94 | 59.522 | 46.277 | 46.711 | 39.882 | 25.899 | -0.533 | 1 | 0 | 58.087 | 54.142 | 47.56 | 17.989 | 0 | 0 | 49.556 | 32.9 | [5 empty] | 0 | 12.229 | 3 | 6.7516 | 6.3425 | 4.95 | 4.6154 | 1.7271 | 25.5813
2006-03-12 | 0:49 | 1 | 16.038 | 0 | 4 | 0 | 58.984 | 59.545 | 46.253 | 46.804 | 39.504 | 25.877 | -0.559 | 1 | 0 | 58.087 | 54.119 | 47.537 | 18.014 | 0 | 0 | 49.533 | 32.854 | [5 empty] | 16.038 | 12.18 | 4 | 6.7592 | 6.3497 | 4.9503 | 4.6154 | 1.7343 | 25.6591
2006-03-12 | 0:50 | 0 | 16.064 | 0 | 5 | 0 | 58.918 | 59.545 | 46.277 | 46.711 | 38.612 | 26.068 | -0.608 | 1 | 0 | 58.11 | 54.163 | 47.514 | 18.04 | 0 | 0 | 49.533 | 32.854 | [5 empty] | 0 | 12.207 | 5 | 6.7734 | 6.3633 | 4.9509 | 4.6154 | 1.7479 | 25.8053
2006-03-12 | 0:51 | 0 | 16.008 | 1 | 5 | 0 | 58.822 | 59.449 | 46.27 | 46.683 | 39.43 | 25.943 | -0.616 | 1 | 0 | 58.06 | 54.135 | 47.556 | 18.009 | 0 | 0 | 49.505 | 32.802 | [5 empty] | 0 | 12.139 | 6 | 6.7758 | 6.3655 | 4.951 | 4.6154 | 1.7501 | 25.8291
2006-03-12 | 0:52 | 0 | 16.008 | 0 | 5 | 0 | 58.845 | 59.472 | 46.27 | 46.797 | 39.289 | 25.943 | -0.616 | 1 | 0 | 58.037 | 54.135 | 47.509 | 17.959 | 0 | 0 | 49.528 | 32.826 | [5 empty] | 0 | 12.048 | 7 | 6.7758 | 6.3655 | 4.951 | 4.6154 | 1.7501 | 25.8291
2006-03-12 | 0:53 | 1 | 16.008 | 0 | 4 | 0 | 58.89 | 59.406 | 46.386 | 46.706 | 39.052 | 26.014 | -0.564 | 1 | 0 | 58.082 | 54.114 | 47.486 | 18.009 | 0 | 0 | 49.528 | 32.826 | [5 empty] | 16.008 | 12.184 | 8 | 6.7606 | 6.3511 | 4.9503 | 4.6154 | 1.7357 | 25.6741
2006-03-12 | 0:54 | 0 | 15.983 | 0 | 5 | 0 | 58.822 | 59.495 | 46.386 | 46.844 | 39.265 | 25.919 | -0.538 | 1 | 0 | 58.037 | 54.091 | 47.486 | 18.009 | 0 | 0 | 49.505 | 32.85 | [5 empty] | 0 | 11.978 | 9 | 6.7531 | 6.3439 | 4.95 | 4.6154 | 1.7285 | 25.5963
2006-03-12 | 0:55 | 0 | 15.976 | 0 | 5 | 0 | 58.792 | 59.42 | 46.377 | 46.814 | 38.81 | 25.862 | -0.52 | 1 | 0 | 58.03 | 54.037 | 47.525 | 17.977 | 0 | 0 | 49.474 | 32.84 | [5 empty] | 0 | 11.978 | 10 | 6.7478 | 6.3389 | 4.9498 | 4.6154 | 1.7236 | 25.5423
2006-03-12 | 0:56 | 1 | 16.008 | 0 | 5 | 0 | 58.822 | 59.426 | 46.363 | 46.753 | 38.983 | 25.943 | -0.538 | 1 | 0 | 58.037 | 54.114 | 47.486 | 18.009 | 0 | 0 | 49.528 | 32.85 | [5 empty] | 16.008 | 12.069 | 11 | 6.7531 | 6.3439 | 4.95 | 4.6154 | 1.7285 | 25.5963
2006-03-12 | 0:57 | 0 | 16.033 | 0 | 4 | 1 | 58.822 | 59.449 | 46.34 | 46.706 | 39.313 | 25.968 | -0.538 | 0 | 0 | 58.06 | 54.091 | 47.509 | 18.009 | 0 | 0 | 49.505 | 32.826 | [5 empty] | 0 | 12.116 | 12 | 6.7531 | 6.3439 | 4.95 | 4.6154 | 1.7285 | 25.5963
2006-03-12 | 0:58 | 0 | 16.021 | 0 | 5 | 0 | 58.787 | 59.438 | 46.281 | 46.694 | 39.959 | 25.882 | -0.425 | 1 | 0 | 58.025 | 54.126 | 47.451 | 18.072 | 0 | 0 | 49.561 | 32.814 | [5 empty] | 0 | 12.093 | 0 | 6.7202 | 6.3126 | 4.9487 | 4.6154 | 1.6973 | 25.2562
2006-03-12 | 0:59 | 0 | 15.996 | 0 | 5 | 0 | 58.833 | 59.484 | 46.375 | 46.741 | 39.088 | 25.811 | -0.525 | 2 | 0 | 58.005 | 54.033 | 47.567 | 17.997 | 0 | 0 | 49.493 | 32.766 | [5 empty] | 0 | 12.092 | 1 | 6.7493 | 6.3403 | 4.6202 | 4.2857 | 2.0546 | 30.4419
2006-03-12 | 1:00 | 1 | 15.996 | 0 | 5 | 0 | 58.787 | 59.461 | 46.375 | 46.832 | 39.229 | 25.835 | -0.525 | 1 | 0 | 57.982 | 54.079 | 47.474 | 18.022 | 0 | 0 | 49.493 | 32.79 | [5 empty] | 15.996 | 11.955 | 2 | 6.7493 | 6.3403 | 4.6202 | 4.2857 | 2.0546 | 30.4419
2006-03-12 | 1:01 | 0 | 15.996 | 1 | 4 | 0 | 58.856 | 59.395 | 46.351 | 46.694 | 39.511 | 25.857 | -0.474 | 1 | 0 | 58.005 | 54.033 | 47.567 | 17.947 | 0 | 0 | 49.47 | 32.766 | [5 empty] | 0 | 12.162 | 3 | 6.7344 | 6.3262 | 4.6196 | 4.2857 | 2.0405 | 30.2994
2006-03-12 | 1:02 | 0 | 16.021 | 0 | 5 | 0 | 58.744 | 59.417 | 46.375 | 46.741 | 39.583 | 25.931 | -0.525 | 0 | 0 | 58.005 | 54.049 | 47.376 | 17.964 | 0 | 0 | 49.463 | 32.711 | [5 empty] | 0 | 12.003 | 4 | 6.7493 | 6.3403 | 4.6202 | 4.2857 | 2.0546 | 30.4419
2006-03-12 | 1:03 | 0 | 15.938 | 0 | 5 | 0 | 58.872 | 59.319 | 46.274 | 46.664 | 38.987 | 25.826 | -0.533 | 1 | 0 | 57.975 | 54.049 | 47.537 | 17.964 | 0 | 0 | 49.463 | 32.735 | [5 empty] | 0 | 12.208 | 5 | 6.7516 | 6.3425 | 4.6203 | 4.2857 | 2.0568 | 30.4641
2006-03-12 | 1:04 | 1 | 15.996 | 0 | 4 | 0 | 58.787 | 59.417 | 46.328 | 46.718 | 39.887 | 25.906 | -0.474 | 1 | 0 | 58.025 | 54.079 | 47.588 | 17.997 | 0 | 0 | 49.493 | 32.766 | [5 empty] | 15.996 | 12.069 | 6 | 6.7344 | 6.3262 | 4.6196 | 4.2857 | 2.0405 | 30.2994
2006-03-12 | 1:05 | 0 | 15.988 | 0 | 5 | 0 | 58.803 | 59.388 | 46.274 | 46.802 | 38.54 | 25.779 | -0.458 | 1 | 0 | 57.952 | 54.002 | 47.467 | 17.964 | 0 | 0 | 49.486 | 32.641 | [5 empty] | 0 | 12.001 | 7 | 6.7298 | 6.3218 | 4.6194 | 4.2857 | 2.0361 | 30.2545
2006-03-12 | 1:06 | 0 | 15.996 | 0 | 5 | 0 | 58.856 | 59.417 | 46.351 | 46.832 | 38.923 | 25.835 | -0.324 | 1 | 0 | 57.959 | 54.103 | 47.474 | 17.972 | 0 | 0 | 49.493 | 32.742 | [5 empty] | 0 | 12.024 | 8 | 6.6907 | 6.2847 | 4.6178 | 4.2857 | 1.999 | 29.8766
2006-03-12 | 1:07 | 1 | 15.963 | 0 | 5 | 0 | 58.781 | 59.454 | 46.321 | 46.734 | 38.657 | 25.924 | -0.407 | 1 | 0 | 57.952 | 54.002 | 47.42 | 18.014 | 0 | 0 | 49.325 | 32.618 | [5 empty] | 15.963 | 12.047 | 9 | 6.7149 | 6.3077 | 4.6188 | 4.2857 | 2.0219 | 30.1112
2006-03-12 | 1:08 | 0 | 16.021 | 0 | 4 | 0 | 58.833 | 59.438 | 46.396 | 46.741 | 38.995 | 25.906 | -0.399 | 1 | 0 | 58.005 | 53.988 | 47.406 | 17.997 | 0 | 0 | 49.309 | 32.673 | [5 empty] | 0 | 12.092 | 10 | 6.7126 | 6.3054 | 4.6187 | 4.2857 | 2.0197 | 30.0887
2006-03-12 | 1:09 | 0 | 15.988 | 0 | 5 | 0 | 58.758 | 59.408 | 46.389 | 46.711 | 38.189 | 25.754 | -0.332 | 1 | 0 | 57.952 | 53.935 | 47.42 | 17.964 | 0 | 0 | 49.234 | 32.665 | [5 empty] | 0 | 12.047 | 11 | 6.6931 | 6.2869 | 4.6179 | 4.2857 | 2.0012 | 29.8993
2006-03-12 | 1:10 | 0 | 15.963 | 1 | 5 | 0 | 58.781 | 59.365 | 46.435 | 46.711 | 38.447 | 25.875 | -0.358 | 1 | 0 | 57.952 | 53.958 | 47.49 | 18.014 | 0 | 0 | 49.187 | 32.689 | [5 empty] | 0 | 12.07 | 12 | 6.7006 | 6.2941 | 4.6182 | 4.2857 | 2.0084 | 29.9729
2006-03-12 | 1:11 | 1 | 15.971 | 0 | 4 | 1 | 58.767 | 59.484 | 46.419 | 46.741 | 38.196 | 25.906 | -0.247 | 1 | 0 | 57.959 | 54.033 | 47.497 | 17.997 | 0 | 0 | 49.126 | 32.72 | [5 empty] | 15.971 | 12.026 | 13 | 6.6683 | 6.2634 | 4.6169 | 4.2857 | 1.9777 | 29.6574
2006-03-12 | 1:12 | 0 | 15.988 | 0 | 5 | 0 | 58.758 | 59.388 | 46.298 | 46.825 | 37.741 | 25.803 | -0.255 | 1 | 0 | 57.929 | 53.935 | 47.444 | 17.939 | 0 | 0 | 49.096 | 32.689 | [5 empty] | 0 | 11.933 | 0 | 6.6707 | 6.2656 | 4.617 | 4.2857 | 1.9799 | 29.6803
2006-03-12 | 1:13 | 0 | 15.988 | 0 | 5 | 0 | 58.781 | 59.388 | 46.344 | 46.711 | 38.916 | 25.779 | -0.229 | 1 | 0 | 57.929 | 53.911 | 47.42 | 17.914 | 0 | 0 | 49.073 | 32.711 | [5 empty] | 0 | 12.07 | 1 | 6.6631 | 6.2584 | 4.9464 | 4.6154 | 1.643 | 24.6583
2006-03-12 | 1:14 | 0 | 15.988 | 0 | 4 | 0 | 58.849 | 59.365 | 46.389 | 46.711 | 38.822 | 25.779 | -0.154 | 1 | 0 | 57.907 | 53.888 | 47.444 | 17.914 | 0 | 0 | 49.049 | 32.689 | [5 empty] | 0 | 12.138 | 2 | 6.6412 | 6.2376 | 4.9455 | 4.6154 | 1.6222 | 24.4268
2006-03-12 | 1:15 | 1 | 15.963 | 0 | 5 | 0 | 58.826 | 59.477 | 46.412 | 46.849 | 38.729 | 25.85 | -0.229 | 1 | 0 | 57.907 | 53.958 | 47.42 | 17.964 | 0 | 0 | 49.049 | 32.689 | [5 empty] | 15.963 | 11.977 | 3 | 6.6631 | 6.2584 | 4.9464 | 4.6154 | 1.643 | 24.6583
2006-03-12 | 1:16 | 0 | 16.013 | 0 | 5 | 0 | 58.803 | 59.408 | 46.389 | 46.755 | 38.399 | 25.85 | -0.206 | 1 | 0 | 57.929 | 53.911 | 47.42 | 17.964 | 0 | 0 | 49.003 | 32.689 | [5 empty] | 0 | 12.048 | 4 | 6.6564 | 6.252 | 4.9461 | 4.6154 | 1.6366 | 24.5875
2006-03-12 | 1:17 | 0 | 16.013 | 0 | 5 | 0 | 58.737 | 59.408 | 46.251 | 46.893 | 38.306 | 25.875 | -0.281 | 1 | 0 | 57.907 | 53.911 | 47.353 | 17.989 | 0 | 0 | 48.982 | 32.711 | [5 empty] | 0 | 11.844 | 5 | 6.6782 | 6.2728 | 4.947 | 4.6154 | 1.6574 | 24.8179
2006-03-12 | 1:18 | 0 | 16.031 | 0 | 4 | 0 | 58.799 | 59.383 | 46.498 | 46.821 | 38.959 | 26.061 | -0.237 | 1 | 0 | 57.993 | 53.998 | 47.462 | 17.982 | 0 | 0 | 49.021 | 32.775 | [5 empty] | 0 | 11.978 | 6 | 6.6654 | 6.2606 | 4.9465 | 4.6154 | 1.6452 | 24.6829
2006-03-12 | 1:19 | 1 | 16.031 | 1 | 5 | 0 | 58.799 | 59.449 | 46.568 | 46.821 | 38.229 | 25.965 | -0.111 | 0 | 0 | 57.948 | 53.93 | 47.486 | 18.007 | 0 | 0 | 48.998 | 32.775 | [5 empty] | 16.031 | 11.978 | 7 | 6.6287 | 6.2257 | 4.945 | 4.6154 | 1.6103 | 24.2934
2006-03-12 | 1:20 | 0 | 16.026 | 0 | 5 | 0 | 58.794 | 59.399 | 46.608 | 46.792 | 37.753 | 25.985 | -0.219 | 1 | 0 | 57.898 | 53.902 | 47.434 | 17.952 | 0 | 0 | 48.947 | 32.725 | [5 empty] | 0 | 12.002 | 8 | 6.6602 | 6.2556 | 4.9463 | 4.6154 | 1.6402 | 24.6275
2006-03-12 | 1:21 | 0 | 16.056 | 0 | 5 | 0 | 58.845 | 59.518 | 46.545 | 46.867 | 39.028 | 25.99 | -0.188 | 1 | 0 | 57.948 | 53.883 | 47.416 | 17.982 | 0 | 0 | 48.998 | 32.706 | [5 empty] | 0 | 11.978 | 9 | 6.6511 | 6.247 | 4.9459 | 4.6154 | 1.6317 | 24.5319
2006-03-12 | 1:22 | 1 | 16.031 | 0 | 4 | 0 | 58.799 | 59.426 | 46.475 | 46.797 | 39.992 | 26.036 | -0.036 | 1 | 0 | 57.925 | 54.021 | 47.462 | 18.007 | 0 | 0 | 48.954 | 32.73 | [5 empty] | 16.031 | 12.002 | 10 | 6.6069 | 6.205 | 4.9441 | 4.6154 | 1.5896 | 24.0595
2006-03-12 | 1:23 | 0 | 16.031 | 0 | 5 | 0 | 58.845 | 59.426 | 46.384 | 46.821 | 39.428 | 26.014 | -0.111 | 1 | 0 | 57.925 | 53.93 | 47.462 | 18.007 | 0 | 0 | 48.93 | 32.754 | [5 empty] | 0 | 12.024 | 11 | 6.6287 | 6.2257 | 4.945 | 4.6154 | 1.6103 | 24.2934
2006-03-12 | 1:24 | 0 | 15.951 | 0 | 5 | 1 | 58.683 | 59.333 | 46.403 | 46.816 | 38.693 | 26.032 | -0.118 | 1 | 0 | 57.898 | 53.946 | 47.388 | 17.952 | 0 | 0 | 48.926 | 32.725 | [5 empty] | 0 | 11.867 | 12 | 6.6308 | 6.2277 | 4.9451 | 4.6154 | 1.6123 | 24.3151
2006-03-12 | 1:25 | 0 | 15.981 | 0 | 4 | 0 | 58.799 | 59.292 | 46.431 | 46.821 | 38.911 | 26.061 | -0.01 | 1 | 0 | 57.925 | 53.93 | 47.509 | 17.957 | 0 | 0 | 48.907 | 32.754 | [5 empty] | 0 | 11.978 | 0 | 6.5993 | 6.1978 | 4.9438 | 4.6154 | 1.5824 | 23.978
2006-03-12 | 1:26 | 1 | 15.976 | 0 | 5 | 0 | 58.571 | 59.287 | 46.47 | 46.839 | 38.531 | 26.007 | 0.111 | 1 | 0 | 57.898 | 53.879 | 47.364 | 17.952 | 0 | 0 | 48.902 | 32.725 | [5 empty] | 15.976 | 11.732 | 1 | 6.5641 | 6.1643 | 4.6127 | 4.2857 | 1.8786 | 28.6188
2006-03-12 | 1:27 | 0 | 15.981 | 0 | 5 | 0 | 58.53 | 59.271 | 46.431 | 46.912 | 38.37 | 26.061 | 0.142 | 1 | 0 | 57.925 | 53.974 | 47.462 | 17.982 | 0 | 0 | 48.998 | 32.706 | [5 empty] | 0 | 11.618 | 2 | 6.555 | 6.1557 | 4.6123 | 4.2857 | 1.87 | 28.5273
2006-03-12 | 1:28 | 0 | 16.001 | 1 | 5 | 0 | 58.413 | 59.244 | 46.447 | 46.816 | 37.425 | 26.056 | 0.338 | 1 | 0 | 57.898 | 53.879 | 47.388 | 17.952 | 0 | 0 | 48.902 | 32.701 | [5 empty] | 0 | 11.597 | 3 | 6.498 | 6.1014 | 4.61 | 4.2857 | 1.8157 | 27.943
2006-03-12 | 1:29 | 0 | 16.006 | 0 | 4 | 0 | 58.418 | 59.137 | 46.454 | 46.912 | 37.806 | 26.061 | 0.369 | 1 | 0 | 57.902 | 53.907 | 47.509 | 17.982 | 0 | 0 | 48.86 | 32.754 | [5 empty] | 0 | 11.506 | 4 | 6.4889 | 6.0929 | 4.6097 | 4.2857 | 1.8071 | 27.8496
2006-03-12 | 1:30 | 1 | 16.001 | 0 | 5 | 0 | 58.594 | 59.064 | 46.54 | 46.816 | 38.201 | 26.176 | 0.263 | 1 | 0 | 57.875 | 53.855 | 47.411 | 18.052 | 0 | 0 | 48.926 | 32.701 | [5 empty] | 16.001 | 11.778 | 5 | 6.5198 | 6.1222 | 4.6109 | 4.2857 | 1.8365 | 28.1678
2006-03-12 | 1:31 | 0 | 15.976 | 0 | 5 | 0 | 58.571 | 59.175 | 46.356 | 46.746 | 38.318 | 26.081 | 0.085 | 1 | 0 | 57.852 | 53.832 | 47.458 | 17.977 | 0 | 0 | 48.856 | 32.677 | [5 empty] | 0 | 11.825 | 6 | 6.5716 | 6.1715 | 4.613 | 4.2857 | 1.8858 | 28.6954
2006-03-12 | 1:32 | 0 | 16.001 | 0 | 5 | 0 | 58.616 | 59.198 | 46.356 | 46.701 | 38.366 | 26.007 | 0.059 | 0 | 0 | 57.852 | 53.855 | 47.434 | 17.977 | 0 | 0 | 48.832 | 32.701 | [5 empty] | 0 | 11.915 | 7 | 6.5792 | 6.1787 | 4.6133 | 4.2857 | 1.893 | 28.7717
2006-03-12 | 1:33 | 0 | 16.001 | 0 | 4 | 0 | 58.66 | 59.221 | 46.426 | 46.722 | 39.141 | 26.105 | 0.034 | 1 | 0 | 57.852 | 53.832 | 47.343 | 17.952 | 0 | 0 | 48.856 | 32.725 | [5 empty] | 0 | 11.938 | 8 | 6.5865 | 6.1856 | 4.6136 | 4.2857 | 1.8999 | 28.845
2006-03-12 | 1:34 | 1 | 16.001 | 0 | 5 | 0 | 58.637 | 59.287 | 46.312 | 46.701 | 38.389 | 25.985 | -0.041 | 1 | 0 | 57.831 | 53.832 | 47.411 | 18.002 | 0 | 0 | 48.832 | 32.725 | [5 empty] | 16.001 | 11.936 | 9 | 6.6083 | 6.2063 | 4.6145 | 4.2857 | 1.9206 | 29.0638
2006-03-12 | 1:35 | 0 | 16.001 | 0 | 5 | 0 | 58.594 | 59.244 | 46.403 | 46.655 | 38.318 | 26.007 | -0.015 | 1 | 0 | 57.898 | 53.855 | 47.364 | 18.027 | 0 | 0 | 48.832 | 32.701 | [5 empty] | 0 | 11.939 | 10 | 6.6008 | 6.1992 | 4.6142 | 4.2857 | 1.9134 | 28.9881
2006-03-12 | 1:36 | 0 | 16.001 | 0 | 5 | 0 | 58.616 | 59.221 | 46.379 | 46.816 | 38.858 | 25.911 | -0.067 | 1 | 0 | 57.831 | 53.879 | 47.343 | 17.952 | 0 | 0 | 48.811 | 32.677 | [5 empty] | 0 | 11.8 | 11 | 6.6159 | 6.2135 | 4.6148 | 4.2857 | 1.9278 | 29.1393
2006-03-12 | 1:37 | 0 | 15.976 | 1 | 4 | 0 | 58.637 | 59.264 | 46.403 | 46.678 | 38.059 | 25.985 | -0.067 | 1 | 0 | 57.831 | 53.808 | 47.343 | 17.952 | 0 | 0 | 48.832 | 32.701 | [5 empty] | 0 | 11.959 | 12 | 6.6159 | 6.2135 | 4.6148 | 4.2857 | 1.9278 | 29.1393
2006-03-12 | 1:38 | 1 | 15.983 | 0 | 5 | 1 | 58.644 | 59.271 | 46.295 | 46.844 | 38.655 | 25.919 | -0.085 | 1 | 0 | 57.815 | 53.792 | 47.441 | 17.959 | 0 | 0 | 48.863 | 32.685 | [5 empty] | 15.983 | 11.8 | 13 | 6.6212 | 6.2185 | 4.615 | 4.2857 | 1.9328 | 29.1915
2006-03-12 | 1:39 | 0 | 15.903 | 0 | 5 | 0 | 58.594 | 59.29 | 46.335 | 46.748 | 38.578 | 25.96 | 0.062 | 1 | 0 | 57.788 | 53.743 | 47.276 | 17.954 | 0 | 0 | 48.788 | 32.656 | [5 empty] | 0 | 11.846 | 0 | 6.5783 | 6.1778 | 4.6133 | 4.2857 | 1.8921 | 28.7629
2006-03-12 | 1:40 | 0 | 15.983 | 0 | 5 | 0 | 58.6 | 59.205 | 46.295 | 46.729 | 38.655 | 25.943 | 0.093 | 1 | 0 | 57.815 | 53.792 | 47.371 | 17.959 | 0 | 0 | 48.795 | 32.73 | [5 empty] | 0 | 11.871 | 1 | 6.5693 | 6.1693 | 4.6129 | 4.2857 | 1.8835 | 28.6718
2006-03-12 | 1:41 | 1 | 15.983 | 0 | 4 | 0 | 58.6 | 59.205 | 46.34 | 46.706 | 38.418 | 25.99 | -0.16 | 1 | 0 | 57.815 | 53.771 | 47.418 | 17.984 | 0 | 0 | 48.748 | 32.73 | [5 empty] | 15.983 | 11.894 | 2 | 6.643 | 6.2393 | 4.6159 | 4.2857 | 1.9536 | 29.408
2006-03-12 | 1:42 | 0 | 15.903 | 0 | 5 | 0 | 58.55 | 59.201 | 46.312 | 46.839 | 38.014 | 25.889 | 0.01 | 1 | 0 | 57.765 | 53.764 | 47.276 | 17.979 | 0 | 0 | 48.744 | 32.749 | [5 empty] | 0 | 11.711 | 3 | 6.5935 | 6.1922 | 4.6139 | 4.2857 | 1.9065 | 28.9152
2006-03-12 | 1:43 | 0 | 16.008 | 0 | 5 | 0 | 58.6 | 59.205 | 46.454 | 46.706 | 38.232 | 26.039 | 0.041 | 1 | 0 | 57.815 | 53.771 | 47.395 | 17.984 | 0 | 0 | 48.748 | 32.778 | [5 empty] | 0 | 11.894 | 4 | 6.5845 | 6.1837 | 4.6135 | 4.2857 | 1.8979 | 28.8245
2006-03-12 | 1:44 | 0 | 15.928 | 0 | 5 | 0 | 58.482 | 59.109 | 46.449 | 46.795 | 37.78 | 25.889 | 0.062 | 1 | 0 | 57.742 | 53.696 | 47.276 | 17.979 | 0 | 0 | 48.744 | 32.797 | [5 empty] | 0 | 11.687 | 5 | 6.5783 | 6.1778 | 4.6133 | 4.2857 | 1.8921 | 28.7629
2006-03-12 | 1:45 | 1 | 15.953 | 0 | 4 | 0 | 58.459 | 59.086 | 46.335 | 46.863 | 38.389 | 25.914 | 0.062 | 1 | 0 | 57.742 | 53.743 | 47.252 | 17.929 | 0 | 0 | 48.744 | 32.749 | [5 empty] | 15.953 | 11.596 | 6 | 6.5783 | 6.1778 | 4.6133 | 4.2857 | 1.8921 | 28.7629
2006-03-12 | 1:46 | 0 | 15.983 | 1 | 5 | 0 | 58.578 | 59.114 | 46.41 | 46.823 | 38.232 | 25.894 | 0.193 | 1 | 0 | 57.793 | 53.748 | 47.441 | 17.984 | 0 | 0 | 48.839 | 32.778 | [5 empty] | 0 | 11.755 | 7 | 6.5402 | 6.1416 | 4.6117 | 4.2857 | 1.8559 | 28.3763
2006-03-12 | 1:47 | 0 | 15.953 | 0 | 5 | 0 | 58.616 | 59.109 | 46.288 | 46.771 | 39.071 | 25.84 | 0.265 | 1 | 0 | 57.742 | 53.673 | 47.276 | 17.954 | 0 | 0 | 48.744 | 32.749 | [5 empty] | 0 | 11.845 | 8 | 6.5192 | 6.1216 | 4.6109 | 4.2857 | 1.8359 | 28.1618
2006-03-12 | 1:48 | 0 | 15.928 | 0 | 5 | 0 | 58.594 | 59.132 | 46.288 | 46.701 | 39.684 | 25.96 | 0.113 | 1 | 0 | 57.742 | 53.764 | 47.276 | 17.954 | 0 | 0 | 48.744 | 32.725 | [5 empty] | 0 | 11.893 | 9 | 6.5635 | 6.1637 | 4.6127 | 4.2857 | 1.878 | 28.6129
2006-03-12 | 1:49 | 1 | 15.928 | 0 | 5 | 0 | 58.416 | 59.155 | 46.312 | 46.725 | 38.978 | 25.889 | 0.088 | 0 | 0 | 57.742 | 53.72 | 47.276 | 17.979 | 0 | 0 | 48.744 | 32.701 | [5 empty] | 15.928 | 11.691 | 10 | 6.5708 | 6.1706 | 4.613 | 4.2857 | 1.8849 | 28.6865
2006-03-12 | 1:50 | 0 | 15.953 | 0 | 4 | 0 | 58.281 | 58.975 | 46.403 | 46.657 | 38.885 | 25.914 | 0.137 | 1 | 0 | 57.742 | 53.696 | 47.252 | 17.929 | 0 | 0 | 48.72 | 32.725 | [5 empty] | 0 | 11.624 | 11 | 6.5565 | 6.1571 | 4.6124 | 4.2857 | 1.8714 | 28.5421
2006-03-12 | 1:51 | 0 | 15.928 | 0 | 5 | 0 | 58.505 | 58.975 | 46.288 | 46.701 | 39.167 | 25.865 | 0.188 | 1 | 0 | 57.742 | 53.696 | 47.229 | 17.979 | 0 | 0 | 48.697 | 32.725 | [5 empty] | 0 | 11.804 | 12 | 6.5417 | 6.143 | 4.6118 | 4.2857 | 1.8572 | 28.3911
2006-03-12 | 1:52 | 0 | 15.983 | 0 | 5 | 1 | 58.644 | 59.182 | 46.386 | 46.753 | 38.772 | 26.014 | 0.168 | 1 | 0 | 57.724 | 53.724 | 47.348 | 18.009 | 0 | 0 | 48.702 | 32.73 | [5 empty] | 0 | 11.891 | 13 | 6.5475 | 6.1485 | 4.612 | 4.2857 | 1.8628 | 28.4504
2006-03-12 | 1:53 | 1 | 15.953 | 0 | 5 | 0 | 58.482 | 59.109 | 46.335 | 46.657 | 38.837 | 25.96 | 0.088 | 1 | 0 | 57.72 | 53.673 | 47.252 | 17.954 | 0 | 0 | 48.697 | 32.68 | [5 empty] | 15.953 | 11.825 | 0 | 6.5708 | 6.1706 | 4.613 | 4.2857 | 1.8849 | 28.6865
2006-03-12 | 1:54 | 0 | 15.928 | 0 | 4 | 0 | 58.482 | 59.086 | 46.358 | 46.701 | 38.789 | 26.058 | 0.088 | 1 | 0 | 57.72 | 53.696 | 47.252 | 17.979 | 0 | 0 | 48.697 | 32.68 | [5 empty] | 0 | 11.781 | 1 | 6.5708 | 6.1706 | 4.9426 | 4.6154 | 1.5553 | 23.6693
2006-03-12 | 1:55 | 0 | 15.953 | 0 | 5 | 0 | 58.55 | 59.155 | 46.312 | 46.634 | 38.978 | 25.938 | 0.01 | 1 | 0 | 57.742 | 53.65 | 47.206 | 17.904 | 0 | 0 | 48.697 | 32.725 | [5 empty] | 0 | 11.916 | 2 | 6.5935 | 6.1922 | 4.9436 | 4.6154 | 1.5768 | 23.9152
2006-03-12 | 1:56 | 1 | 15.953 | 1 | 5 | 0 | 58.594 | 59.132 | 46.382 | 46.634 | 38.954 | 25.914 | 0.113 | 1 | 0 | 57.72 | 53.696 | 47.276 | 17.904 | 0 | 0 | 48.72 | 32.68 | [5 empty] | 15.953 | 11.96 | 3 | 6.5635 | 6.1637 | 4.9424 | 4.6154 | 1.5483 | 23.5901
2006-03-12 | 1:57 | 0 | 15.928 | 0 | 5 | 0 | 58.527 | 59.221 | 46.312 | 46.701 | 39.684 | 25.914 | 0.036 | 1 | 0 | 57.697 | 53.65 | 47.32 | 17.954 | 0 | 0 | 48.65 | 32.656 | [5 empty] | 0 | 11.826 | 4 | 6.5859 | 6.185 | 4.9433 | 4.6154 | 1.5697 | 23.8334
2006-03-12 | 1:58 | 0 | 15.938 | 0 | 5 | 0 | 58.557 | 59.162 | 46.526 | 46.641 | 39.339 | 25.97 | 0.047 | 1 | 0 | 57.66 | 53.636 | 47.236 | 17.914 | 0 | 0 | 48.66 | 32.639 | [5 empty] | 0 | 11.916 | 5 | 6.5827 | 6.182 | 4.9431 | 4.6154 | 1.5666 | 23.7988
2006-03-12 | 1:59 | 0 | 15.908 | 0 | 4 | 0 | 58.461 | 59.134 | 46.314 | 46.68 | 39.38 | 26.012 | -0.033 | 1 | 0 | 57.676 | 53.629 | 47.164 | 17.934 | 0 | 0 | 48.653 | 32.589 | [5 empty] | 0 | 11.781 | 6 | 6.606 | 6.2041 | 4.9441 | 4.6154 | 1.5887 | 24.0501
2006-03-12 | 2:00 | 1 | 15.883 | 0 | 5 | 0 | 58.53 | 59.112 | 46.291 | 46.75 | 38.911 | 25.747 | 0.016 | 1 | 0 | 57.676 | 53.652 | 47.301 | 17.934 | 0 | 0 | 48.653 | 32.61 | [5 empty] | 15.883 | 11.78 | 7 | 6.5917 | 6.1906 | 4.9435 | 4.6154 | 1.5752 | 23.8964
2006-03-12 | 2:01 | 0 | 15.938 | 0 | 5 | 0 | 58.511 | 59.139 | 46.319 | 46.825 | 39.222 | 25.85 | 0.124 | 1 | 0 | 57.66 | 53.542 | 47.259 | 17.914 | 0 | 0 | 48.681 | 32.618 | [5 empty] | 0 | 11.686 | 8 | 6.5603 | 6.1607 | 4.9422 | 4.6154 | 1.5453 | 23.5552
2006-03-12 | 2:02 | 0 | 15.933 | 0 | 5 | 0 | 58.507 | 59.201 | 46.27 | 46.727 | 38.464 | 25.845 | -0.059 | 1 | 0 | 57.633 | 53.538 | 47.208 | 17.884 | 0 | 0 | 48.676 | 32.589 | [5 empty] | 0 | 11.78 | 9 | 6.6136 | 6.2113 | 4.9444 | 4.6154 | 1.5959 | 24.1314
2006-03-12 | 2:03 | 0 | 15.908 | 0 | 5 | 0 | 58.53 | 59.112 | 46.27 | 46.842 | 38.815 | 25.845 | 0.016 | 1 | 0 | 57.653 | 53.584 | 47.278 | 17.909 | 0 | 0 | 48.632 | 32.658 | [5 empty] | 0 | 11.688 | 10 | 6.5917 | 6.1906 | 4.9435 | 4.6154 | 1.5752 | 23.8964
2006-03-12 | 2:04 | 1 | 15.908 | 0 | 4 | 0 | 58.438 | 59.18 | 46.384 | 46.727 | 39.569 | 25.772 | 0.016 | 1 | 0 | 57.633 | 53.584 | 47.164 | 17.934 | 0 | 0 | 48.632 | 32.634 | [5 empty] | 15.908 | 11.711 | 11 | 6.5917 | 6.1906 | 4.9435 | 4.6154 | 1.5752 | 23.8964
2006-03-12 | 2:05 | 0 | 15.938 | 1 | 5 | 1 | 58.534 | 59.093 | 46.503 | 46.846 | 39.361 | 25.897 | 0.124 | 1 | 0 | 57.637 | 53.612 | 47.168 | 17.964 | 0 | 0 | 48.636 | 32.687 | [5 empty] | 0 | 11.688 | 12 | 6.5603 | 6.1607 | 4.9422 | 4.6154 | 1.5453 | 23.5552
2006-03-12 | 2:06 | 0 | 15.883 | 0 | 5 | 0 | 58.461 | 59.18 | 46.223 | 46.704 | 39.473 | 25.916 | -0.059 | 1 | 0 | 57.633 | 53.561 | 47.117 | 17.909 | 0 | 0 | 48.632 | 32.658 | [5 empty] | 0 | 11.757 | 0 | 6.6136 | 6.2113 | 4.9444 | 4.6154 | 1.5959 | 24.1314
2006-03-12 | 2:07 | 0 | 15.913 | 0 | 5 | 0 | 58.489 | 59.139 | 46.319 | 46.846 | 39.621 | 25.85 | -0.054 | 0 | 0 | 57.615 | 53.636 | 47.215 | 17.939 | 0 | 0 | 48.636 | 32.687 | [5 empty] | 0 | 11.643 | 1 | 6.6121 | 6.2099 | 4.6147 | 4.2857 | 1.9242 | 29.1016
2006-03-12 | 2:08 | 1 | 16.006 | 0 | 5 | 0 | 58.461 | 59.112 | 46.405 | 46.704 | 39.452 | 25.867 | -0.033 | 1 | 0 | 57.61 | 53.561 | 47.117 | 17.909 | 0 | 0 | 48.608 | 32.682 | [5 empty] | 16.006 | 11.757 | 2 | 6.606 | 6.2041 | 4.6144 | 4.2857 | 1.9184 | 29.0405
2006-03-12 | 2:09 | 0 | 15.933 | 0 | 5 | 0 | 58.55 | 59.066 | 46.522 | 46.704 | 39.31 | 25.965 | -0.085 | 1 | 0 | 57.61 | 53.538 | 47.14 | 17.909 | 0 | 0 | 48.608 | 32.706 | [5 empty] | 0 | 11.846 | 3 | 6.6212 | 6.2185 | 4.615 | 4.2857 | 1.9328 | 29.1915
2006-03-12 | 2:10 | 0 | 15.938 | 0 | 4 | 0 | 58.489 | 59.139 | 46.342 | 46.825 | 38.492 | 25.897 | -0.105 | 1 | 0 | 57.637 | 53.589 | 47.168 | 17.914 | 0 | 0 | 48.66 | 32.663 | [5 empty] | 0 | 11.664 | 4 | 6.627 | 6.2241 | 4.6153 | 4.2857 | 1.9383 | 29.2494
2006-03-12 | 2:11 | 0 | 15.908 | 0 | 5 | 0 | 58.461 | 59.045 | 46.337 | 46.774 | 38.229 | 25.845 | -0.059 | 1 | 0 | 57.61 | 53.584 | 47.164 | 17.934 | 0 | 0 | 48.608 | 32.658 | [5 empty] | 0 | 11.687 | 5 | 6.6136 | 6.2113 | 4.6147 | 4.2857 | 1.9256 | 29.1161
2006-03-12 | 2:12 | 1 | 15.933 | 0 | 5 | 0 | 58.416 | 59.023 | 46.522 | 46.75 | 38.629 | 26.012 | -0.211 | 1 | 0 | 57.633 | 53.514 | 47.164 | 17.859 | 0 | 0 | 48.723 | 32.682 | [5 empty] | 15.933 | 11.666 | 6 | 6.6578 | 6.2534 | 4.6165 | 4.2857 | 1.9677 | 29.5545
2006-03-12 | 2:13 | 0 | 15.908 | 0 | 5 | 0 | 58.327 | 59 | 46.361 | 46.75 | 38.253 | 25.892 | -0.162 | 1 | 0 | 57.633 | 53.538 | 47.094 | 17.909 | 0 | 0 | 48.608 | 32.682 | [5 empty] | 0 | 11.577 | 7 | 6.6436 | 6.2398 | 4.6159 | 4.2857 | 1.9541 | 29.4138
2006-03-12 | 2:14 | 0 | 15.908 | 1 | 5 | 0 | 58.283 | 58.911 | 46.314 | 46.75 | 37.875 | 25.845 | -0.136 | 1 | 0 | 57.61 | 53.514 | 47.117 | 17.884 | 0 | 0 | 48.608 | 32.73 | [5 empty] | 0 | 11.533 | 8 | 6.636 | 6.2326 | 4.6156 | 4.2857 | 1.9469 | 29.3389
2006-03-12 | 2:15 | 1 | 15.883 | 0 | 4 | 0 | 58.304 | 58.865 | 46.337 | 46.865 | 38.064 | 25.916 | -0.263 | 1 | 0 | 57.564 | 53.514 | 47.164 | 17.909 | 0 | 0 | 48.585 | 32.706 | [5 empty] | 15.883 | 11.439 | 9 | 6.673 | 6.2678 | 4.6171 | 4.2857 | 1.9821 | 29.7031
2006-03-12 | 2:16 | 0 | 15.908 | 0 | 5 | 0 | 58.416 | 59.023 | 46.291 | 46.797 | 39.428 | 25.821 | -0.288 | 1 | 0 | 57.61 | 53.514 | 47.094 | 17.909 | 0 | 0 | 48.632 | 32.634 | [5 empty] | 0 | 11.619 | 10 | 6.6803 | 6.2747 | 4.6174 | 4.2857 | 1.989 | 29.7743
2006-03-12 | 2:17 | 0 | 15.908 | 0 | 5 | 0 | 58.372 | 59.045 | 46.337 | 46.727 | 39.779 | 25.892 | -0.288 | 1 | 0 | 57.61 | 53.47 | 47.117 | 17.884 | 0 | 0 | 48.608 | 32.658 | [5 empty] | 0 | 11.645 | 11 | 6.6803 | 6.2747 | 4.6174 | 4.2857 | 1.989 | 29.7743
2006-03-12 | 2:18 | 0 | 15.868 | 0 | 5 | 0 | 58.336 | 58.918 | 46.414 | 46.713 | 39.789 | 25.951 | -0.33 | 1 | 0 | 57.528 | 53.477 | 47.126 | 17.844 | 0 | 0 | 48.571 | 32.668 | [5 empty] | 0 | 11.623 | 12 | 6.6925 | 6.2863 | 4.6179 | 4.2857 | 2.0006 | 29.8936
2006-03-12 | 2:19 | 1 | 15.868 | 0 | 5 | 1 | 58.381 | 58.94 | 46.3 | 46.69 | 39.179 | 25.806 | -0.33 | 1 | 0 | 57.528 | 53.477 | 47.194 | 17.942 | 0 | 0 | 48.571 | 32.644 | [5 empty] | 15.868 | 11.691 | 13 | 6.6925 | 6.2863 | 4.6179 | 4.2857 | 2.0006 | 29.8936
2006-03-12 | 2:20 | 0 | 15.893 | 0 | 5 | 0 | 58.47 | 58.963 | 46.277 | 46.783 | 39.696 | 25.83 | -0.353 | 1 | 0 | 57.528 | 53.409 | 47.173 | 17.894 | 0 | 0 | 48.548 | 32.62 | [5 empty] | 0 | 11.687 | 0 | 6.6992 | 6.2927 | 4.6182 | 4.2857 | 2.007 | 29.9588
2006-03-12 | 2:21 | 0 | 15.868 | 0 | 4 | 0 | 58.425 | 59.032 | 46.232 | 46.645 | 39.507 | 26.046 | -0.353 | 1 | 0 | 57.528 | 53.547 | 47.217 | 17.919 | 0 | 0 | 48.524 | 32.62 | [5 empty] | 0 | 11.78 | 1 | 6.6992 | 6.2927 | 4.6182 | 4.2857 | 2.007 | 29.9588
2006-03-12 | 2:22 | 0 | 15.868 | 0 | 5 | 0 | 58.313 | 58.986 | 46.414 | 46.666 | 39.2 | 25.902 | -0.379 | 1 | 0 | 57.505 | 53.409 | 47.056 | 17.894 | 0 | 0 | 48.571 | 32.596 | [5 empty] | 0 | 11.647 | 2 | 6.7068 | 6.2999 | 4.6185 | 4.2857 | 2.0142 | 30.0323
2006-03-12 | 2:23 | 1 | 15.893 | 1 | 5 | 0 | 58.29 | 58.918 | 46.323 | 46.804 | 39.107 | 25.902 | -0.404 | 1 | 0 | 57.505 | 53.456 | 47.08 | 17.894 | 0 | 0 | 48.571 | 32.62 | [5 empty] | 15.893 | 11.486 | 3 | 6.714 | 6.3068 | 4.6188 | 4.2857 | 2.0211 | 30.1028
2006-03-12 | 2:24 | 0 | 15.893 | 0 | 5 | 0 | 58.336 | 58.918 | 46.414 | 46.804 | 39.648 | 25.975 | -0.456 | 0 | 0 | 57.528 | 53.456 | 47.056 | 17.894 | 0 | 0 | 48.571 | 32.62 | [5 empty] | 0 | 11.532 | 4 | 6.7292 | 6.3212 | 4.6194 | 4.2857 | 2.0355 | 30.2489
2006-03-12 | 2:25 | 0 | 15.893 | 0 | 5 | 0 | 58.224 | 58.874 | 46.645 | 46.989 | 39.6 | 25.926 | -0.353 | 1 | 0 | 57.528 | 53.433 | 47.035 | 17.869 | 0 | 0 | 48.571 | 32.596 | [5 empty] | 0 | 11.235 | 5 | 6.6992 | 6.2927 | 4.6182 | 4.2857 | 2.007 | 29.9588
2006-03-12 | 2:26 | 0 | 15.868 | 0 | 5 | 0 | 58.178 | 58.785 | 46.69 | 47.012 | 39.459 | 26.12 | -0.33 | 1 | 0 | 57.505 | 53.386 | 47.056 | 17.869 | 0 | 0 | 48.548 | 32.596 | [5 empty] | 0 | 11.166 | 6 | 6.6925 | 6.2863 | 4.6179 | 4.2857 | 2.0006 | 29.8936
2006-03-12 | 2:27 | 1 | 15.835 | 0 | 5 | 0 | 58.105 | 58.733 | 46.522 | 47.073 | 38.911 | 26.014 | -0.363 | 1 | 0 | 57.455 | 53.356 | 47.119 | 17.861 | 0 | 0 | 48.541 | 32.613 | [5 empty] | 15.835 | 11.032 | 7 | 6.7021 | 6.2955 | 4.6183 | 4.2857 | 2.0098 | 29.9871
2006-03-12 | 2:28 | 0 | 15.86 | 0 | 5 | 0 | 58.26 | 58.756 | 46.522 | 47.187 | 38.607 | 25.919 | -0.286 | 1 | 0 | 57.455 | 53.356 | 47.164 | 17.861 | 0 | 0 | 48.517 | 32.613 | [5 empty] | 0 | 11.073 | 8 | 6.6797 | 6.2742 | 4.6174 | 4.2857 | 1.9885 | 29.7686
2006-03-12 | 2:29 | 0 | 15.81 | 0 | 5 | 0 | 58.082 | 58.776 | 46.477 | 47.164 | 39.076 | 26.088 | -0.26 | 1 | 0 | 57.455 | 53.426 | 47.143 | 17.861 | 0 | 0 | 48.494 | 32.565 | [5 empty] | 0 | 10.918 | 9 | 6.6721 | 6.267 | 4.6171 | 4.2857 | 1.9813 | 29.6946
2006-03-12 | 2:30 | 0 | 15.835 | 0 | 5 | 0 | 58.105 | 58.733 | 46.592 | 47.049 | 39.028 | 26.063 | -0.26 | 1 | 0 | 57.498 | 53.288 | 47.026 | 17.811 | 0 | 0 | 48.494 | 32.52 | [5 empty] | 0 | 11.056 | 10 | 6.6721 | 6.267 | 4.6171 | 4.2857 | 1.9813 | 29.6946
2006-03-12 | 2:31 | 1 | 15.835 | 0 | 5 | 0 | 58.126 | 58.733 | 46.545 | 46.982 | 38.911 | 26.014 | -0.363 | 1 | 0 | 57.455 | 53.309 | 47.026 | 17.886 | 0 | 0 | 48.494 | 32.495 | [5 empty] | 15.835 | 11.144 | 11 | 6.7021 | 6.2955 | 4.6183 | 4.2857 | 2.0098 | 29.9871
2006-03-12 | 2:32 | 0 | 15.835 | 1 | 5 | 0 | 58.126 | 58.733 | 46.683 | 47.073 | 38.607 | 25.919 | -0.312 | 1 | 0 | 57.409 | 53.309 | 47.049 | 17.909 | 0 | 0 | 48.471 | 32.52 | [5 empty] | 0 | 11.053 | 12 | 6.6873 | 6.2814 | 4.6177 | 4.2857 | 1.9956 | 29.8426
2006-03-12 | 2:33 | 0 | 15.81 | 0 | 5 | 1 | 58.126 | 58.756 | 46.592 | 47.026 | 38.607 | 25.965 | -0.286 | 1 | 0 | 57.432 | 53.309 | 47.164 | 17.836 | 0 | 0 | 48.45 | 32.565 | [5 empty] | 0 | 11.1 | 13 | 6.6797 | 6.2742 | 4.6174 | 4.2857 | 1.9885 | 29.7686
2006-03-12 | 2:34 | 1 | 15.835 | 0 | 5 | 0 | 58.171 | 58.756 | 46.636 | 46.982 | 38.535 | 26.063 | -0.211 | 0 | 0 | 57.455 | 53.332 | 47.026 | 17.861 | 0 | 0 | 48.494 | 32.543 | [5 empty] | 15.835 | 11.189 | 0 | 6.6578 | 6.2534 | 4.6165 | 4.2857 | 1.9677 | 29.5545
2006-03-12 | 2:35 | 0 | 15.81 | 0 | 5 | 0 | 58.082 | 58.867 | 46.568 | 47.119 | 39.052 | 26.039 | -0.234 | 1 | 0 | 57.409 | 53.265 | 47.119 | 17.886 | 0 | 0 | 48.541 | 32.495 | [5 empty] | 0 | 10.963 | 1 | 6.6645 | 6.2598 | 4.6168 | 4.2857 | 1.9741 | 29.6203
2006-03-12 | 2:36 | 0 | 15.86 | 0 | 5 | 0 | 58.105 | 58.776 | 46.498 | 47.049 | 39.052 | 26.088 | -0.185 | 1 | 0 | 57.409 | 53.265 | 47.143 | 17.861 | 0 | 0 | 48.517 | 32.565 | [5 empty] | 0 | 11.056 | 2 | 6.6503 | 6.2462 | 4.6162 | 4.2857 | 1.9605 | 29.4799
2006-03-12 | 2:37 | 0 | 15.835 | 0 | 5 | 0 | 58.082 | 58.71 | 46.454 | 47.026 | 38.77 | 26.039 | -0.16 | 1 | 0 | 57.409 | 53.402 | 47.096 | 17.959 | 0 | 0 | 48.471 | 32.589 | [5 empty] | 0 | 11.056 | 3 | 6.643 | 6.2393 | 4.6159 | 4.2857 | 1.9536 | 29.408
2006-03-12 | 2:38 | 1 | 15.86 | 0 | 5 | 0 | 58.107 | 58.735 | 46.501 | 47.052 | 38.796 | 25.943 | -0.16 | 1 | 0 | 57.411 | 53.311 | 47.075 | 17.911 | 0 | 0 | 48.496 | 32.661 | [5 empty] | 15.86 | 11.055 | 4 | 6.643 | 6.2393 | 4.6159 | 4.2857 | 1.9536 | 29.408
2006-03-12 | 2:39 | 0 | 15.855 | 0 | 5 | 0 | 58.123 | 58.73 | 46.519 | 46.933 | 38.672 | 25.938 | -0.09 | 1 | 0 | 57.43 | 53.353 | 47.047 | 17.904 | 0 | 0 | 48.492 | 32.632 | [5 empty] | 0 | 11.19 | 5 | 6.6226 | 6.2199 | 4.6151 | 4.2857 | 1.9342 | 29.206
2006-03-12 | 2:40 | 0 | 15.86 | 0 | 5 | 0 | 58.128 | 58.712 | 46.547 | 47.005 | 38.796 | 25.992 | -0.059 | 1 | 0 | 57.411 | 53.335 | 47.098 | 17.911 | 0 | 0 | 48.496 | 32.637 | [5 empty] | 0 | 11.123 | 6 | 6.6136 | 6.2113 | 4.6147 | 4.2857 | 1.9256 | 29.1161
2006-03-12 | 2:41 | 0 | 15.86 | 1 | 5 | 0 | 58.151 | 58.689 | 46.547 | 47.005 | 38.796 | 26.088 | -0.085 | 1 | 0 | 57.411 | 53.358 | 47.028 | 17.934 | 0 | 0 | 48.52 | 32.615 | [5 empty] | 0 | 11.146 | 7 | 6.6212 | 6.2185 | 4.615 | 4.2857 | 1.9328 | 29.1915
2006-03-12 | 2:42 | 1 | 15.885 | 0 | 5 | 0 | 58.107 | 58.735 | 46.501 | 46.961 | 38.913 | 26.014 | -0.134 | 1 | 0 | 57.434 | 53.311 | 47.005 | 17.911 | 0 | 0 | 48.473 | 32.591 | [5 empty] | 15.885 | 11.146 | 8 | 6.6354 | 6.2321 | 4.6156 | 4.2857 | 1.9464 | 29.3331
2006-03-12 | 2:43 | 0 | 15.86 | 0 | 5 | 0 | 58.151 | 58.712 | 46.477 | 47.005 | 38.607 | 26.039 | -0.211 | 1 | 0 | 57.434 | 53.311 | 47.052 | 17.911 | 0 | 0 | 48.52 | 32.615 | [5 empty] | 0 | 11.146 | 9 | 6.6578 | 6.2534 | 4.6165 | 4.2857 | 1.9677 | 29.5545
2006-03-12 | 2:44 | 0 | 15.86 | 0 | 5 | 0 | 58.151 | 58.778 | 46.501 | 47.005 | 38.865 | 25.919 | -0.185 | 1 | 0 | 57.411 | 53.311 | 47.028 | 17.911 | 0 | 0 | 48.473 | 32.615 | [5 empty] | 0 | 11.146 | 10 | 6.6503 | 6.2462 | 4.6162 | 4.2857 | 1.9605 | 29.4799
2006-03-12 | 2:45 | 0 | 15.83 | 0 | 5 | 0 | 58.123 | 58.708 | 46.496 | 46.977 | 39.284 | 25.938 | -0.242 | 1 | 0 | 57.407 | 53.353 | 47.115 | 18.004 | 0 | 0 | 48.468 | 32.632 | [5 empty] | 0 | 11.146 | 11 | 6.6669 | 6.262 | 4.6169 | 4.2857 | 1.9763 | 29.6432
2006-03-12 | 2:46 | 1 | 15.81 | 0 | 5 | 0 | 58.085 | 58.758 | 46.477 | 47.005 | 38.748 | 26.039 | -0.286 | 1 | 0 | 57.457 | 53.29 | 46.982 | 17.934 | 0 | 0 | 48.473 | 32.567 | [5 empty] | 15.81 | 11.08 | 12 | 6.6797 | 6.2742 | 4.6174 | 4.2857 | 1.9885 | 29.7686
2006-03-12 | 2:47 | 0 | 15.805 | 0 | 5 | 1 | 58.169 | 58.662 | 46.449 | 46.977 | 39.401 | 25.914 | -0.291 | 1 | 0 | 57.407 | 53.307 | 47.161 | 17.881 | 0 | 0 | 48.445 | 32.608 | [5 empty] | 0 | 11.192 | 13 | 6.6811 | 6.2755 | 4.6174 | 4.2857 | 1.9898 | 29.7829
2006-03-12 | 2:48 | 0 | 15.83 | 0 | 5 | 0 | 58.08 | 58.73 | 46.587 | 46.954 | 39.095 | 25.963 | -0.394 | 1 | 0 | 57.361 | 53.262 | 46.933 | 17.881 | 0 | 0 | 48.445 | 32.563 | [5 empty] | 0 | 11.126 | 0 | 6.7111 | 6.3041 | 4.6187 | 4.2857 | 2.0183 | 30.0746
2006-03-12 | 2:49 | 0 | 15.855 | 0 | 5 | 0 | 58.101 | 58.73 | 46.564 | 46.954 | 39.942 | 25.938 | -0.394 | 0 | 0 | 57.407 | 53.239 | 46.977 | 17.831 | 0 | 0 | 48.422 | 32.563 | [5 empty] | 0 | 11.147 | 1 | 6.7111 | 6.3041 | 4.9483 | 4.6154 | 1.6887 | 25.1623
2006-03-12 | 2:50 | 1 | 15.885 | 1 | 5 | 0 | 58.219 | 58.824 | 46.547 | 46.937 | 39.124 | 25.894 | -0.363 | 1 | 0 | 57.411 | 53.267 | 47.143 | 17.886 | 0 | 0 | 48.473 | 32.567 | [5 empty] | 15.885 | 11.282 | 2 | 6.7021 | 6.2955 | 4.948 | 4.6154 | 1.6801 | 25.0681
2006-03-12 | 2:51 | 0 | 15.83 | 0 | 5 | 0 | 58.101 | 58.774 | 46.543 | 46.933 | 39.236 | 26.009 | -0.342 | 1 | 0 | 57.384 | 53.239 | 46.954 | 17.856 | 0 | 0 | 48.422 | 32.539 | [5 empty] | 0 | 11.168 | 3 | 6.696 | 6.2897 | 4.9477 | 4.6154 | 1.6743 | 25.0042
2006-03-12 | 2:52 | 0 | 15.805 | 0 | 5 | 0 | 58.215 | 58.774 | 46.449 | 46.933 | 38.531 | 25.963 | -0.291 | 1 | 0 | 57.361 | 53.262 | 47 | 17.831 | 0 | 0 | 48.422 | 32.563 | [5 empty] | 0 | 11.282 | 4 | 6.6811 | 6.2755 | 4.9471 | 4.6154 | 1.6602 | 24.8485
2006-03-12 | 2:53 | 1 | 15.855 | 0 | 5 | 0 | 58.192 | 58.797 | 46.564 | 46.954 | 38.65 | 25.865 | -0.368 | 1 | 0 | 57.316 | 53.262 | 47.07 | 18.004 | 0 | 0 | 48.422 | 32.586 | [5 empty] | 15.855 | 11.238 | 5 | 6.7036 | 6.2969 | 4.948 | 4.6154 | 1.6815 | 25.0833
2006-03-12 | 2:54 | 0 | 15.86 | 0 | 5 | 0 | 58.242 | 58.824 | 46.524 | 47.005 | 39.007 | 26.063 | -0.337 | 1 | 0 | 57.389 | 53.244 | 46.937 | 17.911 | 0 | 0 | 48.429 | 32.591 | [5 empty] | 0 | 11.237 | 6 | 6.6945 | 6.2883 | 4.9477 | 4.6154 | 1.6729 | 24.989
2006-03-12 | 2:55 | 0 | 15.83 | 0 | 5 | 0 | 58.327 | 58.819 | 46.564 | 46.909 | 39.071 | 25.84 | -0.317 | 1 | 0 | 57.338 | 53.192 | 47.07 | 17.904 | 0 | 0 | 48.401 | 32.608 | [5 empty] | 0 | 11.418 | 7 | 6.6887 | 6.2827 | 4.9474 | 4.6154 | 1.6674 | 24.928
2006-03-12 | 2:56 | 0 | 15.835 | 0 | 5 | 0 | 58.331 | 59.048 | 46.571 | 46.937 | 38.631 | 25.943 | -0.26 | 1 | 0 | 57.343 | 53.267 | 46.982 | 17.911 | 0 | 0 | 48.45 | 32.567 | [5 empty] | 0 | 11.394 | 8 | 6.6721 | 6.267 | 4.9468 | 4.6154 | 1.6516 | 24.7535
2006-03-12 | 2:57 | 1 | 15.83 | 0 | 5 | 0 | 58.281 | 58.863 | 46.496 | 47.024 | 39.002 | 25.794 | -0.19 | 1 | 0 | 57.338 | 53.216 | 47.024 | 17.881 | 0 | 0 | 48.401 | 32.563 | [5 empty] | 15.83 | 11.257 | 9 | 6.6517 | 6.2476 | 4.9459 | 4.6154 | 1.6322 | 24.5381
2006-03-12 | 2:58 | 0 | 15.857 | 0 | 5 | 0 | 58.327 | 58.886 | 46.519 | 46.909 | 39.284 | 25.818 | -0.188 | 1 | 0 | 57.361 | 53.192 | 46.956 | 17.859 | 0 | 0 | 48.424 | 32.61 | [5 empty] | 0 | 11.418 | 10 | 6.6511 | 6.247 | 4.9459 | 4.6154 | 1.6317 | 24.5319
2006-03-12 | 2:59 | 0 | 15.857 | 1 | 5 | 0 | 58.416 | 58.931 | 46.566 | 46.956 | 39.473 | 25.818 | -0.237 | 1 | 0 | 57.318 | 53.192 | 47.024 | 17.859 | 0 | 0 | 48.377 | 32.61 | [5 empty] | 0 | 11.46 | 11 | 6.6654 | 6.2606 | 4.9465 | 4.6154 | 1.6452 | 24.6829
2006-03-12 | 3:00 | 0 | 15.832 | 0 | 5 | 1 | 58.416 | 59.02 | 46.589 | 46.979 | 39.284 | 25.916 | -0.314 | 1 | 0 | 57.361 | 53.239 | 46.933 | 17.906 | 0 | 0 | 48.401 | 32.61 | [5 empty] | 0 | 11.437 | 12 | 6.6878 | 6.2819 | 4.9474 | 4.6154 | 1.6665 | 24.9188
2006-03-12 | 3:01 | 1 | 15.832 | 0 | 5 | 0 | 58.416 | 58.954 | 46.589 | 47.003 | 39.449 | 25.867 | -0.136 | 1 | 0 | 57.318 | 53.216 | 47.003 | 17.884 | 0 | 0 | 48.354 | 32.61 | [5 empty] | 15.832 | 11.413 | 0 | 6.636 | 6.2326 | 4.9453 | 4.6154 | 1.6173 | 24.371
2006-03-12 | 3:02 | 0 | 15.775 | 0 | 5 | 0 | 58.185 | 58.902 | 46.445 | 46.949 | 39.889 | 25.786 | -0.296 | 1 | 0 | 57.265 | 53.139 | 47.017 | 17.801 | 0 | 0 | 48.347 | 32.485 | [5 empty] | 0 | 11.236 | 1 | 6.6826 | 6.2769 | 4.6175 | 4.2857 | 1.9912 | 29.7971
2006-03-12 | 3:03 | 0 | 15.825 | 0 | 5 | 0 | 58.274 | 58.856 | 46.536 | 46.993 | 39.559 | 25.715 | -0.17 | 1 | 0 | 57.265 | 53.118 | 46.926 | 17.851 | 0 | 0 | 48.324 | 32.51 | [5 empty] | 0 | 11.281 | 2 | 6.6459 | 6.2421 | 4.616 | 4.2857 | 1.9563 | 29.4368
2006-03-12 | 3:04 | 0 | 15.825 | 0 | 5 | 0 | 58.274 | 58.902 | 46.697 | 46.993 | 39.466 | 25.835 | -0.018 | 1 | 0 | 57.265 | 53.139 | 46.856 | 17.874 | 0 | 0 | 48.37 | 32.531 | [5 empty] | 0 | 11.281 | 3 | 6.6016 | 6.2 | 4.6142 | 4.2857 | 1.9143 | 28.9969
2006-03-12 | 3:05 | 1 | 15.807 | 0 | 5 | 0 | 58.258 | 58.886 | 46.634 | 47.094 | 39.731 | 25.818 | 0.041 | 1 | 0 | 57.295 | 53.169 | 47.094 | 17.833 | 0 | 0 | 48.377 | 32.541 | [5 empty] | 15.807 | 11.164 | 4 | 6.5845 | 6.1837 | 4.6135 | 4.2857 | 1.8979 | 28.8245
2006-03-12 | 3:06 | 0 | 15.825 | 0 | 5 | 0 | 58.297 | 58.813 | 46.718 | 47.017 | 39.112 | 25.909 | 0.008 | 0 | 0 | 57.309 | 53.094 | 46.879 | 17.826 | 0 | 0 | 48.37 | 32.436 | [5 empty] | 0 | 11.28 | 5 | 6.5941 | 6.1928 | 4.6139 | 4.2857 | 1.9071 | 28.921
2006-03-12 | 3:07 | 0 | 15.825 | 0 | 6 | 0 | 58.185 | 58.835 | 46.65 | 47.063 | 39.184 | 25.811 | 0.031 | 2 | 0 | 57.288 | 53.118 | 47.017 | 17.851 | 0 | 0 | 48.347 | 32.365 | [5 empty] | 0 | 11.122 | 6 | 6.5874 | 6.1864 | 4.6136 | 4.2857 | 1.9007 | 28.8538
2006-03-12 | 3:08 | 1 | 15.832 | 1 | 5 | 0 | 58.08 | 58.797 | 46.519 | 47.047 | 38.815 | 26.036 | 0.065 | 0 | 0 | 57.318 | 53.169 | 46.933 | 17.884 | 0 | 0 | 48.331 | 32.348 | [5 empty] | 15.832 | 11.033 | 7 | 6.5775 | 6.177 | 4.6132 | 4.2857 | 1.8913 | 28.7541
2006-03-12 | 3:09 | 0 | 15.832 | 0 | 5 | 0 | 58.169 | 58.774 | 46.543 | 47.094 | 38.98 | 25.843 | 0.142 | 1 | 0 | 57.295 | 53.125 | 47.047 | 17.884 | 0 | 0 | 48.263 | 32.468 | [5 empty] | 0 | 11.075 | 8 | 6.555 | 6.1557 | 4.6123 | 4.2857 | 1.87 | 28.5273
2006-03-12 | 3:10 | 0 | 15.775 | 0 | 5 | 0 | 58.028 | 58.701 | 46.489 | 46.972 | 38.502 | 25.86 | 0.134 | 1 | 0 | 57.243 | 53.139 | 46.993 | 17.851 | 0 | 0 | 48.163 | 32.316 | [5 empty] | 0 | 11.056 | 9 | 6.5574 | 6.1579 | 4.6124 | 4.2857 | 1.8722 | 28.551
2006-03-12 | 3:11 | 0 | 15.807 | 0 | 5 | 0 | 57.916 | 58.587 | 46.603 | 46.993 | 38.736 | 25.811 | 0.235 | 1 | 0 | 57.265 | 53.094 | 46.926 | 17.826 | 0 | 0 | 48.118 | 32.316 | [5 empty] | 0 | 10.923 | 10 | 6.528 | 6.13 | 4.6112 | 4.2857 | 1.8442 | 28.2513
2006-03-12 | 3:12 | 1 | 15.807 | 0 | 5 | 0 | 57.989 | 58.573 | 46.634 | 47.138 | 39.167 | 25.843 | 0.217 | 1 | 0 | 57.272 | 53.101 | 46.979 | 17.884 | 0 | 0 | 48.125 | 32.372 | [5 empty] | 15.807 | 10.851 | 11 | 6.5332 | 6.1349 | 4.6115 | 4.2857 | 1.8492 | 28.3049
2006-03-12 | 3:13 | 0 | 15.775 | 0 | 5 | 0 | 57.916 | 58.632 | 46.58 | 47.201 | 38.901 | 25.811 | 0.16 | 1 | 0 | 57.22 | 53.071 | 46.902 | 17.851 | 0 | 0 | 47.981 | 32.291 | [5 empty] | 0 | 10.715 | 12 | 6.5498 | 6.1507 | 4.6121 | 4.2857 | 1.865 | 28.4741
2006-03-12 | 3:14 | 0 | 15.8 | 0 | 5 | 1 | 57.893 | 58.609 | 46.627 | 47.087 | 38.454 | 25.764 | 0.235 | 1 | 0 | 57.265 | 53.071 | 46.856 | 17.826 | 0 | 0 | 47.934 | 32.341 | [5 empty] | 0 | 10.806 | 13 | 6.528 | 6.13 | 4.6112 | 4.2857 | 1.8442 | 28.2513
2006-03-12 | 3:15 | 0 | 15.8 | 0 | 5 | 0 | 57.916 | 58.52 | 46.673 | 47.063 | 38.526 | 25.909 | 0.209 | 1 | 0 | 57.265 | 53.071 | 46.902 | 17.826 | 0 | 0 | 47.934 | 32.365 | [5 empty] | 0 | 10.853 | 0 | 6.5355 | 6.1371 | 4.6115 | 4.2857 | 1.8514 | 28.3287
2006-03-12 | 3:16 | 1 | 15.825 | 0 | 5 | 0 | 57.893 | 58.52 | 46.536 | 47.063 | 38.784 | 25.786 | 0.235 | 1 | 0 | 57.22 | 53.048 | 46.902 | 17.826 | 0 | 0 | 47.866 | 32.365 | [5 empty] | 15.825 | 10.83 | 1 | 6.528 | 6.13 | 4.9409 | 4.6154 | 1.5146 | 23.2012
2006-03-12 | 3:17 | 0 | 15.8 | 1 | 6 | 0 | 57.893 | 58.543 | 46.603 | 47.04 | 38.643 | 25.835 | 0.286 | 0 | 0 | 57.197 | 53.048 | 46.835 | 17.826 | 0 | 0 | 47.819 | 32.365 | [5 empty] | 0 | 10.853 | 2 | 6.5131 | 6.1158 | 4.9403 | 4.6154 | 1.5005 | 23.0374
2006-03-12 | 3:18 | 0 | 15.837 | 0 | 5 | 0 | 57.882 | 58.578 | 46.592 | 46.982 | 38.208 | 25.848 | 0.374 | 1 | 0 | 57.208 | 53.059 | 46.844 | 17.861 | 0 | 0 | 47.808 | 32.377 | [5 empty] | 0 | 10.9 | 3 | 6.4875 | 6.0915 | 4.9393 | 4.6154 | 1.4761 | 22.7529
2006-03-12 | 3:19 | 0 | 15.837 | 0 | 5 | 0 | 57.904 | 58.532 | 46.592 | 47.098 | 38.466 | 25.992 | 0.348 | 1 | 0 | 57.231 | 53.083 | 46.823 | 17.861 | 0 | 0 | 47.784 | 32.399 | [5 empty] | 0 | 10.806 | 4 | 6.4951 | 6.0987 | 4.9396 | 4.6154 | 1.4833 | 22.8372
2006-03-12 | 3:20 | 1 | 15.837 | 0 | 5 | 0 | 58.062 | 58.598 | 46.615 | 47.052 | 38.842 | 25.919 | 0.425 | 1 | 0 | 57.186 | 53.059 | 46.844 | 17.839 | 0 | 0 | 47.761 | 32.424 | [5 empty] | 15.837 | 11.01 | 5 | 6.4726 | 6.0774 | 4.9387 | 4.6154 | 1.462 | 22.587
2006-03-12 | 3:21 | 0 | 15.837 | 0 | 5 | 0 | 58.062 | 58.712 | 46.524 | 46.961 | 39.736 | 25.823 | 0.399 | 1 | 0 | 57.208 | 53.059 | 46.844 | 17.861 | 0 | 0 | 47.74 | 32.399 | [5 empty] | 0 | 11.101 | 6 | 6.4802 | 6.0846 | 4.939 | 4.6154 | 1.4692 | 22.6717
2006-03-12 | 3:22 | 0 | 15.812 | 0 | 5 | 0 | 58.039 | 58.689 | 46.454 | 47.028 | 40.205 | 25.943 | 0.222 | 1 | 0 | 57.231 | 53.059 | 46.823 | 17.911 | 0 | 0 | 47.717 | 32.377 | [5 empty] | 0 | 11.011 | 7 | 6.5318 | 6.1336 | 4.9411 | 4.6154 | 1.5182 | 23.2429
2006-03-12 | 3:23 | 0 | 15.83 | 0 | 6 | 0 | 58.098 | 58.66 | 46.54 | 47.021 | 40.174 | 25.742 | 0.289 | 1 | 0 | 57.135 | 52.982 | 46.86 | 17.828 | 0 | 0 | 47.663 | 32.392 | [5 empty] | 0 | 11.077 | 8 | 6.5122 | 6.115 | 4.9403 | 4.6154 | 1.4996 | 23.0277
2006-03-12 | 3:24 | 1 | 15.78 | 0 | 5 | 0 | 58.053 | 58.683 | 46.494 | 47.112 | 40.832 | 25.791 | 0.314 | 1 | 0 | 57.156 | 53.029 | 46.814 | 17.828 | 0 | 0 | 47.663 | 32.392 | [5 empty] | 15.78 | 10.941 | 9 | 6.505 | 6.1081 | 4.94 | 4.6154 | 1.4927 | 22.9471
2006-03-12 | 3:25 | 0 | 15.754 | 0 | 5 | 0 | 58.121 | 58.683 | 46.561 | 47.089 | 40.528 | 25.742 | 0.392 | 1 | 0 | 57.135 | 52.982 | 46.907 | 17.806 | 0 | 0 | 47.616 | 32.367 | [5 empty] | 0 | 11.032 | 10 | 6.4822 | 6.0865 | 4.9391 | 4.6154 | 1.4711 | 22.6944
2006-03-12 | 3:26 | 0 | 15.78 | 1 | 5 | 0 | 58.009 | 58.726 | 46.585 | 47.045 | 39.351 | 25.742 | 0.34 | 1 | 0 | 57.135 | 52.938 | 46.837 | 17.806 | 0 | 0 | 47.64 | 32.345 | [5 empty] | 0 | 10.964 | 11 | 6.4974 | 6.1009 | 4.9397 | 4.6154 | 1.4855 | 22.8631
2006-03-12 | 3:27 | 1 | 15.787 | 0 | 5 | 1 | 58.016 | 58.621 | 46.608 | 47.068 | 39.21 | 25.936 | 0.314 | 1 | 0 | 57.135 | 53.006 | 46.792 | 17.806 | 0 | 0 | 47.616 | 32.321 | [5 empty] | 15.787 | 10.948 | 12 | 6.505 | 6.1081 | 4.94 | 4.6154 | 1.4927 | 22.9471
2006-03-12 | 3:28 | 0 | 15.78 | 0 | 5 | 0 | 58.009 | 58.637 | 46.54 | 47.182 | 39.516 | 25.84 | 0.314 | 1 | 0 | 57.113 | 52.982 | 46.814 | 17.806 | 0 | 0 | 47.595 | 32.321 | [5 empty] | 0 | 10.827 | 0 | 6.505 | 6.1081 | 4.94 | 4.6154 | 1.4927 | 22.9471
2006-03-12 | 3:29 | 0 | 15.812 | 0 | 5 | 0 | 58.062 | 58.667 | 46.547 | 47.213 | 39.406 | 25.823 | 0.425 | 1 | 0 | 57.165 | 52.992 | 46.961 | 17.861 | 0 | 0 | 47.626 | 32.424 | [5 empty] | 0 | 10.849 | 1 | 6.4726 | 6.0774 | 4.609 | 4.2857 | 1.7916 | 27.6803
2006-03-12 | 3:30 | 0 | 15.805 | 0 | 5 | 0 | 58.009 | 58.66 | 46.655 | 47.089 | 39.564 | 25.84 | 0.366 | 0 | 0 | 57.156 | 52.938 | 46.792 | 17.828 | 0 | 0 | 47.595 | 32.392 | [5 empty] | 0 | 10.92 | 2 | 6.4898 | 6.0937 | 4.6097 | 4.2857 | 1.808 | 27.8587
2006-03-12 | 3:31 | 1 | 15.78 | 0 | 5 | 0 | 58.053 | 58.703 | 46.517 | 47.089 | 39.471 | 25.936 | 0.34 | 1 | 0 | 57.113 | 52.961 | 46.907 | 17.879 | 0 | 0 | 47.595 | 32.345 | [5 empty] | 15.78 | 10.964 | 3 | 6.4974 | 6.1009 | 4.61 | 4.2857 | 1.8152 | 27.937
2006-03-12 | 3:32 | 0 | 15.78 | 0 | 5 | 0 | 58.009 | 58.66 | 46.561 | 47.112 | 39.564 | 25.865 | 0.314 | 1 | 0 | 57.135 | 52.938 | 46.792 | 17.854 | 0 | 0 | 47.572 | 32.321 | [5 empty] | 0 | 10.897 | 4 | 6.505 | 6.1081 | 4.6103 | 4.2857 | 1.8224 | 28.0151
2006-03-12 | 3:33 | 0 | 15.83 | 0 | 5 | 0 | 58.009 | 58.66 | 46.54 | 47.045 | 39.351 | 25.936 | 0.392 | 1 | 0 | 57.113 | 52.915 | 46.792 | 17.806 | 0 | 0 | 47.572 | 32.345 | [5 empty] | 0 | 10.964 | 5 | 6.4822 | 6.0865 | 4.6094 | 4.2857 | 1.8008 | 27.7802
2006-03-12 | 3:34 | 0 | 15.78 | 0 | 5 | 0 | 57.964 | 58.703 | 46.608 | 47.045 | 38.552 | 25.936 | 0.34 | 1 | 0 | 57.113 | 52.961 | 46.722 | 17.806 | 0 | 0 | 47.572 | 32.367 | [5 empty] | 0 | 10.919 | 6 | 6.4974 | 6.1009 | 4.61 | 4.2857 | 1.8152 | 27.937
2006-03-12 | 3:35 | 1 | 15.78 | 1 | 6 | 0 | 58.053 | 58.637 | 46.631 | 47.159 | 39.282 | 25.936 | 0.34 | 1 | 0 | 57.067 | 52.938 | 46.814 | 17.806 | 0 | 0 | 47.549 | 32.367 | [5 empty] | 15.78 | 10.894 | 7 | 6.4974 | 6.1009 | 4.61 | 4.2857 | 1.8152 | 27.937
2006-03-12 | 3:36 | 0 | 15.78 | 0 | 5 | 0 | 57.987 | 58.66 | 46.54 | 47.182 | 39.471 | 26.009 | 0.24 | 1 | 0 | 57.09 | 52.961 | 46.792 | 17.828 | 0 | 0 | 47.525 | 32.392 | [5 empty] | 0 | 10.805 | 8 | 6.5265 | 6.1286 | 4.6112 | 4.2857 | 1.8429 | 28.2364
2006-03-12 | 3:37 | 0 | 15.805 | 0 | 5 | 0 | 58.009 | 58.614 | 46.631 | 47.068 | 39.164 | 26.105 | 0.392 | 1 | 0 | 57.113 | 52.915 | 46.792 | 17.806 | 0 | 0 | 47.549 | 32.392 | [5 empty] | 0 | 10.941 | 9 | 6.4822 | 6.0865 | 4.6094 | 4.2857 | 1.8008 | 27.7802
2006-03-12 | 3:38 | 0 | 15.764 | 0 | 5 | 0 | 57.952 | 58.603 | 46.573 | 47.031 | 39.222 | 25.995 | 0.399 | 1 | 0 | 57.055 | 52.88 | 46.802 | 17.791 | 0 | 0 | 47.514 | 32.355 | [5 empty] | 0 | 10.921 | 10 | 6.4802 | 6.0846 | 4.6093 | 4.2857 | 1.7988 | 27.759
2006-03-12 | 3:39 | 1 | 15.815 | 0 | 5 | 0 | 57.929 | 58.557 | 46.503 | 47.192 | 39.363 | 26.139 | 0.502 | 1 | 0 | 57.055 | 52.88 | 46.778 | 17.816 | 0 | 0 | 47.537 | 32.402 | [5 empty] | 15.815 | 10.737 | 11 | 6.4502 | 6.056 | 4.6081 | 4.2857 | 1.7703 | 27.4461
2006-03-12 | 3:40 | 0 | 15.79 | 0 | 5 | 0 | 57.929 | 58.557 | 46.55 | 46.986 | 39.597 | 26.019 | 0.376 | 0 | 0 | 57.078 | 52.926 | 46.802 | 17.816 | 0 | 0 | 47.514 | 32.38 | [5 empty] | 0 | 10.943 | 12 | 6.4869 | 6.0909 | 4.6096 | 4.2857 | 1.8052 | 27.8285
2006-03-12 | 3:41 | 0 | 15.785 | 0 | 5 | 1 | 57.902 | 58.53 | 46.431 | 47.003 | 39.758 | 25.916 | 0.268 | 1 | 0 | 57.028 | 52.805 | 46.774 | 17.761 | 0 | 0 | 47.462 | 32.35 | [5 empty] | 0 | 10.899 | 13 | 6.5184 | 6.1208 | 4.6109 | 4.2857 | 1.8351 | 28.1528
2006-03-12 | 3:42 | 0 | 15.79 | 0 | 5 | 0 | 57.929 | 58.58 | 46.596 | 46.986 | 39.27 | 26.041 | 0.299 | 1 | 0 | 57.033 | 52.856 | 46.734 | 17.816 | 0 | 0 | 47.49 | 32.355 | [5 empty] | 0 | 10.943 | 0 | 6.5093 | 6.1122 | 4.6105 | 4.2857 | 1.8265 | 28.0601
2006-03-12 | 3:43 | 1 | 15.79 | 0 | 5 | 0 | 57.929 | 58.536 | 46.664 | 47.01 | 39.291 | 26.134 | 0.294 | 1 | 0 | 57.097 | 52.852 | 46.683 | 17.833 | 0 | 0 | 47.462 | 32.326 | [5 empty] | 15.79 | 10.919 | 1 | 6.5108 | 6.1136 | 4.6105 | 4.2857 | 1.8279 | 28.075
2006-03-12 | 3:44 | 0 | 15.764 | 0 | 5 | 0 | 57.975 | 58.58 | 46.55 | 47.054 | 38.892 | 26.164 | 0.399 | 1 | 0 | 57.078 | 52.88 | 46.734 | 17.864 | 0 | 0 | 47.537 | 32.331 | [5 empty] | 0 | 10.921 | 2 | 6.4802 | 6.0846 | 4.6093 | 4.2857 | 1.7988 | 27.759
2006-03-12 | 3:45 | 0 | 15.79 | 1 | 6 | 0 | 58.064 | 58.671 | 46.526 | 46.986 | 39.198 | 26.041 | 0.451 | 1 | 0 | 57.055 | 52.856 | 46.825 | 17.864 | 0 | 0 | 47.49 | 32.355 | [5 empty] | 0 | 11.078 | 3 | 6.4651 | 6.0702 | 4.6087 | 4.2857 | 1.7844 | 27.6014
2006-03-12 | 3:46 | 1 | 15.759 | 0 | 5 | 0 | 58.082 | 58.733 | 46.522 | 46.912 | 39.1 | 25.892 | 0.369 | 1 | 0 | 57.028 | 52.828 | 46.729 | 17.808 | 0 | 0 | 47.462 | 32.35 | [5 empty] | 15.759 | 11.17 | 4 | 6.4889 | 6.0929 | 4.6097 | 4.2857 | 1.8071 | 27.8496
2006-03-12 | 3:47 | 0 | 15.764 | 0 | 5 | 0 | 58.176 | 58.783 | 46.62 | 46.986 | 39.363 | 25.899 | 0.477 | 1 | 0 | 57.055 | 52.856 | 46.849 | 17.816 | 0 | 0 | 47.467 | 32.355 | [5 empty] | 0 | 11.19 | 5 | 6.4575 | 6.063 | 4.6084 | 4.2857 | 1.7773 | 27.5223
2006-03-12 | 3:48 | 0 | 15.764 | 0 | 5 | 0 | 58.133 | 58.714 | 46.526 | 47.054 | 38.916 | 25.85 | 0.603 | 1 | 0 | 57.055 | 52.856 | 46.872 | 17.839 | 0 | 0 | 47.444 | 32.355 | [5 empty] | 0 | 11.079 | 6 | 6.4208 | 6.0281 | 4.6069 | 4.2857 | 1.7424 | 27.1364
2006-03-12 | 3:49 | 0 | 15.79 | 0 | 5 | 0 | 58.11 | 58.714 | 46.459 | 46.986 | 38.94 | 25.777 | 0.603 | 1 | 0 | 57.01 | 52.833 | 46.711 | 17.839 | 0 | 0 | 47.467 | 32.306 | [5 empty] | 0 | 11.124 | 7 | 6.4208 | 6.0281 | 4.6069 | 4.2857 | 1.7424 | 27.1364
2006-03-12 | 3:50 | 1 | 15.734 | 0 | 5 | 0 | 58.014 | 58.552 | 46.613 | 47.026 | 39.334 | 25.87 | 0.572 | 1 | 0 | 57.005 | 52.805 | 46.683 | 17.833 | 0 | 0 | 47.439 | 32.301 | [5 empty] | 15.734 | 10.988 | 8 | 6.4298 | 6.0367 | 4.6073 | 4.2857 | 1.751 | 27.2317
2006-03-12 | 3:51 | 0 | 15.709 | 0 | 5 | 0 | 57.948 | 58.733 | 46.636 | 47.073 | 39.334 | 25.821 | 0.345 | 1 | 0 | 57.055 | 52.81 | 46.711 | 17.791 | 0 | 0 | 47.467 | 32.355 | [5 empty] | 0 | 10.875 | 9 | 6.4959 | 6.0995 | 4.6099 | 4.2857 | 1.8138 | 27.9219
2006-03-12 | 3:52 | 0 | 15.734 | 0 | 5 | 0 | 57.993 | 58.644 | 46.545 | 47.026 | 39.169 | 25.845 | 0.52 | 1 | 0 | 57.028 | 52.761 | 46.706 | 17.761 | 0 | 0 | 47.416 | 32.326 | [5 empty] | 0 | 10.967 | 10 | 6.445 | 6.0511 | 4.6079 | 4.2857 | 1.7653 | 27.3911
2006-03-12 | 3:53 | 0 | 15.734 | 0 | 5 | 0 | 58.06 | 58.664 | 46.706 | 47.026 | 38.322 | 25.916 | 0.446 | 1 | 0 | 56.982 | 52.761 | 46.659 | 17.761 | 0 | 0 | 47.416 | 32.301 | [5 empty] | 0 | 11.034 | 11 | 6.4665 | 6.0715 | 4.6088 | 4.2857 | 1.7858 | 27.6166
2006-03-12 | 3:54 | 1 | 15.785 | 1 | 6 | 0 | 57.79 | 58.552 | 46.568 | 47.026 | 39.193 | 25.845 | 0.672 | 1 | 0 | 57.005 | 52.782 | 46.636 | 17.808 | 0 | 0 | 47.416 | 32.326 | [5 empty] | 15.785 | 10.764 | 12 | 6.4007 | 6.009 | 4.6061 | 4.2857 | 1.7233 | 26.9232
2006-03-12 | 3:55 | 0 | 15.764 | 0 | 5 | 1 | 57.863 | 58.648 | 46.573 | 47.329 | 39.621 | 26.09 | 0.603 | 1 | 0 | 57.01 | 52.719 | 46.778 | 17.816 | 0 | 0 | 47.444 | 32.306 | [5 empty] | 0 | 10.534 | 13 | 6.4208 | 6.0281 | 4.6069 | 4.2857 | 1.7424 | 27.1364
2006-03-12 | 3:56 | 0 | 15.734 | 0 | 5 | 0 | 57.902 | 58.552 | 46.522 | 47.049 | 38.605 | 25.892 | 0.546 | 1 | 0 | 56.982 | 52.761 | 46.636 | 17.833 | 0 | 0 | 47.392 | 32.277 | [5 empty] | 0 | 10.853 | 0 | 6.4374 | 6.0439 | 4.6076 | 4.2857 | 1.7582 | 27.3115
2006-03-12 | 3:57 | 0 | 15.734 | 0 | 5 | 0 | 57.859 | 58.509 | 46.522 | 47.073 | 38.535 | 26.036 | 0.472 | 0 | 0 | 56.982 | 52.761 | 46.636 | 17.833 | 0 | 0 | 47.416 | 32.301 | [5 empty] | 0 | 10.786 | 1 | 6.459 | 6.0644 | 4.6084 | 4.2857 | 1.7786 | 27.5375
2006-03-12 | 3:58 | 1 | 15.772 | 0 | 5 | 0 | 57.913 | 58.498 | 46.557 | 47.108 | 38.617 | 25.833 | 0.636 | 1 | 0 | 56.971 | 52.749 | 46.718 | 17.821 | 0 | 0 | 47.404 | 32.363 | [5 empty] | 15.772 | 10.805 | 2 | 6.4112 | 6.019 | 4.6065 | 4.2857 | 1.7332 | 27.0346
2006-03-12 | 3:59 | 0 | 15.777 | 0 | 5 | 0 | 57.898 | 58.502 | 46.561 | 47.066 | 38.222 | 25.982 | 0.667 | 1 | 0 | 57.021 | 52.8 | 46.676 | 17.876 | 0 | 0 | 47.432 | 32.343 | [5 empty] | 0 | 10.832 | 3 | 6.4022 | 6.0104 | 4.6061 | 4.2857 | 1.7247 | 26.9387
2006-03-12 | 4:00 | 0 | 15.772 | 0 | 5 | 0 | 57.959 | 58.475 | 46.466 | 46.97 | 38.452 | 25.808 | 0.611 | 1 | 0 | 56.971 | 52.772 | 46.785 | 17.798 | 0 | 0 | 47.383 | 32.338 | [5 empty] | 0 | 10.989 | 4 | 6.4185 | 6.0259 | 4.6068 | 4.2857 | 1.7402 | 27.1117
2006-03-12 | 4:01 | 0 | 15.772 | 0 | 5 | 0 | 57.779 | 58.475 | 46.442 | 47.038 | 38.148 | 25.784 | 0.533 | 1 | 0 | 56.95 | 52.726 | 46.762 | 17.821 | 0 | 0 | 47.36 | 32.289 | [5 empty] | 0 | 10.741 | 5 | 6.4412 | 6.0475 | 4.6077 | 4.2857 | 1.7618 | 27.3513
2006-03-12 | 4:02 | 1 | 15.772 | 0 | 6 | 0 | 57.779 | 58.429 | 46.466 | 47.014 | 39.157 | 25.713 | 0.611 | 1 | 0 | 56.928 | 52.702 | 46.671 | 17.846 | 0 | 0 | 47.404 | 32.24 | [5 empty] | 15.772 | 10.765 | 6 | 6.4185 | 6.0259 | 4.6068 | 4.2857 | 1.7402 | 27.1117
2006-03-12 | 4:03 | 0 | 15.797 | 1 | 5 | 0 | 57.802 | 58.452 | 46.51 | 46.947 | 38.617 | 25.857 | 0.737 | 1 | 0 | 57.017 | 52.772 | 46.648 | 17.846 | 0 | 0 | 47.404 | 32.264 | [5 empty] | 0 | 10.855 | 7 | 6.3818 | 5.991 | 4.6053 | 4.2857 | 1.7053 | 26.7211
2006-03-12 | 4:04 | 0 | 15.772 | 0 | 5 | 0 | 57.982 | 58.518 | 46.51 | 47.038 | 39.205 | 25.759 | 0.533 | 1 | 0 | 56.905 | 52.702 | 46.718 | 17.821 | 0 | 0 | 47.404 | 32.289 | [5 empty] | 0 | 10.944 | 8 | 6.4412 | 6.0475 | 4.6077 | 4.2857 | 1.7618 | 27.3513
2006-03-12 | 4:05 | 1 | 15.747 | 0 | 5 | 0 | 57.936 | 58.564 | 46.58 | 46.923 | 38.923 | 25.784 | 0.636 | 1 | 0 | 56.928 | 52.749 | 46.694 | 17.821 | 0 | 0 | 47.36 | 32.289 | [5 empty] | 15.747 | 11.013 | 9 | 6.4112 | 6.019 | 4.6065 | 4.2857 | 1.7332 | 27.0346
2006-03-12 | 4:06 | 0 | 15.772 | 0 | 5 | 0 | 57.87 | 58.498 | 46.603 | 46.947 | 39.581 | 25.713 | 0.66 | 1 | 0 | 56.905 | 52.702 | 46.624 | 17.798 | 0 | 0 | 47.36 | 32.314 | [5 empty] | 0 | 10.923 | 10 | 6.4042 | 6.0123 | 4.6062 | 4.2857 | 1.7266 | 26.9604
2006-03-12 | 4:07 | 0 | 15.772 | 0 | 5 | 0 | 57.936 | 58.518 | 46.442 | 46.993 | 39.392 | 25.759 | 0.533 | 0 | 0 | 56.905 | 52.702 | 46.648 | 17.798 | 0 | 0 | 47.383 | 32.314 | [5 empty] | 0 | 10.943 | 11 | 6.4412 | 6.0475 | 4.6077 | 4.2857 | 1.7618 | 27.3513
2006-03-12 | 4:08 | 0 | 15.747 | 0 | 5 | 0 | 58.002 | 58.518 | 46.466 | 46.947 | 39.533 | 25.713 | 0.559 | 1 | 0 | 56.928 | 52.702 | 46.718 | 17.798 | 0 | 0 | 47.36 | 32.314 | [5 empty] | 0 | 11.055 | 12 | 6.4336 | 6.0403 | 4.6074 | 4.2857 | 1.7546 | 27.2717
2006-03-12 | 4:09 | 1 | 15.772 | 0 | 5 | 1 | 57.87 | 58.518 | 46.557 | 46.923 | 39.791 | 25.808 | 0.66 | 1 | 0 | 56.905 | 52.726 | 46.624 | 17.798 | 0 | 0 | 47.383 | 32.289 | [5 empty] | 15.772 | 10.947 | 13 | 6.4042 | 6.0123 | 4.6062 | 4.2857 | 1.7266 | 26.9604
2006-03-12 | 4:10 | 0 | 15.772 | 0 | 5 | 0 | 57.936 | 58.541 | 46.487 | 47.014 | 39.275 | 25.737 | 0.685 | 1 | 0 | 56.882 | 52.679 | 46.739 | 17.798 | 0 | 0 | 47.383 | 32.289 | [5 empty] | 0 | 10.922 | 0 | 6.3969 | 6.0054 | 4.6059 | 4.2857 | 1.7197 | 26.8829
2006-03-12 | 4:11 | 0 | 15.797 | 0 | 6 | 0 | 57.891 | 58.541 | 46.51 | 46.923 | 39.511 | 25.978 | 0.763 | 1 | 0 | 56.882 | 52.726 | 46.694 | 17.871 | 0 | 0 | 47.383 | 32.264 | [5 empty] | 0 | 10.968 | 1 | 6.3742 | 5.9838 | 4.9347 | 4.6154 | 1.3684 | 21.468
2006-03-12 | 4:12 | 0 | 15.772 | 1 | 5 | 0 | 57.824 | 58.498 | 46.466 | 46.9 | 39.392 | 25.857 | 0.737 | 1 | 0 | 56.882 | 52.656 | 46.58 | 17.821 | 0 | 0 | 47.36 | 32.24 | [5 empty] | 0 | 10.924 | 2 | 6.3818 | 5.991 | 4.935 | 4.6154 | 1.3756 | 21.5553
2006-03-12 | 4:13 | 1 | 15.802 | 0 | 5 | 0 | 57.829 | 58.434 | 46.561 | 46.928 | 39.093 | 25.933 | 0.794 | 1 | 0 | 56.955 | 52.684 | 46.631 | 17.851 | 0 | 0 | 47.364 | 32.294 | [5 empty] | 15.802 | 10.901 | 3 | 6.3652 | 5.9752 | 4.9343 | 4.6154 | 1.3598 | 21.3636
2006-03-12 | 4:14 | 0 | 15.747 | 0 | 5 | 0 | 57.756 | 58.475 | 46.533 | 47.084 | 39.088 | 25.857 | 0.711 | 1 | 0 | 56.859 | 52.656 | 46.58 | 17.846 | 0 | 0 | 47.36 | 32.264 | [5 empty] | 0 | 10.672 | 4 | 6.3894 | 5.9982 | 4.9353 | 4.6154 | 1.3828 | 21.6424
2006-03-12 | 4:15 | 0 | 15.772 | 0 | 5 | 0 | 57.735 | 58.406 | 46.58 | 46.97 | 38.851 | 25.833 | 0.763 | 1 | 0 | 56.859 | 52.656 | 46.624 | 17.846 | 0 | 0 | 47.36 | 32.24 | [5 empty] | 0 | 10.765 | 5 | 6.3742 | 5.9838 | 4.9347 | 4.6154 | 1.3684 | 21.468
2006-03-12 | 4:16 | 0 | 15.747 | 0 | 5 | 0 | 57.756 | 58.386 | 46.466 | 46.947 | 38.734 | 25.808 | 0.812 | 1 | 0 | 56.882 | 52.656 | 46.533 | 17.846 | 0 | 0 | 47.36 | 32.218 | [5 empty] | 0 | 10.809 | 6 | 6.3599 | 5.9702 | 4.9341 | 4.6154 | 1.3549 | 21.3029
2006-03-12 | 4:17 | 1 | 15.772 | 0 | 5 | 0 | 57.824 | 58.386 | 46.58 | 46.947 | 38.782 | 25.759 | 0.66 | 1 | 0 | 56.882 | 52.634 | 46.58 | 17.846 | 0 | 0 | 47.336 | 32.314 | [5 empty] | 15.772 | 10.877 | 7 | 6.4042 | 6.0123 | 4.9359 | 4.6154 | 1.3969 | 21.8126
2006-03-12 | 4:18 | 0 | 15.772 | 0 | 6 | 0 | 57.79 | 58.463 | 46.454 | 46.865 | 39.38 | 25.821 | 0.75 | 0 | 0 | 56.871 | 52.667 | 46.592 | 17.786 | 0 | 0 | 47.325 | 32.252 | [5 empty] | 0 | 10.925 | 8 | 6.378 | 5.9874 | 4.9348 | 4.6154 | 1.372 | 21.5117
2006-03-12 | 4:19 | 0 | 15.744 | 0 | 5 | 0 | 57.688 | 58.361 | 46.44 | 46.851 | 40.167 | 25.732 | 0.683 | 1 | 0 | 56.903 | 52.677 | 46.783 | 17.869 | 0 | 0 | 47.311 | 32.238 | [5 empty] | 0 | 10.837 | 9 | 6.3975 | 6.0059 | 4.9356 | 4.6154 | 1.3906 | 21.736
2006-03-12 | 4:20 | 0 | 15.749 | 0 | 5 | 0 | 57.781 | 58.365 | 46.421 | 46.879 | 39.796 | 25.74 | 0.791 | 1 | 0 | 56.818 | 52.613 | 46.559 | 17.801 | 0 | 0 | 47.315 | 32.316 | [5 empty] | 0 | 10.902 | 10 | 6.3661 | 5.9761 | 4.9344 | 4.6154 | 1.3607 | 21.3738
2006-03-12 | 4:21 | 1 | 15.775 | 1 | 5 | 0 | 57.85 | 58.388 | 46.468 | 46.972 | 39.49 | 25.74 | 0.662 | 1 | 0 | 56.818 | 52.66 | 46.65 | 17.801 | 0 | 0 | 47.315 | 32.242 | [5 empty] | 15.775 | 10.878 | 11 | 6.4036 | 6.0118 | 4.9359 | 4.6154 | 1.3964 | 21.806
2006-03-12 | 4:22 | 0 | 15.775 | 0 | 5 | 1 | 57.804 | 58.409 | 46.398 | 46.858 | 38.877 | 25.691 | 0.562 | 1 | 0 | 56.841 | 52.59 | 46.582 | 17.801 | 0 | 0 | 47.339 | 32.267 | [5 empty] | 0 | 10.946 | 12 | 6.4327 | 6.0394 | 4.9371 | 4.6154 | 1.4241 | 22.1376
2006-03-12 | 4:23 | 0 | 15.775 | 0 | 5 | 0 | 57.893 | 58.454 | 46.421 | 46.858 | 39.7 | 25.74 | 0.461 | 1 | 0 | 56.818 | 52.613 | 46.582 | 17.849 | 0 | 0 | 47.339 | 32.267 | [5 empty] | 0 | 11.035 | 0 | 6.4622 | 6.0674 | 4.9382 | 4.6154 | 1.452 | 22.4694
2006-03-12 | 4:24 | 1 | 15.749 | 0 | 5 | 0 | 57.872 | 58.657 | 46.398 | 46.835 | 39.184 | 25.74 | 0.688 | 1 | 0 | 56.841 | 52.59 | 46.536 | 17.823 | 0 | 0 | 47.339 | 32.22 | [5 empty] | 15.749 | 11.037 | 1 | 6.3961 | 6.0046 | 4.6059 | 4.2857 | 1.7188 | 26.8736
2006-03-12 | 4:25 | 0 | 15.775 | 0 | 6 | 0 | 57.827 | 58.523 | 46.536 | 46.835 | 39.466 | 25.811 | 0.662 | 1 | 0 | 56.861 | 52.567 | 46.606 | 17.823 | 0 | 0 | 47.362 | 32.267 | [5 empty] | 0 | 10.992 | 2 | 6.4036 | 6.0118 | 4.6062 | 4.2857 | 1.726 | 26.9542
2006-03-12 | 4:26 | 0 | 15.775 | 0 | 5 | 0 | 57.781 | 58.543 | 46.512 | 46.926 | 38.832 | 25.715 | 0.51 | 1 | 0 | 56.795 | 52.543 | 46.536 | 17.823 | 0 | 0 | 47.339 | 32.267 | [5 empty] | 0 | 10.855 | 3 | 6.4479 | 6.0538 | 4.608 | 4.2857 | 1.7681 | 27.4217
2006-03-12 | 4:27 | 0 | 15.749 | 0 | 5 | 0 | 57.872 | 58.523 | 46.375 | 46.996 | 39.301 | 25.715 | 0.435 | 1 | 0 | 56.818 | 52.59 | 46.697 | 17.899 | 0 | 0 | 47.339 | 32.267 | [5 empty] | 0 | 10.876 | 4 | 6.4697 | 6.0746 | 4.6089 | 4.2857 | 1.7889 | 27.65
2006-03-12 | 4:28 | 1 | 15.744 | 0 | 5 | 0 | 57.957 | 58.427 | 46.461 | 46.83 | 39.413 | 25.686 | 0.479 | 1 | 0 | 56.768 | 52.494 | 46.531 | 17.746 | 0 | 0 | 47.287 | 32.262 | [5 empty] | 15.744 | 11.127 | 5 | 6.4569 | 6.0624 | 4.6084 | 4.2857 | 1.7767 | 27.5162
2006-03-12 | 4:29 | 0 | 15.744 | 0 | 5 | 0 | 57.754 | 58.516 | 46.393 | 46.806 | 39.179 | 25.757 | 0.33 | 1 | 0 | 56.791 | 52.562 | 46.461 | 17.746 | 0 | 0 | 47.264 | 32.238 | [5 empty] | 0 | 10.948 | 6 | 6.5003 | 6.1037 | 4.6101 | 4.2857 | 1.8179 | 27.967
2006-03-12 | 4:30 | 0 | 15.744 | 1 | 5 | 0 | 57.866 | 58.381 | 46.37 | 46.851 | 38.59 | 25.926 | 0.253 | 1 | 0 | 56.791 | 52.539 | 46.461 | 17.793 | 0 | 0 | 47.287 | 32.213 | [5 empty] | 0 | 11.015 | 7 | 6.5227 | 6.125 | 4.611 | 4.2857 | 1.8393 | 28.1976
2006-03-12 | 4:31 | 0 | 15.744 | 0 | 6 | 0 | 58.069 | 58.63 | 46.461 | 46.83 | 39.296 | 25.686 | 0.33 | 1 | 0 | 56.768 | 52.515 | 46.578 | 17.771 | 0 | 0 | 47.243 | 32.262 | [5 empty] | 0 | 11.239 | 8 | 6.5003 | 6.1037 | 4.6101 | 4.2857 | 1.8179 | 27.967
2006-03-12 | 4:32 | 1 | 15.775 | 0 | 5 | 0 | 58.185 | 58.769 | 46.445 | 46.926 | 38.901 | 25.715 | 0.41 | 1 | 0 | 56.795 | 52.499 | 46.559 | 17.823 | 0 | 0 | 47.271 | 32.22 | [5 empty] | 15.775 | 11.259 | 9 | 6.477 | 6.0815 | 4.6092 | 4.2857 | 1.7958 | 27.7257
2006-03-12 | 4:33 | 0 | 15.744 | 0 | 5 | 0 | 58.203 | 58.785 | 46.44 | 46.874 | 39.32 | 25.661 | 0.278 | 1 | 0 | 56.745 | 52.471 | 46.484 | 17.793 | 0 | 0 | 47.264 | 32.213 | [5 empty] | 0 | 11.329 | 10 | 6.5154 | 6.118 | 4.6107 | 4.2857 | 1.8323 | 28.1229
2006-03-12 | 4:34 | 0 | 15.8 | 0 | 5 | 0 | 58.254 | 58.835 | 46.468 | 46.879 | 39.418 | 25.835 | 0.384 | 1 | 0 | 56.818 | 52.567 | 46.468 | 17.849 | 0 | 0 | 47.292 | 32.242 | [5 empty] | 0 | 11.375 | 11 | 6.4846 | 6.0887 | 4.6095 | 4.2857 | 1.803 | 27.8043
2006-03-12 | 4:35 | 1 | 15.795 | 0 | 5 | 0 | 58.226 | 58.808 | 46.347 | 46.83 | 40.707 | 25.686 | 0.405 | 1 | 0 | 56.745 | 52.494 | 46.554 | 17.793 | 0 | 0 | 47.334 | 32.191 | [5 empty] | 15.795 | 11.396 | 12 | 6.4785 | 6.0829 | 4.6092 | 4.2857 | 1.7972 | 27.7409
2006-03-12 | 4:36 | 0 | 15.825 | 0 | 5 | 1 | 58.185 | 58.881 | 46.65 | 46.972 | 40.853 | 25.835 | 0.384 | 1 | 0 | 56.795 | 52.543 | 46.445 | 17.849 | 0 | 0 | 47.271 | 32.171 | [5 empty] | 0 | 11.213 | 13 | 6.4846 | 6.0887 | 4.6095 | 4.2857 | 1.803 | 27.8043
2006-03-12 | 4:37 | 0 | 15.744 | 0 | 5 | 0 | 58.135 | 58.785 | 46.508 | 46.944 | 40.308 | 25.83 | 0.456 | 1 | 0 | 56.768 | 52.515 | 46.44 | 17.771 | 0 | 0 | 47.243 | 32.142 | [5 empty] | 0 | 11.191 | 0 | 6.4636 | 6.0688 | 4.6086 | 4.2857 | 1.7831 | 27.5862
2006-03-12 | 4:38 | 0 | 15.898 | 0 | 6 | 0 | 58.208 | 58.835 | 46.489 | 47.017 | 40.217 | 25.811 | 0.714 | 1 | 0 | 56.772 | 52.522 | 46.606 | 17.823 | 0 | 0 | 47.248 | 32.242 | [5 empty] | 0 | 11.191 | 1 | 6.3885 | 5.9974 | 4.9353 | 4.6154 | 1.382 | 21.6324
2006-03-12 | 4:39 | 1 | 15.709 | 1 | 5 | 0 | 58.082 | 58.776 | 46.522 | 47.003 | 39.593 | 25.796 | 0.52 | 1 | 0 | 56.759 | 52.462 | 46.475 | 17.783 | 0 | 0 | 47.231 | 32.203 | [5 empty] | 15.709 | 11.079 | 2 | 6.445 | 6.0511 | 4.9375 | 4.6154 | 1.4357 | 22.2759
2006-03-12 | 4:40 | 0 | 15.769 | 0 | 5 | 0 | 58.135 | 58.808 | 46.554 | 46.989 | 39.107 | 25.806 | 0.683 | 1 | 0 | 56.791 | 52.471 | 46.484 | 17.818 | 0 | 0 | 47.264 | 32.238 | [5 empty] | 0 | 11.146 | 3 | 6.3975 | 6.0059 | 4.9356 | 4.6154 | 1.3906 | 21.736
2006-03-12 | 4:41 | 0 | 15.734 | 0 | 5 | 0 | 58.126 | 58.753 | 46.522 | 46.979 | 39.263 | 25.843 | 0.546 | 1 | 0 | 56.736 | 52.483 | 46.566 | 17.758 | 0 | 0 | 47.187 | 32.179 | [5 empty] | 0 | 11.147 | 4 | 6.4374 | 6.0439 | 4.9372 | 4.6154 | 1.4285 | 22.1903
2006-03-12 | 4:42 | 0 | 15.795 | 0 | 5 | 0 | 58.158 | 58.762 | 46.578 | 46.989 | 39.554 | 25.997 | 0.43 | 1 | 0 | 56.745 | 52.494 | 46.578 | 17.818 | 0 | 0 | 47.243 | 32.238 | [5 empty] | 0 | 11.169 | 5 | 6.4712 | 6.076 | 4.9386 | 4.6154 | 1.4606 | 22.5707
2006-03-12 | 4:43 | 1 | 15.795 | 0 | 5 | 0 | 58.18 | 58.808 | 46.578 | 47.059 | 38.92 | 25.951 | 0.43 | 0 | 0 | 56.768 | 52.494 | 46.554 | 17.894 | 0 | 0 | 47.357 | 32.358 | [5 empty] | 15.795 | 11.121 | 6 | 6.4712 | 6.076 | 4.9386 | 4.6154 | 1.4606 | 22.5707
2006-03-12 | 4:44 | 0 | 15.795 | 0 | 6 | 0 | 58.135 | 58.742 | 46.715 | 47.012 | 38.92 | 26.022 | 0.631 | 1 | 0 | 56.791 | 52.494 | 46.508 | 17.793 | 0 | 0 | 47.264 | 32.262 | [5 empty] | 0 | 11.123 | 7 | 6.4127 | 6.0203 | 4.9362 | 4.6154 | 1.405 | 21.9091
2006-03-12 | 4:45 | 0 | 15.709 | 0 | 5 | 0 | 58.014 | 58.71 | 46.566 | 47.003 | 39.614 | 26.012 | 0.621 | 1 | 0 | 56.713 | 52.438 | 46.407 | 17.783 | 0 | 0 | 47.21 | 32.203 | [5 empty] | 0 | 11.011 | 8 | 6.4156 | 6.0231 | 4.9364 | 4.6154 | 1.4077 | 21.9423
2006-03-12 | 4:46 | 0 | 15.734 | 0 | 5 | 0 | 58.103 | 58.664 | 46.589 | 47.026 | 40.791 | 26.012 | 0.52 | 1 | 0 | 56.713 | 52.415 | 46.522 | 17.735 | 0 | 0 | 47.187 | 32.203 | [5 empty] | 0 | 11.077 | 9 | 6.445 | 6.0511 | 4.9375 | 4.6154 | 1.4357 | 22.2759
2006-03-12 | 4:47 | 1 | 15.734 | 0 | 5 | 0 | 58.103 | 58.71 | 46.566 | 47.14 | 40.602 | 25.916 | 0.647 | 1 | 0 | 56.713 | 52.392 | 46.545 | 17.735 | 0 | 0 | 47.187 | 32.228 | [5 empty] | 15.734 | 10.963 | 10 | 6.408 | 6.0159 | 4.9361 | 4.6154 | 1.4005 | 21.8559
2006-03-12 | 4:48 | 0 | 15.734 | 1 | 5 | 0 | 58.014 | 58.641 | 46.636 | 47.073 | 40.227 | 25.941 | 0.647 | 1 | 0 | 56.69 | 52.415 | 46.475 | 17.758 | 0 | 0 | 47.187 | 32.203 | [5 empty] | 0 | 10.941 | 11 | 6.408 | 6.0159 | 4.9361 | 4.6154 | 1.4005 | 21.8559
2006-03-12 | 4:49 | 0 | 15.769 | 0 | 5 | 1 | 58.046 | 58.63 | 46.531 | 46.989 | 39.906 | 26.046 | 0.861 | 1 | 0 | 56.722 | 52.448 | 46.461 | 17.793 | 0 | 0 | 47.22 | 32.238 | [5 empty] | 0 | 11.057 | 12 | 6.3457 | 5.9567 | 4.9335 | 4.6154 | 1.3413 | 21.1371
2006-03-12 | 4:50 | 1 | 15.734 | 0 | 6 | 0 | 58.037 | 58.619 | 46.407 | 47.117 | 39.521 | 25.941 | 0.672 | 1 | 0 | 56.67 | 52.368 | 46.475 | 17.783 | 0 | 0 | 47.187 | 32.179 | [5 empty] | 15.734 | 10.92 | 0 | 6.4007 | 6.009 | 4.9358 | 4.6154 | 1.3936 | 21.7727
2006-03-12 | 4:51 | 0 | 15.759 | 0 | 5 | 0 | 57.991 | 58.619 | 46.498 | 46.979 | 39.896 | 25.916 | 0.672 | 1 | 0 | 56.67 | 52.415 | 46.407 | 17.808 | 0 | 0 | 47.187 | 32.179 | [5 empty] | 0 | 11.012 | 1 | 6.4007 | 6.009 | 4.6061 | 4.2857 | 1.7233 | 26.9232
2006-03-12 | 4:52 | 0 | 15.734 | 0 | 5 | 0 | 57.948 | 58.641 | 46.683 | 47.003 | 39.71 | 26.012 | 0.799 | 1 | 0 | 56.69 | 52.415 | 46.407 | 17.808 | 0 | 0 | 47.187 | 32.179 | [5 empty] | 0 | 10.945 | 2 | 6.3637 | 5.9738 | 4.6046 | 4.2857 | 1.6881 | 26.5272
2006-03-12 | 4:53 | 0 | 15.795 | 0 | 5 | 0 | 57.957 | 58.63 | 46.645 | 47.012 | 39.53 | 25.975 | 1.013 | 1 | 0 | 56.722 | 52.424 | 46.461 | 17.818 | 0 | 0 | 47.22 | 32.262 | [5 empty] | 0 | 10.945 | 3 | 6.3014 | 5.9146 | 4.6021 | 4.2857 | 1.6289 | 25.8496
2006-03-12 | 4:54 | 1 | 15.734 | 0 | 5 | 0 | 57.968 | 58.507 | 46.522 | 47.073 | 40.344 | 25.843 | 0.899 | 0 | 0 | 56.67 | 52.415 | 46.428 | 17.783 | 0 | 0 | 47.164 | 32.179 | [5 empty] | 15.734 | 10.895 | 4 | 6.3346 | 5.9462 | 4.6034 | 4.2857 | 1.6604 | 26.2122
2006-03-12 | 4:55 | 0 | 15.734 | 0 | 5 | 0 | 57.767 | 58.507 | 46.566 | 46.935 | 40.509 | 25.867 | 0.799 | 1 | 0 | 56.67 | 52.368 | 46.407 | 17.735 | 0 | 0 | 47.164 | 32.179 | [5 empty] | 0 | 10.832 | 5 | 6.3637 | 5.9738 | 4.6046 | 4.2857 | 1.6881 | 26.5272
2006-03-12 | 4:56 | 0 | 15.709 | 0 | 5 | 0 | 57.813 | 58.418 | 46.452 | 46.979 | 40.061 | 25.892 | 0.799 | 1 | 0 | 56.647 | 52.368 | 46.407 | 17.808 | 0 | 0 | 47.164 | 32.179 | [5 empty] | 0 | 10.834 | 6 | 6.3637 | 5.9738 | 4.6046 | 4.2857 | 1.6881 | 26.5272
2006-03-12 | 4:57 | 0 | 15.709 | 1 | 6 | 0 | 57.879 | 58.418 | 46.428 | 46.979 | 39.662 | 25.867 | 0.773 | 1 | 0 | 56.69 | 52.415 | 46.475 | 17.758 | 0 | 0 | 47.14 | 32.157 | [5 empty] | 0 | 10.9 | 7 | 6.3713 | 5.981 | 4.6049 | 4.2857 | 1.6953 | 26.6087
2006-03-12 | 4:58 | 1 | 15.759 | 0 | 5 | 0 | 57.813 | 58.372 | 46.407 | 46.935 | 38.815 | 26.061 | 0.85 | 1 | 0 | 56.69 | 52.392 | 46.361 | 17.808 | 0 | 0 | 47.164 | 32.108 | [5 empty] | 15.759 | 10.878 | 8 | 6.3489 | 5.9597 | 4.604 | 4.2857 | 1.674 | 26.3669
2006-03-12 | 4:59 | 0 | 15.752 | 0 | 5 | 0 | 57.806 | 58.411 | 46.424 | 46.881 | 39.162 | 25.884 | 0.868 | 1 | 0 | 56.64 | 52.361 | 46.4 | 17.753 | 0 | 0 | 47.133 | 32.174 | [5 empty] | 0 | 10.925 | 9 | 6.3436 | 5.9547 | 4.6038 | 4.2857 | 1.669 | 26.3102
2006-03-12 | 5:00 | 0 | 15.702 | 0 | 5 | 0 | 57.715 | 58.411 | 46.424 | 46.951 | 39.231 | 25.958 | 0.817 | 1 | 0 | 56.686 | 52.385 | 46.33 | 17.776 | 0 | 0 | 47.133 | 32.125 | [5 empty] | 0 | 10.764 | 10 | 6.3585 | 5.9689 | 4.6044 | 4.2857 | 1.6831 | 26.4708
2006-03-12 | 5:01 | 0 | 15.727 | 0 | 5 | 0 | 57.783 | 58.365 | 46.491 | 46.881 | 40.291 | 25.933 | 0.842 | 1 | 0 | 56.64 | 52.34 | 46.491 | 17.753 | 0 | 0 | 47.11 | 32.125 | [5 empty] | 0 | 10.902 | 11 | 6.3512 | 5.9619 | 4.6041 | 4.2857 | 1.6762 | 26.3921
2006-03-12 | 5:02 | 1 | 15.759 | 0 | 5 | 0 | 57.813 | 58.53 | 46.475 | 46.912 | 40.722 | 25.916 | 0.951 | 1 | 0 | 56.624 | 52.371 | 46.431 | 17.761 | 0 | 0 | 47.164 | 32.206 | [5 empty] | 15.759 | 10.901 | 12 | 6.3195 | 5.9318 | 4.6028 | 4.2857 | 1.646 | 26.0473
2006-03-12 | 5:03 | 0 | 15.702 | 0 | 6 | 1 | 57.783 | 58.479 | 46.4 | 46.905 | 40.454 | 25.933 | 0.765 | 1 | 0 | 56.617 | 52.361 | 46.491 | 17.801 | 0 | 0 | 47.133 | 32.174 | [5 empty] | 0 | 10.878 | 13 | 6.3736 | 5.9832 | 4.605 | 4.2857 | 1.6975 | 26.6337
2006-03-12 | 5:04 | 0 | 15.727 | 0 | 5 | 0 | 57.761 | 58.411 | 46.4 | 46.835 | 40.009 | 25.884 | 0.842 | 1 | 0 | 56.64 | 52.34 | 46.468 | 17.776 | 0 | 0 | 47.11 | 32.174 | [5 empty] | 0 | 10.926 | 0 | 6.3512 | 5.9619 | 4.6041 | 4.2857 | 1.6762 | 26.3921
2006-03-12 | 5:05 | 1 | 15.694 | 0 | 5 | 0 | 57.843 | 58.404 | 46.438 | 46.783 | 40.188 | 25.926 | 0.783 | 1 | 0 | 56.61 | 52.31 | 46.3 | 17.72 | 0 | 0 | 47.103 | 32.142 | [5 empty] | 15.694 | 11.06 | 1 | 6.3684 | 5.9783 | 4.9344 | 4.6154 | 1.3629 | 21.4007
2006-03-12 | 5:06 | 0 | 15.644 | 1 | 5 | 0 | 57.866 | 58.47 | 46.37 | 46.828 | 40.305 | 25.781 | 0.732 | 1 | 0 | 56.588 | 52.287 | 46.279 | 17.768 | 0 | 0 | 47.103 | 32.117 | [5 empty] | 0 | 11.038 | 2 | 6.3832 | 5.9924 | 4.935 | 4.6154 | 1.377 | 21.5721
2006-03-12 | 5:07 | 0 | 15.792 | 0 | 5 | 0 | 57.731 | 58.45 | 46.37 | 46.828 | 40.095 | 25.902 | 0.809 | 1 | 0 | 56.588 | 52.287 | 46.256 | 17.768 | 0 | 0 | 47.08 | 32.093 | [5 empty] | 0 | 10.903 | 3 | 6.3608 | 5.9711 | 4.9341 | 4.6154 | 1.3557 | 21.313
2006-03-12 | 5:08 | 0 | 15.694 | 0 | 5 | 0 | 57.777 | 58.381 | 46.323 | 46.828 | 39.389 | 25.877 | 0.809 | 1 | 0 | 56.565 | 52.287 | 46.256 | 17.743 | 0 | 0 | 47.103 | 32.117 | [5 empty] | 0 | 10.949 | 4 | 6.3608 | 5.9711 | 4.9341 | 4.6154 | 1.3557 | 21.313
2006-03-12 | 5:09 | 1 | 15.727 | 0 | 6 | 0 | 57.85 | 58.434 | 46.286 | 46.996 | 39.255 | 25.933 | 0.691 | 1 | 0 | 56.572 | 52.294 | 46.354 | 17.776 | 0 | 0 | 47.11 | 32.196 | [5 empty] | 15.727 | 10.854 | 5 | 6.3952 | 6.0037 | 4.9355 | 4.6154 | 1.3883 | 21.7093
2006-03-12 | 5:10 | 0 | 15.694 | 0 | 5 | 0 | 57.82 | 58.427 | 46.393 | 47.059 | 39.155 | 25.877 | 0.783 | 1 | 0 | 56.542 | 52.263 | 46.37 | 17.768 | 0 | 0 | 47.08 | 32.142 | [5 empty] | 0 | 10.761 | 6 | 6.3684 | 5.9783 | 4.9344 | 4.6154 | 1.3629 | 21.4007
2006-03-12 | 5:11 | 0 | 15.669 | 0 | 5 | 0 | 57.731 | 58.404 | 46.347 | 46.874 | 39.365 | 25.853 | 0.709 | 0 | 0 | 56.542 | 52.263 | 46.256 | 17.793 | 0 | 0 | 47.08 | 32.188 | [5 empty] | 0 | 10.857 | 7 | 6.3899 | 5.9987 | 4.9353 | 4.6154 | 1.3834 | 21.6491
2006-03-12 | 5:12 | 0 | 15.702 | 0 | 5 | 0 | 57.85 | 58.365 | 46.445 | 46.858 | 39.796 | 25.884 | 0.691 | 1 | 0 | 56.551 | 52.294 | 46.354 | 17.728 | 0 | 0 | 47.11 | 32.125 | [5 empty] | 0 | 10.992 | 8 | 6.3952 | 6.0037 | 4.9355 | 4.6154 | 1.3883 | 21.7093
2006-03-12 | 5:13 | 1 | 15.694 | 0 | 5 | 0 | 57.799 | 58.381 | 46.323 | 46.851 | 39.813 | 25.806 | 0.683 | 1 | 0 | 56.521 | 52.24 | 46.347 | 17.768 | 0 | 0 | 47.08 | 32.117 | [5 empty] | 15.694 | 10.948 | 9 | 6.3975 | 6.0059 | 4.9356 | 4.6154 | 1.3906 | 21.736
2006-03-12 | 5:14 | 0 | 15.727 | 0 | 5 | 0 | 57.806 | 58.411 | 46.445 | 46.881 | 39.42 | 25.909 | 0.765 | 1 | 0 | 56.594 | 52.294 | 46.263 | 17.753 | 0 | 0 | 47.133 | 32.125 | [5 empty] | 0 | 10.925 | 10 | 6.3736 | 5.9832 | 4.9347 | 4.6154 | 1.3679 | 21.4613
2006-03-12 | 5:15 | 0 | 15.727 | 0 | 5 | 0 | 57.761 | 58.457 | 46.377 | 46.858 | 39.609 | 26.005 | 0.817 | 1 | 0 | 56.594 | 52.294 | 46.309 | 17.776 | 0 | 0 | 47.11 | 32.149 | [5 empty] | 0 | 10.903 | 11 | 6.3585 | 5.9689 | 4.934 | 4.6154 | 1.3535 | 21.286
2006-03-12 | 5:16 | 0 | 15.669 | 1 | 6 | 1 | 57.799 | 58.427 | 46.37 | 46.828 | 39.53 | 25.877 | 0.783 | 1 | 0 | 56.521 | 52.24 | 46.232 | 17.743 | 0 | 0 | 47.08 | 32.117 | [5 empty] | 0 | 10.971 | 12 | 6.3684 | 5.9783 | 4.9344 | 4.6154 | 1.3629 | 21.4007
2006-03-12 | 5:17 | 1 | 15.719 | 0 | 5 | 0 | 57.754 | 58.404 | 46.508 | 46.783 | 39.459 | 25.757 | 0.861 | 1 | 0 | 56.521 | 52.217 | 46.37 | 17.72 | 0 | 0 | 47.035 | 32.142 | [5 empty] | 15.719 | 10.971 | 0 | 6.3457 | 5.9567 | 4.9335 | 4.6154 | 1.3413 | 21.1371
2006-03-12 | 5:18 | 0 | 15.694 | 0 | 5 | 0 | 57.777 | 58.45 | 46.438 | 46.898 | 39.248 | 25.828 | 0.935 | 1 | 0 | 56.521 | 52.263 | 46.279 | 17.793 | 0 | 0 | 47.08 | 32.093 | [5 empty] | 0 | 10.879 | 1 | 6.3241 | 5.9362 | 4.603 | 4.2857 | 1.6505 | 26.0981
2006-03-12 | 5:19 | 0 | 15.727 | 0 | 5 | 0 | 57.806 | 58.365 | 46.354 | 46.858 | 39.114 | 25.838 | 0.894 | 1 | 0 | 56.572 | 52.294 | 46.445 | 17.776 | 0 | 0 | 47.11 | 32.125 | [5 empty] | 0 | 10.948 | 2 | 6.3361 | 5.9475 | 4.6035 | 4.2857 | 1.6618 | 26.228
2006-03-12 | 5:20 | 0 | 15.719 | 0 | 5 | 0 | 57.777 | 58.358 | 46.347 | 46.874 | 38.897 | 25.828 | 0.884 | 1 | 0 | 56.521 | 52.217 | 46.347 | 17.768 | 0 | 0 | 47.08 | 32.142 | [5 empty] | 0 | 10.903 | 3 | 6.339 | 5.9503 | 4.6036 | 4.2857 | 1.6646 | 26.2597
2006-03-12 | 5:21 | 1 | 15.727 | 0 | 5 | 0 | 57.738 | 58.411 | 46.561 | 46.858 | 38.856 | 25.958 | 0.994 | 1 | 0 | 56.528 | 52.27 | 46.354 | 17.826 | 0 | 0 | 47.11 | 32.174 | [5 empty] | 15.727 | 10.88 | 4 | 6.3069 | 5.9199 | 4.6023 | 4.2857 | 1.6341 | 25.9103
2006-03-12 | 5:22 | 0 | 15.719 | 0 | 6 | 0 | 57.866 | 58.427 | 46.393 | 46.828 | 38.849 | 25.806 | 0.757 | 1 | 0 | 56.521 | 52.217 | 46.323 | 17.743 | 0 | 0 | 47.08 | 32.142 | [5 empty] | 0 | 11.038 | 5 | 6.376 | 5.9855 | 4.6051 | 4.2857 | 1.6997 | 26.6587
2006-03-12 | 5:23 | 0 | 15.719 | 0 | 5 | 0 | 57.82 | 58.45 | 46.393 | 46.804 | 38.918 | 25.877 | 0.783 | 1 | 0 | 56.499 | 52.217 | 46.3 | 17.793 | 0 | 0 | 47.059 | 32.068 | [5 empty] | 0 | 11.016 | 6 | 6.3684 | 5.9783 | 4.6048 | 4.2857 | 1.6926 | 26.5774
2006-03-12 | 5:24 | 1 | 15.719 | 0 | 5 | 0 | 57.82 | 58.427 | 46.393 | 46.828 | 38.966 | 25.877 | 0.709 | 0 | 0 | 56.521 | 52.24 | 46.37 | 17.844 | 0 | 0 | 47.059 | 32.044 | [5 empty] | 15.719 | 10.992 | 7 | 6.3899 | 5.9987 | 4.6056 | 4.2857 | 1.713 | 26.8083
2006-03-12 | 5:25 | 0 | 15.752 | 1 | 5 | 0 | 57.872 | 58.479 | 46.491 | 46.996 | 39.114 | 25.838 | 0.917 | 1 | 0 | 56.528 | 52.226 | 46.377 | 17.801 | 0 | 0 | 47.089 | 32.076 | [5 empty] | 0 | 10.876 | 8 | 6.3294 | 5.9412 | 4.6032 | 4.2857 | 1.6555 | 26.1552
2006-03-12 | 5:26 | 0 | 15.719 | 0 | 5 | 0 | 57.843 | 58.427 | 46.508 | 46.851 | 39.437 | 26.142 | 0.757 | 1 | 0 | 56.499 | 52.24 | 46.3 | 17.793 | 0 | 0 | 47.08 | 32.044 | [5 empty] | 0 | 10.992 | 9 | 6.376 | 5.9855 | 4.6051 | 4.2857 | 1.6997 | 26.6587
2006-03-12 | 5:27 | 0 | 15.719 | 0 | 5 | 0 | 57.799 | 58.45 | 46.484 | 46.828 | 39.578 | 25.853 | 0.884 | 1 | 0 | 56.521 | 52.196 | 46.256 | 17.793 | 0 | 0 | 47.059 | 32.068 | [5 empty] | 0 | 10.971 | 10 | 6.339 | 5.9503 | 4.6036 | 4.2857 | 1.6646 | 26.2597
2006-03-12 | 5:28 | 1 | 15.689 | 0 | 6 | 0 | 57.772 | 58.354 | 46.342 | 46.799 | 39.337 | 25.872 | 0.853 | 1 | 0 | 56.471 | 52.168 | 46.342 | 17.763 | 0 | 0 | 47.007 | 32.039 | [5 empty] | 15.689 | 10.973 | 11 | 6.348 | 5.9589 | 4.6039 | 4.2857 | 1.6732 | 26.3575
2006-03-12 | 5:29 | 0 | 15.744 | 0 | 5 | 0 | 57.866 | 58.381 | 46.531 | 46.898 | 39.765 | 25.973 | 0.835 | 1 | 0 | 56.521 | 52.172 | 46.3 | 17.793 | 0 | 0 | 47.059 | 32.068 | [5 empty] | 0 | 10.968 | 12 | 6.3532 | 5.9639 | 4.6042 | 4.2857 | 1.6782 | 26.4142
2006-03-12 | 5:30 | 0 | 15.689 | 0 | 5 | 1 | 57.861 | 58.534 | 46.365 | 46.799 | 39.009 | 25.848 | 0.804 | 1 | 0 | 56.471 | 52.189 | 46.319 | 17.763 | 0 | 0 | 47.007 | 32.039 | [5 empty] | 0 | 11.062 | 13 | 6.3623 | 5.9725 | 4.6045 | 4.2857 | 1.6867 | 26.5116
2006-03-12 | 5:31 | 0 | 15.694 | 0 | 5 | 0 | 57.82 | 58.47 | 46.347 | 46.851 | 38.849 | 25.828 | 0.809 | 1 | 0 | 56.499 | 52.196 | 46.232 | 17.793 | 0 | 0 | 47.059 | 32.068 | [5 empty] | 0 | 10.969 | 0 | 6.3608 | 5.9711 | 4.6045 | 4.2857 | 1.6854 | 26.4959
2006-03-12 | 5:32 | 1 | 15.694 | 0 | 5 | 0 | 57.843 | 58.427 | 46.414 | 46.921 | 38.966 | 25.877 | 0.861 | 1 | 0 | 56.453 | 52.196 | 46.232 | 17.793 | 0 | 0 | 47.035 | 32.068 | [5 empty] | 15.694 | 10.922 | 1 | 6.3457 | 5.9567 | 4.9335 | 4.6154 | 1.3413 | 21.1371
2006-03-12 | 5:33 | 0 | 15.694 | 0 | 5 | 0 | 57.777 | 58.427 | 46.393 | 46.942 | 38.801 | 25.828 | 0.909 | 1 | 0 | 56.453 | 52.149 | 46.347 | 17.793 | 0 | 0 | 47.035 | 32.117 | [5 empty] | 0 | 10.835 | 2 | 6.3317 | 5.9434 | 4.933 | 4.6154 | 1.328 | 20.9739
2006-03-12 | 5:34 | 0 | 15.744 | 1 | 6 | 0 | 57.799 | 58.427 | 46.461 | 46.989 | 38.897 | 25.948 | 1.087 | 1 | 0 | 56.499 | 52.149 | 46.232 | 17.768 | 0 | 0 | 47.035 | 32.068 | [5 empty] | 0 | 10.81 | 3 | 6.2799 | 5.8941 | 4.9309 | 4.6154 | 1.2787 | 20.3624
2006-03-12 | 5:35 | 0 | 15.694 | 0 | 5 | 0 | 57.777 | 58.427 | 46.461 | 46.898 | 38.732 | 25.973 | 0.935 | 1 | 0 | 56.499 | 52.172 | 46.209 | 17.743 | 0 | 0 | 47.035 | 32.093 | [5 empty] | 0 | 10.879 | 4 | 6.3241 | 5.9362 | 4.9327 | 4.6154 | 1.3208 | 20.8852
2006-03-12 | 5:36 | 1 | 15.719 | 0 | 5 | 0 | 57.82 | 58.404 | 46.37 | 46.942 | 38.708 | 25.877 | 0.961 | 1 | 0 | 56.453 | 52.126 | 46.256 | 17.743 | 0 | 0 | 47.012 | 32.142 | [5 empty] | 15.719 | 10.878 | 5 | 6.3166 | 5.929 | 4.9323 | 4.6154 | 1.3136 | 20.7963
2006-03-12 | 5:37 | 0 | 15.744 | 0 | 5 | 0 | 57.777 | 58.427 | 46.37 | 46.874 | 40.399 | 25.877 | 0.909 | 1 | 0 | 56.453 | 52.149 | 46.186 | 17.793 | 0 | 0 | 47.012 | 32.117 | [5 empty] | 0 | 10.903 | 6 | 6.3317 | 5.9434 | 4.933 | 4.6154 | 1.328 | 20.9739
2006-03-12 | 5:38 | 0 | 15.719 | 0 | 5 | 0 | 57.754 | 58.441 | 46.2 | 46.933 | 40.179 | 25.818 | 0.897 | 1 | 0 | 56.421 | 52.14 | 46.2 | 17.756 | 0 | 0 | 46.979 | 32.081 | [5 empty] | 0 | 10.821 | 7 | 6.3352 | 5.9467 | 4.9331 | 4.6154 | 1.3313 | 21.0148
2006-03-12 | 5:39 | 1 | 15.704 | 0 | 5 | 0 | 57.765 | 58.459 | 46.358 | 46.792 | 39.963 | 25.816 | 0.868 | 0 | 0 | 56.419 | 52.114 | 46.197 | 17.753 | 0 | 0 | 46.977 | 32.056 | [5 empty] | 15.704 | 10.973 | 8 | 6.3436 | 5.9547 | 4.9334 | 4.6154 | 1.3394 | 21.1133
2006-03-12 | 5:40 | 0 | 15.679 | 0 | 6 | 0 | 57.788 | 58.438 | 46.358 | 46.816 | 40.128 | 25.838 | 0.868 | 2 | 0 | 56.419 | 52.091 | 46.197 | 17.73 | 0 | 0 | 47 | 32.032 | [5 empty] | 0 | 10.972 | 9 | 6.3436 | 5.9547 | 4.9334 | 4.6154 | 1.3394 | 21.1133
2006-03-12 | 5:41 | 0 | 15.714 | 0 | 5 | 0 | 57.886 | 58.425 | 46.435 | 46.825 | 39.951 | 25.85 | 0.982 | 0 | 0 | 56.474 | 52.1 | 46.207 | 17.715 | 0 | 0 | 47.033 | 32.09 | [5 empty] | 0 | 11.061 | 10 | 6.3104 | 5.9232 | 4.9321 | 4.6154 | 1.3078 | 20.7243
2006-03-12 | 5:42 | 0 | 15.654 | 0 | 5 | 0 | 57.809 | 58.438 | 46.312 | 46.886 | 39.399 | 25.742 | 0.894 | 1 | 0 | 56.375 | 52.114 | 46.174 | 17.879 | 0 | 0 | 46.977 | 32.056 | [5 empty] | 0 | 10.923 | 11 | 6.3361 | 5.9475 | 4.9331 | 4.6154 | 1.3322 | 21.025
2006-03-12 | 5:43 | 1 | 15.714 | 1 | 5 | 1 | 57.863 | 58.47 | 46.412 | 46.849 | 39.739 | 25.801 | 1.005 | 1 | 0 | 56.474 | 52.1 | 46.183 | 17.788 | 0 | 0 | 47.01 | 32.09 | [5 empty] | 15.714 | 11.014 | 12 | 6.3037 | 5.9168 | 4.9318 | 4.6154 | 1.3014 | 20.6454
2006-03-12 | 5:44 | 0 | 15.679 | 0 | 5 | 0 | 57.809 | 58.438 | 46.358 | 46.816 | 39.798 | 25.911 | 0.842 | 1 | 0 | 56.396 | 52.091 | 46.127 | 17.753 | 0 | 0 | 46.977 | 32.056 | [5 empty] | 0 | 10.993 | 0 | 6.3512 | 5.9619 | 4.9337 | 4.6154 | 1.3465 | 21.2015
2006-03-12 | 5:45 | 0 | 15.679 | 0 | 5 | 0 | 57.765 | 58.393 | 46.403 | 46.954 | 40.435 | 25.838 | 0.92 | 1 | 0 | 56.396 | 52.044 | 46.221 | 17.705 | 0 | 0 | 46.977 | 32.056 | [5 empty] | 0 | 10.811 | 1 | 6.3285 | 5.9403 | 5.3174 | 5 | 0.94034 | 14.8589
2006-03-12 | 5:46 | 0 | 15.704 | 0 | 5 | 0 | 57.809 | 58.416 | 46.449 | 46.839 | 39.471 | 26.007 | 0.716 | 1 | 0 | 56.353 | 52.044 | 46.197 | 17.705 | 0 | 0 | 46.954 | 32.032 | [5 empty] | 0 | 10.97 | 2 | 6.3879 | 5.9968 | 5.3199 | 5 | 0.99681 | 15.6047
2006-03-12 | 5:47 | 1 | 15.739 | 0 | 6 | 0 | 57.84 | 58.425 | 46.526 | 46.849 | 39.105 | 26.066 | 0.93 | 1 | 0 | 56.428 | 52.1 | 46.183 | 17.74 | 0 | 0 | 46.986 | 32.09 | [5 empty] | 15.739 | 10.991 | 3 | 6.3256 | 5.9376 | 5.3173 | 5 | 0.93758 | 14.822
2006-03-12 | 5:48 | 0 | 15.679 | 0 | 5 | 0 | 57.765 | 58.393 | 46.449 | 46.886 | 39.212 | 26.007 | 0.742 | 1 | 0 | 56.353 | 52.044 | 46.151 | 17.73 | 0 | 0 | 46.954 | 32.056 | [5 empty] | 0 | 10.879 | 4 | 6.3803 | 5.9896 | 5.3195 | 5 | 0.98961 | 15.5104
2006-03-12 | 5:49 | 0 | 15.739 | 0 | 5 | 0 | 57.886 | 58.402 | 46.459 | 46.895 | 39.739 | 25.97 | 0.879 | 1 | 0 | 56.385 | 52.1 | 46.183 | 17.788 | 0 | 0 | 46.986 | 32.09 | [5 empty] | 0 | 10.991 | 5 | 6.3404 | 5.9517 | 5.3179 | 5 | 0.95169 | 15.0099
2006-03-12 | 5:50 | 0 | 15.679 | 0 | 5 | 0 | 57.809 | 58.438 | 46.449 | 46.839 | 39.141 | 26.032 | 0.969 | 1 | 0 | 56.375 | 52.023 | 46.174 | 17.803 | 0 | 0 | 46.954 | 32.032 | [5 empty] | 0 | 10.97 | 6 | 6.3142 | 5.9268 | 5.3169 | 5 | 0.92678 | 14.6777
2006-03-12 | 5:51 | 1 | 15.679 | 0 | 5 | 0 | 57.742 | 58.416 | 46.358 | 46.863 | 39.939 | 26.032 | 0.794 | 1 | 0 | 56.353 | 52.044 | 46.221 | 17.73 | 0 | 0 | 46.954 | 32.056 | [5 empty] | 15.679 | 10.879 | 7 | 6.3652 | 5.9752 | 5.3189 | 5 | 0.97522 | 15.3212
2006-03-12 | 5:52 | 0 | 15.704 | 1 | 5 | 0 | 57.765 | 58.416 | 46.426 | 46.839 | 39.681 | 25.96 | 0.794 | 1 | 0 | 56.33 | 52 | 46.151 | 17.73 | 0 | 0 | 46.93 | 32.056 | [5 empty] | 0 | 10.926 | 8 | 6.3652 | 5.9752 | 5.3189 | 5 | 0.97522 | 15.3212
2006-03-12 | 5:53 | 0 | 15.679 | 0 | 13 | 0 | 58.169 | 58.304 | 46.449 | 52.413 | 54.429 | 25.982 | 0.868 | 1 | 0 | 55.736 | 52.023 | 52.87 | 17.73 | 0 | 0 | 46.907 | 32.103 | [5 empty] | 0 | 5.756 | 9 | 6.3436 | 5.9547 | 5.3181 | 5 | 0.95474 | 15.0503
2006-03-12 | 5:54 | 1 | 15.679 | 0 | 15 | 0 | 65.905 | 58.012 | 47.504 | 56.419 | 56.105 | 25.887 | 0.92 | 1 | 0 | 63.885 | 52.023 | 57.046 | 17.778 | 0 | 0 | 46.93 | 33.29 | [5 empty] | 15.679 | 9.486 | 10 | 6.3285 | 5.9403 | 5.3174 | 5 | 0.94034 | 14.8589
2006-03-12 | 5:55 | 1 | 15.729 | 0 | 15 | 1 | 69.65 | 57.742 | 49.131 | 60.725 | 56.035 | 25.911 | 1.098 | 1 | 1 | 68.179 | 52.275 | 60.725 | 17.753 | 0 | 0 | 46.93 | 36.909 | [5 empty] | 15.729 | 8.925 | 11 | 6.2767 | 5.8911 | 5.3153 | 5 | 0.89107 | 14.1966
2006-03-12 | 5:56 | 1 | 15.739 | 0 | 15 | 0 | 70.782 | 57.528 | 50.611 | 62.863 | 55.816 | 25.872 | 1.031 | 0 | 0 | 69.704 | 52.856 | 62.662 | 17.839 | 0 | 0 | 46.963 | 39.786 | [5 empty] | 15.739 | 7.919 | 0 | 6.2962 | 5.9096 | 5.3161 | 5 | 0.90962 | 14.4472
2006-03-12 | 5:57 | 0 | 15.739 | 0 | 15 | 0 | 71.088 | 57.304 | 51.734 | 63.851 | 55.517 | 25.897 | 0.982 | 0 | 0 | 70.232 | 53.5 | 63.739 | 17.788 | 0 | 0 | 47.033 | 41.832 | [5 empty] | 0 | 7.237 | 1 | 6.3104 | 5.9232 | 8.8881 | 8.5714 | -2.6482 | -41.9661
2006-03-12 | 5:58 | 1 | 15.679 | 1 | 15 | 0 | 70.992 | 57.069 | 52.571 | 64.465 | 55.664 | 25.933 | 0.871 | 1 | 0 | 70.305 | 54.105 | 64.353 | 17.901 | 0 | 0 | 47.11 | 43.322 | [5 empty] | 15.679 | 6.527 | 2 | 6.3428 | 5.9539 | 8.8895 | 8.5714 | -2.6175 | -41.2678
2006-03-12 | 5:59 | 0 | 15.654 | 0 | 15 | 0 | 71.007 | 56.818 | 53.188 | 65.001 | 55.435 | 25.862 | 0.92 | 0 | 0 | 70.37 | 54.586 | 64.846 | 17.728 | 0 | 0 | 47.224 | 44.451 | [5 empty] | 0 | 6.006 | 3 | 6.3285 | 5.9403 | 8.8889 | 8.5714 | -2.6311 | -41.5752
2006-03-12 | 6:00 | 1 | 15.654 | 0 | 15 | 0 | 70.985 | 56.64 | 53.738 | 65.339 | 55.321 | 25.862 | 0.971 | 0 | 0 | 70.435 | 55.137 | 65.248 | 17.728 | 0 | 0 | 47.409 | 45.322 | [5 empty] | 15.654 | 5.646 | 4 | 6.3136 | 5.9262 | 8.8883 | 8.5714 | -2.6452 | -41.8966
2006-03-12 | 6:01 | 0 | 15.654 | 0 | 9 | 0 | 71.622 | 67.176 | 47.775 | 61.079 | 48.212 | 25.982 | 0.971 | 0 | 0 | 70.106 | 55.664 | 65.136 | 17.728 | 0 | 0 | 47.593 | 45.712 | [5 empty] | 0 | 10.543 | 5 | 6.3136 | 5.9262 | 8.8883 | 8.5714 | -2.6452 | -41.8966
2006-03-12 | 6:02 | 0 | 15.679 | 0 | 5 | 1 | 59.105 | 70.766 | 43.346 | 46.767 | 31.45 | 25.789 | 0.971 | 1 | 0 | 68.436 | 56.054 | 63.164 | 17.728 | 0 | 0 | 47.822 | 45.322 | [5 empty] | 0 | 12.338 | 6 | 6.3136 | 5.9262 | 8.8883 | 8.5714 | -2.6452 | -41.8966
2006-03-12 | 6:03 | 0 | 15.679 | 0 | 5 | 0 | 47.066 | 52.845 | 42.241 | 42.992 | 24.08 | 25.813 | 0.92 | 0 | 0 | 66.975 | 56.371 | 60.159 | 17.753 | 0 | 0 | 47.959 | 44.795 | [5 empty] | 0 | 4.074 | 0 | 6.3285 | 5.9403 | 8.8889 | 8.5714 | -2.6311 | -41.5752
2006-03-12 | 6:04 | 0 | 15.679 | 0 | 5 | 0 | 43.745 | 45.527 | 42.147 | 42.217 | 19.754 | 25.838 | 0.997 | 0 | 0 | 65.832 | 56.526 | 57.603 | 17.753 | 0 | 0 | 48.097 | 44.238 | [5 empty] | 0 | 1.528 | 1 | 6.3061 | 5.919 | 3.8459 | 3.5294 | 2.3896 | 37.8939
2006-03-12 | 6:05 | 0 | 15.654 | 1 | 6 | 0 | 42.946 | 43.815 | 42.992 | 42.898 | 16.519 | 25.887 | 1.02 | 0 | 0 | 65.024 | 56.64 | 55.711 | 17.753 | 0 | 0 | 48.212 | 43.745 | [5 empty] | 0 | 0.048 | 2 | 6.2994 | 5.9127 | 3.8457 | 3.5294 | 2.3833 | 37.8331
2006-03-12 | 6:06 | 0 | 15.654 | 0 | 5 | 0 | 43.628 | 43.886 | 41.865 | 43.228 | 14.937 | 25.718 | 0.997 | 0 | 0 | 64.351 | 56.795 | 54.243 | 17.778 | 0 | 0 | 48.279 | 43.346 | [5 empty] | 0 | 0.4 | 3 | 6.3061 | 5.919 | 3.8459 | 3.5294 | 2.3896 | 37.8939
2006-03-12 | 6:07 | 0 | 15.654 | 0 | 6 | 0 | 42.757 | 44.097 | 40.736 | 41.583 | 15.332 | 25.862 | 1.123 | 0 | 0 | 63.858 | 56.841 | 53.188 | 17.778 | 0 | 0 | 48.396 | 42.781 | [5 empty] | 0 | 1.174 | 4 | 6.2694 | 5.8842 | 3.8445 | 3.5294 | 2.3547 | 37.5594
2006-03-12 | 6:08 | 0 | 15.629 | 0 | 6 | 0 | 41.277 | 42.523 | 39.772 | 40.36 | 13.655 | 25.862 | 0.997 | 0 | 0 | 63.477 | 56.93 | 52.385 | 17.753 | 0 | 0 | 48.417 | 42.334 | [5 empty] | 0 | 0.917 | 5 | 6.3061 | 5.919 | 3.8459 | 3.5294 | 2.3896 | 37.8939
2006-03-12 | 6:09 | 0 | 15.629 | 0 | 6 | 0 | 40.195 | 41.207 | 39.255 | 39.727 | 12.939 | 25.669 | 1.02 | 0 | 0 | 63.096 | 56.907 | 51.538 | 17.753 | 0 | 0 | 48.464 | 41.889 | [5 empty] | 0 | 0.468 | 6 | 6.2994 | 5.9127 | 3.8457 | 3.5294 | 2.3833 | 37.8331
2006-03-12 | 6:10 | 0 | 15.599 | 0 | 5 | 0 | 39.626 | 40.284 | 38.5 | 39.227 | 11.724 | 25.568 | 1.041 | 1 | 0 | 62.822 | 56.925 | 51.187 | 17.723 | 0 | 0 | 48.482 | 41.506 | [5 empty] | 0 | 0.399 | 7 | 6.2933 | 5.9069 | 3.8454 | 3.5294 | 2.3774 | 37.7775
2006-03-12 | 6:11 | 0 | 15.654 | 0 | 6 | 0 | 38.904 | 39.82 | 37.799 | 38.339 | 10.767 | 25.598 | 1.123 | 0 | 0 | 62.557 | 56.998 | 50.735 | 17.728 | 0 | 0 | 48.555 | 41.159 | [5 empty] | 0 | 0.565 | 8 | 6.2694 | 5.8842 | 3.8445 | 3.5294 | 2.3547 | 37.5594
2006-03-12 | 6:12 | 0 | 15.704 | 0 | 6 | 0 | 45.826 | 39.186 | 37.234 | 37.634 | 33.333 | 25.548 | 1.098 | 0 | 0 | 62.334 | 56.998 | 50.527 | 17.728 | 0 | 0 | 48.555 | 40.853 | [5 empty] | 0 | 8.192 | 9 | 6.2767 | 5.8911 | 3.8448 | 3.5294 | 2.3617 | 37.6261
2006-03-12 | 6:13 | 1 | 15.624 | 0 | 6 | 0 | 53.136 | 51.302 | 36.572 | 36.902 | 36.43 | 25.254 | 1.092 | 0 | 0 | 62.06 | 56.994 | 50.27 | 17.65 | 0 | 0 | 48.55 | 40.497 | [5 empty] | 15.624 | 16.234 | 10 | 6.2784 | 5.8927 | 3.8448 | 3.5294 | 2.3633 | 37.6421
2006-03-12 | 6:14 | 0 | 15.604 | 0 | 6 | 0 | 55.435 | 55.069 | 36.318 | 36.507 | 37.492 | 25.139 | 1.072 | 0 | 0 | 61.907 | 56.998 | 50.16 | 17.778 | 0 | 0 | 48.601 | 40.313 | [5 empty] | 0 | 18.928 | 11 | 6.2842 | 5.8983 | 3.8451 | 3.5294 | 2.3689 | 37.6953
2006-03-12 | 6:15 | 1 | 15.624 | 1 | 6 | 0 | 56.633 | 56.633 | 37.064 | 36.548 | 38.004 | 25.11 | 1.067 | 3 | 0 | 61.724 | 56.994 | 49.995 | 17.698 | 0 | 0 | 48.573 | 39.956 | [5 empty] | 15.624 | 20.085 | 12 | 6.2857 | 5.8997 | 3.8451 | 3.5294 | 2.3702 | 37.7086
2006-03-12 | 6:16 | 0 | 15.624 | 0 | 6 | 0 | 57.083 | 57.418 | 38.734 | 38.287 | 39.203 | 24.965 | 1.041 | 2 | 0 | 61.613 | 57.014 | 50.018 | 17.698 | 0 | 0 | 48.55 | 39.674 | [5 empty] | 0 | 18.796 | 13 | 6.2933 | 5.9069 | 3.8454 | 3.5294 | 2.3774 | 37.7775
2006-03-12 | 6:17 | 1 | 15.624 | 0 | 5 | 0 | 57.756 | 57.934 | 40.449 | 40.097 | 40.848 | 25.085 | 1.041 | 2 | 0 | 61.521 | 57.037 | 49.834 | 17.723 | 0 | 0 | 48.597 | 39.44 | [5 empty] | 15.624 | 17.659 | 14 | 6.2933 | 5.9069 | 3.8454 | 3.5294 | 2.3774 | 37.7775
2006-03-12 | 6:18 | 0 | 15.679 | 0 | 6 | 0 | 57.961 | 58.589 | 41.922 | 41.901 | 42.042 | 25.007 | 1.01 | 2 | 0 | 61.448 | 57.076 | 49.873 | 17.791 | 0 | 0 | 48.636 | 39.291 | [5 empty] | 0 | 16.06 | 15 | 6.3023 | 5.9154 | 3.8458 | 3.5294 | 2.386 | 37.8596
2006-03-12 | 6:19 | 1 | 15.641 | 0 | 6 | 1 | 58.107 | 58.646 | 43.051 | 43.262 | 42.886 | 24.908 | 1.11 | 1 | 0 | 61.291 | 57.008 | 49.897 | 17.715 | 0 | 0 | 48.59 | 39.033 | [5 empty] | 15.641 | 14.845 | 16 | 6.2732 | 5.8878 | 3.8446 | 3.5294 | 2.3583 | 37.5941
2006-03-12 | 6:20 | 0 | 15.616 | 0 | 6 | 0 | 58.242 | 58.801 | 43.733 | 44.295 | 43.709 | 24.982 | 1.059 | 2 | 0 | 61.202 | 57.053 | 49.92 | 17.74 | 0 | 0 | 48.59 | 38.82 | [5 empty] | 0 | 13.947 | 0 | 6.288 | 5.9019 | 3.8452 | 3.5294 | 2.3725 | 37.7298
2006-03-12 | 6:21 | 0 | 15.676 | 0 | 6 | 0 | 58.183 | 58.968 | 44.47 | 44.883 | 44.283 | 25.087 | 1.273 | 1 | 0 | 61.211 | 57.062 | 49.974 | 17.751 | 0 | 0 | 48.667 | 38.712 | [5 empty] | 0 | 13.3 | 1 | 6.2257 | 5.8426 | 6.3133 | 6 | -0.15737 | -2.5277
2006-03-12 | 6:22 | 1 | 15.666 | 0 | 6 | 0 | 58.13 | 58.913 | 44.897 | 45.334 | 44.415 | 25.151 | 1.059 | 1 | 0 | 61.044 | 57.03 | 50.011 | 17.766 | 0 | 0 | 48.657 | 38.444 | [5 empty] | 15.666 | 12.796 | 2 | 6.288 | 5.9019 | 6.3158 | 6 | -0.098131 | -1.5606
2006-03-12 | 6:23 | 0 | 15.651 | 0 | 6 | 0 | 58.139 | 58.879 | 45.068 | 45.639 | 44.907 | 25.087 | 1.146 | 2 | 0 | 60.965 | 57.062 | 50.135 | 17.776 | 0 | 0 | 48.69 | 38.337 | [5 empty] | 0 | 12.5 | 3 | 6.2627 | 5.8778 | 6.3148 | 6 | -0.12221 | -1.9514
2006-03-12 | 6:24 | 0 | 15.676 | 1 | 6 | 0 | 58.071 | 58.813 | 45.112 | 45.847 | 44.816 | 25.186 | 0.969 | 1 | 0 | 60.873 | 57.085 | 50.135 | 17.751 | 0 | 0 | 48.667 | 38.172 | [5 empty] | 0 | 12.224 | 4 | 6.3142 | 5.9268 | 6.3169 | 6 | -0.073219 | -1.1596
2006-03-12 | 6:25 | 1 | 15.641 | 0 | 6 | 0 | 57.884 | 58.712 | 45.516 | 45.952 | 44.622 | 25.102 | 0.958 | 1 | 0 | 60.752 | 57.03 | 50.172 | 17.766 | 0 | 0 | 48.634 | 37.997 | [5 empty] | 15.641 | 11.932 | 5 | 6.3174 | 5.9298 | 6.317 | 6 | -0.070174 | -1.1108
2006-03-12 | 6:26 | 0 | 15.676 | 0 | 6 | 0 | 57.781 | 58.543 | 45.525 | 46.146 | 44.953 | 25.137 | 1.17 | 1 | 0 | 60.695 | 57.085 | 50.205 | 17.776 | 0 | 0 | 48.69 | 37.866 | [5 empty] | 0 | 11.635 | 6 | 6.2557 | 5.8711 | 6.3145 | 6 | -0.12886 | -2.0598
2006-03-12 | 6:27 | 0 | 15.641 | 0 | 6 | 0 | 57.904 | 58.443 | 45.492 | 46.272 | 44.575 | 25.173 | 0.83 | 1 | 0 | 60.595 | 57.03 | 50.172 | 17.74 | 0 | 0 | 48.634 | 37.669 | [5 empty] | 0 | 11.632 | 7 | 6.3547 | 5.9653 | 6.3185 | 6 | -0.034744 | -0.54674
2006-03-12 | 6:28 | 1 | 15.676 | 0 | 6 | 0 | 57.802 | 58.429 | 45.686 | 46.351 | 44.93 | 25.186 | 1.146 | 1 | 0 | 60.561 | 57.062 | 50.249 | 17.751 | 0 | 0 | 48.667 | 37.562 | [5 empty] | 15.676 | 11.451 | 8 | 6.2627 | 5.8778 | 6.3148 | 6 | -0.12221 | -1.9514
2006-03-12 | 6:29 | 0 | 15.641 | 0 | 6 | 1 | 57.838 | 58.555 | 45.607 | 46.319 | 45.079 | 25.247 | 1.007 | 1 | 0 | 60.483 | 57.03 | 50.216 | 17.715 | 0 | 0 | 48.795 | 37.411 | [5 empty] | 0 | 11.519 | 9 | 6.3032 | 5.9163 | 6.3164 | 6 | -0.083738 | -1.3285
2006-03-12 | 6:30 | 0 | 15.616 | 0 | 6 | 0 | 57.815 | 58.511 | 45.768 | 46.365 | 45.012 | 25.342 | 0.958 | 1 | 0 | 60.394 | 57.053 | 50.331 | 17.715 | 0 | 0 | 48.657 | 37.294 | [5 empty] | 0 | 11.45 | 0 | 6.3174 | 5.9298 | 6.317 | 6 | -0.070174 | -1.1108
2006-03-12 | 6:31 | 1 | 15.616 | 0 | 6 | 0 | 57.77 | 58.466 | 45.745 | 46.386 | 44.484 | 25.342 | 1.033 | 1 | 0 | 60.394 | 57.076 | 50.24 | 17.69 | 0 | 0 | 48.657 | 37.174 | [5 empty] | 15.616 | 11.384 | 1 | 6.2956 | 5.9091 | 5.3161 | 5 | 0.90907 | 14.4397
2006-03-12 | 6:32 | 0 | 15.616 | 0 | 6 | 0 | 57.793 | 58.443 | 45.997 | 46.503 | 45.334 | 25.367 | 1.033 | 1 | 0 | 60.282 | 57.03 | 50.24 | 17.74 | 0 | 0 | 48.657 | 37.033 | [5 empty] | 0 | 11.29 | 2 | 6.2956 | 5.9091 | 5.3161 | 5 | 0.90907 | 14.4397
2006-03-12 | 6:33 | 0 | 15.616 | 1 | 6 | 0 | 57.726 | 58.42 | 45.906 | 46.571 | 44.942 | 25.318 | 0.958 | 1 | 0 | 60.237 | 57.008 | 50.263 | 17.715 | 0 | 0 | 48.657 | 36.964 | [5 empty] | 0 | 11.155 | 3 | 6.3174 | 5.9298 | 5.317 | 5 | 0.92983 | 14.7184
2006-03-12 | 6:34 | 1 | 15.641 | 0 | 6 | 0 | 57.726 | 58.397 | 46.113 | 46.571 | 45.31 | 25.463 | 0.982 | 1 | 0 | 60.282 | 57.008 | 50.24 | 17.74 | 0 | 0 | 48.657 | 36.847 | [5 empty] | 15.641 | 11.155 | 4 | 6.3104 | 5.9232 | 5.3167 | 5 | 0.92318 | 14.6294
2006-03-12 | 6:35 | 0 | 15.641 | 0 | 6 | 0 | 57.77 | 58.377 | 46.113 | 46.662 | 45.126 | 25.342 | 1.085 | 1 | 0 | 60.17 | 57.03 | 50.286 | 17.74 | 0 | 0 | 48.634 | 36.775 | [5 empty] | 0 | 11.108 | 5 | 6.2804 | 5.8947 | 5.3155 | 5 | 0.89467 | 14.2454
2006-03-12 | 6:36 | 0 | 15.714 | 0 | 6 | 0 | 57.749 | 58.397 | 46.134 | 46.732 | 45.149 | 25.463 | 1.007 | 1 | 0 | 60.17 | 57.053 | 50.354 | 17.766 | 0 | 0 | 48.657 | 36.682 | [5 empty] | 0 | 11.017 | 6 | 6.3032 | 5.9163 | 5.3164 | 5 | 0.91626 | 14.5366
2006-03-12 | 6:37 | 1 | 15.616 | 0 | 6 | 0 | 57.815 | 58.532 | 46.228 | 46.846 | 45.355 | 25.561 | 0.958 | 1 | 0 | 60.17 | 57.053 | 50.24 | 17.791 | 0 | 0 | 48.634 | 36.612 | [5 empty] | 15.616 | 10.969 | 7 | 6.3174 | 5.9298 | 5.317 | 5 | 0.92983 | 14.7184
2006-03-12 | 6:38 | 0 | 15.641 | 0 | 6 | 0 | 57.793 | 58.555 | 46.204 | 46.937 | 44.97 | 25.512 | 0.93 | 1 | 0 | 60.084 | 57.058 | 50.198 | 17.791 | 0 | 0 | 48.683 | 36.567 | [5 empty] | 0 | 10.856 | 8 | 6.3256 | 5.9376 | 5.3173 | 5 | 0.93758 | 14.822
2006-03-12 | 6:39 | 0 | 15.661 | 0 | 6 | 0 | 57.793 | 58.489 | 46.386 | 47.098 | 45.033 | 25.531 | 1.054 | 1 | 0 | 60.125 | 57.076 | 50.307 | 17.836 | 0 | 0 | 48.681 | 36.514 | [5 empty] | 0 | 10.695 | 9 | 6.2895 | 5.9033 | 5.3159 | 5 | 0.90325 | 14.3613
2006-03-12 | 6:40 | 1 | 15.687 | 0 | 6 | 0 | 57.77 | 58.511 | 46.501 | 47.028 | 44.781 | 25.605 | 1.054 | 1 | 0 | 60.102 | 57.099 | 50.378 | 17.761 | 0 | 0 | 48.681 | 36.445 | [5 empty] | 15.687 | 10.742 | 10 | 6.2895 | 5.9033 | 5.3159 | 5 | 0.90325 | 14.3613
2006-03-12 | 6:41 | 0 | 15.654 | 0 | 6 | 1 | 57.809 | 58.436 | 46.426 | 47.159 | 44.75 | 25.499 | 1.069 | 1 | 0 | 60.052 | 57.024 | 50.371 | 17.728 | 0 | 0 | 48.674 | 36.32 | [5 empty] | 0 | 10.65 | 11 | 6.2851 | 5.8991 | 5.3157 | 5 | 0.8991 | 14.3053
2006-03-12 | 6:42 | 0 | 15.712 | 1 | 6 | 0 | 57.793 | 58.466 | 46.638 | 47.189 | 45.217 | 25.531 | 1.128 | 1 | 0 | 60.081 | 57.03 | 50.286 | 17.761 | 0 | 0 | 48.704 | 36.234 | [5 empty] | 0 | 10.604 | 0 | 6.2679 | 5.8828 | 5.315 | 5 | 0.88277 | 14.0839
2006-03-12 | 6:43 | 0 | 15.687 | 0 | 6 | 0 | 57.793 | 58.466 | 46.708 | 47.213 | 44.988 | 25.605 | 1.154 | 0 | 0 | 60.059 | 57.076 | 50.378 | 17.786 | 0 | 0 | 48.681 | 36.115 | [5 empty] | 0 | 10.58 | 1 | 6.2604 | 5.8756 | 5.3147 | 5 | 0.87557 | 13.986
2006-03-12 | 6:44 | 1 | 15.687 | 0 | 6 | 0 | 57.927 | 58.489 | 46.846 | 47.488 | 45.264 | 25.605 | 1.154 | 1 | 0 | 60.036 | 57.053 | 50.307 | 17.786 | 0 | 0 | 48.725 | 36.093 | [5 empty] | 15.687 | 10.439 | 2 | 6.2604 | 5.8756 | 5.3147 | 5 | 0.87557 | 13.986
2006-03-12 | 6:45 | 0 | 15.661 | 0 | 6 | 0 | 57.77 | 58.466 | 46.823 | 47.441 | 45.103 | 25.629 | 1.079 | 1 | 0 | 60.013 | 57.076 | 50.331 | 17.859 | 0 | 0 | 48.681 | 36.021 | [5 empty] | 0 | 10.329 | 3 | 6.2822 | 5.8963 | 5.3156 | 5 | 0.89633 | 14.2678
2006-03-12 | 6:46 | 0 | 15.687 | 0 | 6 | 0 | 57.904 | 58.511 | 46.799 | 47.35 | 45.012 | 25.629 | 1.103 | 1 | 0 | 60.013 | 57.053 | 50.24 | 17.786 | 0 | 0 | 48.704 | 35.904 | [5 empty] | 0 | 10.554 | 4 | 6.2752 | 5.8897 | 5.3153 | 5 | 0.88969 | 14.1779
2006-03-12 | 6:47 | 1 | 15.629 | 0 | 6 | 0 | 57.875 | 58.639 | 46.837 | 47.411 | 45.096 | 25.622 | 1.069 | 1 | 0 | 59.96 | 57.046 | 50.347 | 17.778 | 0 | 0 | 48.65 | 35.825 | [5 empty] | 15.629 | 10.464 | 5 | 6.2851 | 5.8991 | 5.3157 | 5 | 0.8991 | 14.3053
2006-03-12 | 6:48 | 0 | 15.661 | 0 | 6 | 0 | 57.861 | 58.534 | 47.075 | 47.511 | 44.965 | 25.789 | 1.095 | 1 | 0 | 59.96 | 57.024 | 50.256 | 17.753 | 0 | 0 | 48.674 | 35.78 | [5 empty] | 0 | 10.35 | 6 | 6.2775 | 5.8919 | 5.3154 | 5 | 0.8919 | 14.2079
2006-03-12 | 6:49 | 0 | 15.687 | 0 | 6 | 0 | 57.838 | 58.466 | 47.098 | 47.579 | 44.599 | 25.774 | 1.18 | 1 | 0 | 59.967 | 57.053 | 50.263 | 17.811 | 0 | 0 | 48.681 | 35.739 | [5 empty] | 0 | 10.259 | 7 | 6.2528 | 5.8684 | 5.3144 | 5 | 0.86838 | 13.8878
2006-03-12 | 6:50 | 0 | 15.654 | 0 | 6 | 0 | 57.786 | 58.482 | 47.136 | 47.619 | 44.568 | 25.622 | 1.273 | 1 | 0 | 59.938 | 57.001 | 50.371 | 17.728 | 0 | 0 | 48.627 | 35.684 | [5 empty] | 0 | 10.167 | 8 | 6.2257 | 5.8426 | 5.3133 | 5 | 0.84263 | 13.5348
2006-03-12 | 6:51 | 1 | 15.687 | 1 | 6 | 0 | 57.793 | 58.489 | 47.257 | 47.693 | 44.224 | 25.725 | 1.306 | 1 | 0 | 59.947 | 57.008 | 50.401 | 17.786 | 0 | 0 | 48.657 | 35.67 | [5 empty] | 15.687 | 10.1 | 9 | 6.2161 | 5.8335 | 5.3129 | 5 | 0.8335 | 13.4087
2006-03-12 | 6:52 | 0 | 15.687 | 0 | 6 | 0 | 57.793 | 58.466 | 47.441 | 47.878 | 44.013 | 25.725 | 1.407 | 0 | 0 | 59.901 | 57.008 | 50.331 | 17.811 | 0 | 0 | 48.681 | 35.622 | [5 empty] | 0 | 9.915 | 10 | 6.1867 | 5.8055 | 5.3117 | 5 | 0.80554 | 13.0206
2006-03-12 | 6:53 | 0 | 15.629 | 0 | 5 | 1 | 57.74 | 58.436 | 47.136 | 47.824 | 44.522 | 25.644 | 1.298 | 1 | 0 | 59.894 | 56.957 | 50.3 | 17.728 | 0 | 0 | 48.65 | 35.543 | [5 empty] | 0 | 9.916 | 11 | 6.2184 | 5.8357 | 5.313 | 5 | 0.83571 | 13.4393
2006-03-12 | 6:54 | 1 | 15.661 | 0 | 6 | 0 | 57.77 | 58.489 | 47.143 | 47.901 | 44.037 | 25.75 | 1.28 | 1 | 0 | 59.901 | 57.03 | 50.286 | 17.811 | 0 | 0 | 48.657 | 35.529 | [5 empty] | 15.661 | 9.869 | 0 | 6.2237 | 5.8407 | 5.3132 | 5 | 0.8407 | 13.5081
2006-03-12 | 6:55 | 0 | 15.661 | 0 | 6 | 0 | 57.704 | 58.42 | 47.236 | 47.763 | 43.896 | 25.821 | 1.358 | 1 | 0 | 59.924 | 57.008 | 50.445 | 17.811 | 0 | 0 | 48.657 | 35.457 | [5 empty] | 0 | 9.941 | 1 | 6.201 | 5.8191 | 4.9277 | 4.6154 | 1.2037 | 19.4119
2006-03-12 | 6:56 | 0 | 15.629 | 0 | 6 | 0 | 57.786 | 58.459 | 47.206 | 47.871 | 43.934 | 25.813 | 1.399 | 1 | 0 | 59.894 | 56.978 | 50.347 | 17.803 | 0 | 0 | 48.627 | 35.38 | [5 empty] | 0 | 9.915 | 2 | 6.189 | 5.8078 | 4.9272 | 4.6154 | 1.1924 | 19.266
2006-03-12 | 6:57 | 0 | 15.654 | 0 | 6 | 0 | 57.831 | 58.436 | 47.32 | 47.777 | 43.958 | 25.958 | 1.373 | 1 | 0 | 59.894 | 56.957 | 50.277 | 17.728 | 0 | 0 | 48.65 | 35.309 | [5 empty] | 0 | 10.054 | 3 | 6.1966 | 5.815 | 4.9275 | 4.6154 | 1.1996 | 19.3586
2006-03-12 | 6:58 | 1 | 15.661 | 0 | 6 | 0 | 57.815 | 58.534 | 47.236 | 47.808 | 43.611 | 25.99 | 1.409 | 0 | 0 | 59.899 | 56.985 | 50.445 | 17.786 | 0 | 0 | 48.632 | 35.292 | [5 empty] | 15.661 | 10.007 | 4 | 6.1861 | 5.805 | 4.9271 | 4.6154 | 1.1896 | 19.2303
2006-03-12 | 6:59 | 0 | 15.599 | 0 | 5 | 0 | 57.756 | 58.429 | 47.152 | 47.726 | 44.116 | 25.904 | 1.394 | 1 | 0 | 59.842 | 56.95 | 50.27 | 17.773 | 0 | 0 | 48.597 | 35.184 | [5 empty] | 0 | 10.03 | 5 | 6.1905 | 5.8091 | 4.9272 | 4.6154 | 1.1938 | 19.2838
2006-03-12 | 7:00 | 0 | 15.624 | 1 | 6 | 0 | 57.779 | 58.518 | 47.152 | 47.887 | 43.365 | 26.169 | 1.42 | 1 | 0 | 59.887 | 56.928 | 50.27 | 17.773 | 0 | 0 | 48.597 | 35.139 | [5 empty] | 0 | 9.892 | 6 | 6.1829 | 5.8019 | 4.9269 | 4.6154 | 1.1866 | 19.191
2006-03-12 | 7:01 | 0 | 15.634 | 0 | 6 | 0 | 57.788 | 58.416 | 47.231 | 47.85 | 43.963 | 25.987 | 1.381 | 1 | 0 | 59.828 | 56.937 | 50.396 | 17.733 | 0 | 0 | 48.606 | 35.172 | [5 empty] | 0 | 9.938 | 7 | 6.1943 | 5.8127 | 4.9274 | 4.6154 | 1.1974 | 19.3301
2006-03-12 | 7:02 | 1 | 15.659 | 0 | 6 | 0 | 57.856 | 58.372 | 47.276 | 47.896 | 43.963 | 26.012 | 1.456 | 1 | 0 | 59.828 | 56.937 | 50.35 | 17.783 | 0 | 0 | 48.653 | 35.124 | [5 empty] | 15.659 | 9.96 | 8 | 6.1724 | 5.792 | 4.9265 | 4.6154 | 1.1766 | 19.0621
2006-03-12 | 7:03 | 0 | 15.634 | 0 | 6 | 0 | 57.745 | 58.395 | 47.255 | 47.92 | 44.708 | 26.034 | 1.381 | 1 | 0 | 59.851 | 57.003 | 50.326 | 17.808 | 0 | 0 | 48.606 | 35.055 | [5 empty] | 0 | 9.825 | 9 | 6.1943 | 5.8127 | 4.9274 | 4.6154 | 1.1974 | 19.3301
2006-03-12 | 7:04 | 0 | 15.599 | 0 | 6 | 0 | 57.733 | 58.34 | 47.175 | 47.817 | 44.212 | 25.953 | 1.394 | 1 | 0 | 59.796 | 56.928 | 50.226 | 17.773 | 0 | 0 | 48.597 | 35.022 | [5 empty] | 0 | 9.916 | 10 | 6.1905 | 5.8091 | 4.9272 | 4.6154 | 1.1938 | 19.2838
2006-03-12 | 7:05 | 1 | 15.599 | 0 | 5 | 0 | 57.756 | 58.363 | 47.175 | 47.749 | 44.329 | 25.953 | 1.445 | 1 | 0 | 59.796 | 56.905 | 50.387 | 17.773 | 0 | 0 | 48.573 | 34.998 | [5 empty] | 15.599 | 10.007 | 11 | 6.1756 | 5.795 | 4.9266 | 4.6154 | 1.1796 | 19.1016
2006-03-12 | 7:06 | 0 | 15.659 | 0 | 6 | 1 | 57.811 | 58.507 | 47.322 | 47.803 | 45.534 | 26.083 | 1.456 | 1 | 0 | 59.874 | 56.937 | 50.303 | 17.808 | 0 | 0 | 48.629 | 34.983 | [5 empty] | 0 | 10.008 | 12 | 6.1724 | 5.792 | 4.9265 | 4.6154 | 1.1766 | 19.0621
2006-03-12 | 7:07 | 0 | 15.624 | 0 | 6 | 0 | 57.802 | 58.406 | 47.29 | 47.749 | 45.203 | 26.049 | 1.494 | 0 | 0 | 59.796 | 56.905 | 50.249 | 17.748 | 0 | 0 | 48.597 | 34.926 | [5 empty] | 0 | 10.053 | 0 | 6.1613 | 5.7815 | 4.9261 | 4.6154 | 1.1661 | 18.9257
2006-03-12 | 7:08 | 0 | 15.649 | 0 | 6 | 0 | 57.802 | 58.452 | 47.108 | 47.817 | 44.837 | 26.169 | 1.623 | 1 | 0 | 59.776 | 56.971 | 50.249 | 17.773 | 0 | 0 | 48.573 | 34.88 | [5 empty] | 0 | 9.985 | 1 | 6.1238 | 5.7458 | 4.9245 | 4.6154 | 1.1304 | 18.4587
2006-03-12 | 7:09 | 1 | 15.659 | 1 | 6 | 0 | 57.879 | 58.461 | 47.185 | 47.803 | 45.464 | 25.987 | 1.556 | 1 | 0 | 59.808 | 56.891 | 50.326 | 17.783 | 0 | 0 | 48.606 | 34.89 | [5 empty] | 15.659 | 10.076 | 2 | 6.1433 | 5.7643 | 4.9253 | 4.6154 | 1.1489 | 18.7019
2006-03-12 | 7:10 | 0 | 15.649 | 0 | 5 | 0 | 57.891 | 58.384 | 47.222 | 47.679 | 45.754 | 25.904 | 1.319 | 1 | 0 | 59.776 | 56.905 | 50.226 | 17.748 | 0 | 0 | 48.573 | 34.833 | [5 empty] | 0 | 10.212 | 3 | 6.2123 | 5.8299 | 4.9281 | 4.6154 | 1.2145 | 19.5502
2006-03-12 | 7:11 | 0 | 15.624 | 0 | 6 | 0 | 57.802 | 58.498 | 47.152 | 47.656 | 44.743 | 25.929 | 1.293 | 1 | 0 | 59.753 | 56.859 | 50.249 | 17.723 | 0 | 0 | 48.597 | 34.809 | [5 empty] | 0 | 10.146 | 4 | 6.2199 | 5.8371 | 4.9284 | 4.6154 | 1.2217 | 19.6421
2006-03-12 | 7:12 | 1 | 15.599 | 0 | 6 | 0 | 57.779 | 58.475 | 47.152 | 47.679 | 45.294 | 25.929 | 1.242 | 1 | 0 | 59.776 | 56.859 | 50.226 | 17.748 | 0 | 0 | 48.573 | 34.785 | [5 empty] | 15.599 | 10.1 | 5 | 6.2347 | 5.8512 | 4.929 | 4.6154 | 1.2358 | 19.8217
2006-03-12 | 7:13 | 0 | 15.624 | 0 | 6 | 0 | 57.802 | 58.429 | 47.129 | 47.726 | 44.652 | 26 | 1.319 | 1 | 0 | 59.753 | 56.905 | 50.34 | 17.748 | 0 | 0 | 48.573 | 34.715 | [5 empty] | 0 | 10.076 | 6 | 6.2123 | 5.8299 | 4.9281 | 4.6154 | 1.2145 | 19.5502
2006-03-12 | 7:14 | 0 | 15.624 | 0 | 6 | 0 | 57.802 | 58.498 | 47.108 | 47.703 | 44.585 | 25.978 | 1.216 | 1 | 0 | 59.73 | 56.882 | 50.249 | 17.698 | 0 | 0 | 48.552 | 34.691 | [5 empty] | 0 | 10.099 | 7 | 6.2423 | 5.8584 | 4.9293 | 4.6154 | 1.243 | 19.913
2006-03-12 | 7:15 | 0 | 15.649 | 0 | 6 | 0 | 57.824 | 58.452 | 47.061 | 47.77 | 44.35 | 25.904 | 1.242 | 0 | 0 | 59.73 | 56.905 | 50.202 | 17.748 | 0 | 0 | 48.506 | 34.691 | [5 empty] | 0 | 10.054 | 8 | 6.2347 | 5.8512 | 4.929 | 4.6154 | 1.2358 | 19.8217
2006-03-12 | 7:16 | 1 | 15.624 | 0 | 5 | 0 | 57.756 | 58.429 | 47.175 | 47.656 | 45.25 | 25.929 | 1.394 | 1 | 0 | 59.753 | 56.836 | 50.317 | 17.748 | 0 | 0 | 48.459 | 34.668 | [5 empty] | 15.624 | 10.1 | 9 | 6.1905 | 5.8091 | 4.9272 | 4.6154 | 1.1938 | 19.2838
2006-03-12 | 7:17 | 0 | 15.599 | 0 | 6 | 0 | 57.779 | 58.429 | 47.108 | 47.703 | 44.928 | 26.049 | 1.293 | 1 | 0 | 59.776 | 56.859 | 50.226 | 17.773 | 0 | 0 | 48.436 | 34.622 | [5 empty] | 0 | 10.076 | 10 | 6.2199 | 5.8371 | 4.9284 | 4.6154 | 1.2217 | 19.6421
2006-03-12 | 7:18 | 0 | 15.624 | 1 | 6 | 0 | 57.802 | 58.452 | 47.129 | 47.612 | 44.629 | 25.953 | 1.316 | 1 | 0 | 59.732 | 56.861 | 50.205 | 17.796 | 0 | 0 | 48.391 | 34.622 | [5 empty] | 0 | 10.19 | 11 | 6.2132 | 5.8307 | 4.9282 | 4.6154 | 1.2153 | 19.5608
2006-03-12 | 7:19 | 0 | 15.654 | 0 | 6 | 1 | 57.72 | 58.436 | 47.068 | 47.619 | 44.545 | 25.911 | 1.399 | 1 | 0 | 59.76 | 56.843 | 50.371 | 17.803 | 0 | 0 | 48.352 | 34.581 | [5 empty] | 0 | 10.101 | 12 | 6.189 | 5.8078 | 4.9272 | 4.6154 | 1.1924 | 19.266
2006-03-12 | 7:20 | 1 | 15.654 | 0 | 6 | 0 | 57.763 | 58.436 | 47.045 | 47.572 | 44.636 | 25.911 | 1.373 | 1 | 0 | 59.737 | 56.866 | 50.233 | 17.803 | 0 | 0 | 48.352 | 34.534 | [5 empty] | 15.654 | 10.191 | 0 | 6.1966 | 5.815 | 4.9275 | 4.6154 | 1.1996 | 19.3586
2006-03-12 | 7:21 | 0 | 15.654 | 0 | 6 | 0 | 57.809 | 58.39 | 46.998 | 47.686 | 45.439 | 25.862 | 1.45 | 1 | 0 | 59.737 | 56.8 | 50.233 | 17.753 | 0 | 0 | 48.305 | 34.51 | [5 empty] | 0 | 10.123 | 1 | 6.1742 | 5.7936 | 4.9266 | 4.6154 | 1.1783 | 19.0837
2006-03-12 | 7:22 | 0 | 15.654 | 0 | 5 | 0 | 57.674 | 58.301 | 46.998 | 47.572 | 45.187 | 25.862 | 1.577 | 1 | 0 | 59.714 | 56.843 | 50.324 | 17.753 | 0 | 0 | 48.261 | 34.486 | [5 empty] | 0 | 10.102 | 2 | 6.1372 | 5.7585 | 4.9251 | 4.6154 | 1.1431 | 18.6259
2006-03-12 | 7:23 | 1 | 15.679 | 0 | 6 | 0 | 57.651 | 58.279 | 46.93 | 47.458 | 44.659 | 25.982 | 1.45 | 0 | 0 | 59.714 | 56.889 | 50.324 | 17.778 | 0 | 0 | 48.237 | 34.486 | [5 empty] | 15.679 | 10.193 | 3 | 6.1742 | 5.7936 | 4.9266 | 4.6154 | 1.1783 | 19.0837
2006-03-12 | 7:24 | 0 | 15.679 | 0 | 6 | 0 | 57.651 | 58.279 | 46.884 | 47.434 | 45.187 | 25.862 | 1.628 | 1 | 0 | 59.782 | 56.866 | 50.233 | 17.851 | 0 | 0 | 48.191 | 34.44 | [5 empty] | 0 | 10.217 | 4 | 6.1223 | 5.7444 | 4.9245 | 4.6154 | 1.129 | 18.4405
2006-03-12 | 7:25 | 0 | 15.654 | 0 | 6 | 0 | 57.763 | 58.39 | 46.837 | 47.502 | 45.096 | 25.958 | 1.45 | 1 | 0 | 59.714 | 56.866 | 50.3 | 17.803 | 0 | 0 | 48.191 | 34.392 | [5 empty] | 0 | 10.261 | 5 | 6.1742 | 5.7936 | 4.9266 | 4.6154 | 1.1783 | 19.0837
2006-03-12 | 7:26 | 0 | 15.654 | 0 | 6 | 0 | 57.74 | 58.301 | 46.699 | 47.434 | 45.576 | 25.887 | 1.906 | 1 | 0 | 59.691 | 56.8 | 50.233 | 17.778 | 0 | 0 | 48.191 | 34.392 | [5 empty] | 0 | 10.306 | 6 | 6.0414 | 5.6674 | 4.9212 | 4.6154 | 1.052 | 17.4138
2006-03-12 | 7:27 | 1 | 15.654 | 1 | 6 | 0 | 57.74 | 58.347 | 46.769 | 47.32 | 45.644 | 25.982 | 1.677 | 1 | 0 | 59.691 | 56.8 | 50.256 | 17.753 | 0 | 0 | 48.191 | 34.416 | [5 empty] | 15.654 | 10.42 | 7 | 6.1081 | 5.7308 | 4.9239 | 4.6154 | 1.1154 | 18.2615
2006-03-12 | 7:28 | 0 | 15.654 | 0 | 6 | 0 | 57.786 | 58.39 | 46.699 | 47.364 | 45.644 | 25.911 | 1.729 | 1 | 0 | 59.691 | 56.8 | 50.347 | 17.753 | 0 | 0 | 48.123 | 34.416 | [5 empty] | 0 | 10.422 | 8 | 6.0929 | 5.7164 | 4.9233 | 4.6154 | 1.101 | 18.0706
2006-03-12 | 7:29 | 0 | 15.654 | 0 | 5 | 0 | 57.786 | 58.37 | 46.678 | 47.297 | 46.265 | 25.862 | 1.525 | 1 | 0 | 59.691 | 56.823 | 50.3 | 17.753 | 0 | 0 | 48.123 | 34.369 | [5 empty] | 0 | 10.489 | 9 | 6.1523 | 5.7729 | 4.9257 | 4.6154 | 1.1575 | 18.814
2006-03-12 | 7:30 | 1 | 15.679 | 0 | 6 | 0 | 57.809 | 58.413 | 46.816 | 47.273 | 46.013 | 25.933 | 1.829 | 1 | 0 | 59.714 | 56.8 | 50.163 | 17.778 | 0 | 0 | 48.167 | 34.345 | [5 empty] | 15.679 | 10.536 | 10 | 6.0638 | 5.6887 | 4.9221 | 4.6154 | 1.0733 | 17.7009
2006-03-12 | 7:31 | 0 | 15.687 | 0 | 6 | 0 | 57.793 | 58.489 | 46.799 | 47.28 | 46.225 | 25.894 | 2.015 | 1 | 0 | 59.721 | 56.807 | 50.286 | 17.836 | 0 | 0 | 48.153 | 34.33 | [5 empty] | 0 | 10.513 | 11 | 6.0096 | 5.6372 | 4.9199 | 4.6154 | 1.0219 | 17.0038
2006-03-12 | 7:32 | 0 | 15.679 | 0 | 6 | 1 | 57.809 | 58.436 | 46.769 | 47.273 | 46.104 | 25.958 | 1.906 | 1 | 0 | 59.671 | 56.8 | 50.392 | 17.927 | 0 | 0 | 48.146 | 34.275 | [5 empty] | 0 | 10.536 | 12 | 6.0414 | 5.6674 | 4.9212 | 4.6154 | 1.052 | 17.4138
2006-03-12 | 7:33 | 0 | 15.654 | 0 | 6 | 0 | 57.786 | 58.459 | 46.631 | 47.273 | 46.151 | 25.887 | 1.981 | 0 | 0 | 59.648 | 56.777 | 50.233 | 17.778 | 0 | 0 | 48.1 | 34.275 | [5 empty] | 0 | 10.513 | 0 | 6.0195 | 5.6467 | 4.9203 | 4.6154 | 1.0313 | 17.1321
2006-03-12 | 7:34 | 1 | 15.654 | 0 | 6 | 0 | 57.763 | 58.482 | 46.769 | 47.25 | 45.782 | 25.958 | 2.033 | 1 | 0 | 59.648 | 56.754 | 50.163 | 17.753 | 0 | 0 | 48.123 | 34.299 | [5 empty] | 15.654 | 10.513 | 1 | 6.0044 | 5.6323 | 4.9197 | 4.6154 | 1.0169 | 16.9356
2006-03-12 | 7:35 | 0 | 15.654 | 0 | 6 | 0 | 57.831 | 58.436 | 46.746 | 47.364 | 45.576 | 25.887 | 1.906 | 1 | 0 | 59.648 | 56.731 | 50.277 | 17.778 | 0 | 0 | 48.1 | 34.345 | [5 empty] | 0 | 10.467 | 2 | 6.0414 | 5.6674 | 4.9212 | 4.6154 | 1.052 | 17.4138
2006-03-12 | 7:36 | 0 | 15.629 | 1 | 6 | 0 | 57.74 | 58.436 | 46.792 | 47.273 | 46.265 | 25.958 | 2.107 | 1 | 0 | 59.671 | 56.731 | 50.186 | 17.753 | 0 | 0 | 48.1 | 34.321 | [5 empty] | 0 | 10.467 | 3 | 5.9828 | 5.6118 | 4.9188 | 4.6154 | 0.9964 | 16.6543
2006-03-12 | 7:37 | 1 | 15.687 | 0 | 5 | 0 | 57.815 | 58.466 | 46.776 | 47.35 | 45.836 | 26.039 | 2.218 | 1 | 0 | 59.721 | 56.807 | 50.193 | 17.811 | 0 | 0 | 48.107 | 34.33 | [5 empty] | 15.687 | 10.465 | 4 | 5.9505 | 5.5811 | 4.9175 | 4.6154 | 0.96567 | 16.2284
2006-03-12 | 7:38 | 0 | 15.654 | 0 | 6 | 0 | 57.763 | 58.436 | 46.769 | 47.388 | 46.309 | 25.933 | 2.337 | 1 | 0 | 59.6 | 56.729 | 50.139 | 17.803 | 0 | 0 | 48.074 | 34.273 | [5 empty] | 0 | 10.375 | 5 | 5.9159 | 5.5481 | 4.9161 | 4.6154 | 0.93273 | 15.7666
2006-03-12 | 7:39 | 0 | 15.699 | 0 | 6 | 0 | 57.847 | 58.429 | 46.785 | 47.36 | 45.845 | 25.929 | 1.953 | 1 | 0 | 59.641 | 56.727 | 50.158 | 17.798 | 0 | 0 | 48.072 | 34.247 | [5 empty] | 0 | 10.487 | 6 | 6.0277 | 5.6544 | 4.9206 | 4.6154 | 1.039 | 17.2375
2006-03-12 | 7:40 | 0 | 15.639 | 0 | 6 | 0 | 57.726 | 58.397 | 46.708 | 47.418 | 45.721 | 25.894 | 2.169 | 1 | 0 | 59.586 | 56.738 | 50.149 | 17.788 | 0 | 0 | 48.153 | 34.141 | [5 empty] | 0 | 10.308 | 7 | 5.9648 | 5.5946 | 4.9181 | 4.6154 | 0.97924 | 16.417
2006-03-12 | 7:41 | 1 | 15.664 | 0 | 6 | 0 | 57.704 | 58.377 | 46.685 | 47.35 | 45.607 | 25.799 | 2.499 | 1 | 0 | 59.586 | 56.695 | 50.216 | 17.811 | 0 | 0 | 48.039 | 34.165 | [5 empty] | 15.664 | 10.354 | 8 | 5.8687 | 5.5033 | 4.9142 | 4.6154 | 0.88789 | 15.1293
2006-03-12 | 7:42 | 0 | 15.639 | 0 | 6 | 0 | 57.612 | 58.285 | 46.753 | 47.395 | 45.378 | 25.968 | 2.447 | 1 | 0 | 59.609 | 56.695 | 50.079 | 17.811 | 0 | 0 | 48.039 | 34.117 | [5 empty] | 0 | 10.217 | 9 | 5.8838 | 5.5177 | 4.9148 | 4.6154 | 0.90229 | 15.335
2006-03-12 | 7:43 | 0 | 15.639 | 0 | 6 | 0 | 57.635 | 58.285 | 46.891 | 47.327 | 45.17 | 25.992 | 2.499 | 1 | 0 | 59.586 | 56.672 | 50.125 | 17.738 | 0 | 0 | 48.039 | 34.117 | [5 empty] | 0 | 10.308 | 10 | 5.8687 | 5.5033 | 4.9142 | 4.6154 | 0.88789 | 15.1293
2006-03-12 | 7:44 | 1 | 15.639 | 0 | 6 | 0 | 57.635 | 58.285 | 46.799 | 47.28 | 45.355 | 25.943 | 2.321 | 1 | 0 | 59.586 | 56.695 | 50.24 | 17.788 | 0 | 0 | 48.016 | 34.117 | [5 empty] | 15.639 | 10.355 | 11 | 5.9205 | 5.5525 | 4.9163 | 4.6154 | 0.93716 | 15.829
2006-03-12 | 7:45 | 0 | 15.664 | 1 | 5 | 1 | 57.592 | 58.242 | 46.776 | 47.327 | 44.942 | 26.014 | 2.195 | 1 | 0 | 59.563 | 56.672 | 50.149 | 17.811 | 0 | 0 | 48.039 | 34.117 | [5 empty] | 0 | 10.265 | 12 | 5.9572 | 5.5874 | 4.9178 | 4.6154 | 0.97204 | 16.317
2006-03-12 | 7:46 | 0 | 15.664 | 0 | 6 | 0 | 57.681 | 58.263 | 46.799 | 47.327 | 45.056 | 25.919 | 2.396 | 1 | 0 | 59.563 | 56.672 | 50.193 | 17.788 | 0 | 0 | 47.992 | 34.096 | [5 empty] | 0 | 10.354 | 0 | 5.8987 | 5.5318 | 4.9154 | 4.6154 | 0.9164 | 15.5357
2006-03-12 | 7:47 | 0 | 15.614 | 0 | 6 | 0 | 57.546 | 58.242 | 46.799 | 47.257 | 45.56 | 25.943 | 2.522 | 0 | 0 | 59.563 | 56.695 | 50.079 | 17.788 | 0 | 0 | 48.016 | 34.072 | [5 empty] | 0 | 10.289 | 1 | 5.862 | 5.4969 | 5.2985 | 5 | 0.49691 | 8.4768
2006-03-12 | 7:48 | 1 | 15.674 | 0 | 6 | 0 | 57.624 | 58.228 | 46.718 | 47.29 | 45.296 | 25.978 | 2.687 | 1 | 0 | 59.595 | 56.704 | 50.158 | 17.896 | 0 | 0 | 48.002 | 34.105 | [5 empty] | 15.674 | 10.334 | 2 | 5.8139 | 5.4512 | 5.2966 | 5 | 0.45124 | 7.7613
2006-03-12 | 7:49 | 0 | 15.699 | 0 | 6 | 0 | 57.601 | 58.206 | 46.741 | 47.336 | 45.525 | 25.929 | 2.736 | 1 | 0 | 59.573 | 56.658 | 50.181 | 17.773 | 0 | 0 | 48.048 | 34.129 | [5 empty] | 0 | 10.265 | 3 | 5.7997 | 5.4377 | 5.296 | 5 | 0.43768 | 7.5465
2006-03-12 | 7:50 | 0 | 15.664 | 0 | 6 | 0 | 57.523 | 58.219 | 46.776 | 47.257 | 45.264 | 25.919 | 2.321 | 1 | 0 | 59.541 | 56.626 | 50.102 | 17.788 | 0 | 0 | 47.992 | 34.117 | [5 empty] | 0 | 10.266 | 4 | 5.9205 | 5.5525 | 5.3009 | 5 | 0.55255 | 9.3327
2006-03-12 | 7:51 | 1 | 15.664 | 0 | 5 | 0 | 57.592 | 58.196 | 46.753 | 47.28 | 44.713 | 25.87 | 2.599 | 1 | 0 | 59.52 | 56.649 | 50.149 | 17.788 | 0 | 0 | 48.016 | 34.096 | [5 empty] | 15.664 | 10.312 | 5 | 5.8396 | 5.4756 | 5.2976 | 5 | 0.4756 | 8.1444
2006-03-12 | 7:52 | 0 | 15.639 | 0 | 6 | 0 | 57.546 | 58.263 | 46.799 | 47.28 | 44.895 | 25.968 | 2.321 | 1 | 0 | 59.541 | 56.649 | 50.079 | 17.811 | 0 | 0 | 47.992 | 34.048 | [5 empty] | 0 | 10.266 | 6 | 5.9205 | 5.5525 | 5.3009 | 5 | 0.55255 | 9.3327
2006-03-12 | 7:53 | 0 | 15.699 | 0 | 6 | 0 | 57.667 | 58.251 | 46.718 | 47.383 | 45.135 | 25.953 | 2.61 | 1 | 0 | 59.552 | 56.636 | 50.158 | 17.823 | 0 | 0 | 48.025 | 34.081 | [5 empty] | 0 | 10.284 | 7 | 5.8364 | 5.4726 | 5.2975 | 5 | 0.47255 | 8.0967
2006-03-12 | 7:54 | 0 | 15.699 | 1 | 6 | 0 | 57.624 | 58.274 | 46.856 | 47.29 | 45.021 | 26.122 | 2.787 | 1 | 0 | 59.552 | 56.636 | 50.111 | 17.823 | 0 | 0 | 48.048 | 34.058 | [5 empty] | 0 | 10.334 | 8 | 5.7848 | 5.4236 | 5.2954 | 5 | 0.42356 | 7.3219
2006-03-12 | 7:55 | 1 | 15.664 | 0 | 6 | 0 | 57.635 | 58.242 | 46.753 | 47.257 | 44.942 | 26.088 | 2.852 | 1 | 0 | 59.541 | 56.604 | 50.102 | 17.811 | 0 | 0 | 47.992 | 34.024 | [5 empty] | 15.664 | 10.378 | 9 | 5.7659 | 5.4056 | 5.2946 | 5 | 0.40557 | 7.0339
2006-03-12 | 7:56 | 0 | 15.664 | 0 | 6 | 0 | 57.635 | 58.308 | 46.799 | 47.189 | 44.757 | 25.919 | 3.13 | 1 | 0 | 59.52 | 56.583 | 50.055 | 17.763 | 0 | 0 | 48.016 | 34.048 | [5 empty] | 0 | 10.446 | 10 | 5.6849 | 5.3286 | 5.2914 | 5 | 0.32862 | 5.7805
2006-03-12 | 7:57 | 0 | 15.639 | 0 | 5 | 1 | 57.658 | 58.285 | 46.776 | 47.236 | 44.713 | 25.943 | 3.256 | 1 | 0 | 59.497 | 56.626 | 50.079 | 17.788 | 0 | 0 | 47.969 | 33.979 | [5 empty] | 0 | 10.422 | 11 | 5.6483 | 5.2937 | 5.2899 | 5 | 0.29374 | 5.2005
2006-03-12 | 7:58 | 1 | 15.664 | 0 | 6 | 0 | 57.635 | 58.308 | 46.799 | 47.257 | 45.012 | 25.919 | 2.777 | 1 | 0 | 59.495 | 56.558 | 50.1 | 17.788 | 0 | 0 | 47.99 | 34 | [5 empty] | 15.664 | 10.378 | 0 | 5.7877 | 5.4263 | 5.2955 | 5 | 0.42633 | 7.366
2006-03-12 | 7:59 | 0 | 15.661 | 0 | 6 | 0 | 57.453 | 58.192 | 46.75 | 47.301 | 44.55 | 25.99 | 3.104 | 0 | 0 | 59.515 | 56.579 | 50.144 | 17.811 | 0 | 0 | 47.988 | 34.046 | [5 empty] | 0 | 10.152 | 1 | 5.6925 | 5.3358 | 4.9071 | 4.6154 | 0.72043 | 12.6557
2006-03-12 | 8:00 | 0 | 15.626 | 0 | 6 | 0 | 57.309 | 57.982 | 46.832 | 47.29 | 44.517 | 26.1 | 2.638 | 1 | 0 | 59.506 | 56.547 | 50.02 | 17.751 | 0 | 0 | 47.955 | 33.94 | [5 empty] | 0 | 10.019 | 2 | 5.8282 | 5.4648 | 4.9126 | 4.6154 | 0.84942 | 14.5742
2006-03-12 | 8:01 | 0 | 15.661 | 0 | 6 | 0 | 57.206 | 57.945 | 46.774 | 47.301 | 43.987 | 26.012 | 2.445 | 1 | 0 | 59.515 | 56.579 | 50.074 | 17.761 | 0 | 0 | 48.011 | 33.928 | [5 empty] | 0 | 9.905 | 3 | 5.8844 | 5.5182 | 4.9148 | 4.6154 | 0.90284 | 15.3429
2006-03-12 | 8:02 | 1 | 15.687 | 0 | 5 | 0 | 57.272 | 58.014 | 46.75 | 47.322 | 44.197 | 26.036 | 2.852 | 1 | 0 | 59.47 | 56.51 | 50.121 | 17.811 | 0 | 0 | 47.988 | 33.928 | [5 empty] | 15.687 | 9.95 | 4 | 5.7659 | 5.4056 | 4.91 | 4.6154 | 0.79018 | 13.7044
2006-03-12 | 8:03 | 0 | 15.651 | 0 | 6 | 0 | 57.197 | 57.913 | 46.648 | 47.427 | 43.461 | 26.027 | 2.942 | 1 | 0 | 59.438 | 56.501 | 50.065 | 17.776 | 0 | 0 | 47.955 | 33.895 | [5 empty] | 0 | 9.77 | 5 | 5.7397 | 5.3807 | 4.909 | 4.6154 | 0.76527 | 13.3329
2006-03-12 | 8:04 | 0 | 15.687 | 1 | 6 | 0 | 57.206 | 57.767 | 46.727 | 47.208 | 43.774 | 26.085 | 2.749 | 1 | 0 | 59.515 | 56.556 | 50.053 | 17.833 | 0 | 0 | 47.966 | 33.974 | [5 empty] | 0 | 9.998 | 6 | 5.7959 | 5.4341 | 4.9112 | 4.6154 | 0.81869 | 14.1254
2006-03-12 | 8:05 | 0 | 15.601 | 0 | 6 | 0 | 57.106 | 57.824 | 46.648 | 47.175 | 43.977 | 26.196 | 2.816 | 1 | 0 | 59.415 | 56.547 | 50.041 | 17.798 | 0 | 0 | 47.934 | 33.895 | [5 empty] | 0 | 9.931 | 7 | 5.7764 | 5.4155 | 4.9105 | 4.6154 | 0.80015 | 13.852
2006-03-12 | 8:06 | 1 | 15.687 | 0 | 6 | 0 | 57.16 | 57.745 | 46.659 | 47.187 | 43.353 | 26.206 | 2.445 | 1 | 0 | 59.447 | 56.533 | 50.121 | 17.833 | 0 | 0 | 47.943 | 33.952 | [5 empty] | 15.687 | 9.973 | 8 | 5.8844 | 5.5182 | 4.9148 | 4.6154 | 0.90284 | 15.3429
2006-03-12 | 8:07 | 0 | 15.651 | 0 | 5 | 0 | 57.151 | 57.87 | 46.671 | 47.222 | 43.788 | 26.22 | 2.816 | 1 | 0 | 59.415 | 56.547 | 50.02 | 17.798 | 0 | 0 | 47.887 | 33.847 | [5 empty] | 0 | 9.929 | 9 | 5.7764 | 5.4155 | 4.9105 | 4.6154 | 0.80015 | 13.852
2006-03-12 | 8:08 | 0 | 15.709 | 0 | 6 | 0 | 57.138 | 57.811 | 46.613 | 47.278 | 43.752 | 26.23 | 2.723 | 1 | 0 | 59.404 | 56.51 | 50.006 | 17.811 | 0 | 0 | 47.92 | 33.881 | [5 empty] | 0 | 9.86 | 10 | 5.8035 | 5.4413 | 4.9116 | 4.6154 | 0.82589 | 14.231
2006-03-12 | 8:09 | 1 | 15.661 | 0 | 6 | 0 | 57.117 | 57.811 | 46.566 | 47.117 | 43.587 | 26.326 | 2.774 | 1 | 0 | 59.447 | 56.556 | 49.983 | 17.833 | 0 | 0 | 47.92 | 33.881 | [5 empty] | 15.661 | 10 | 11 | 5.7886 | 5.4272 | 4.911 | 4.6154 | 0.81177 | 14.0236
2006-03-12 | 8:10 | 0 | 15.674 | 0 | 6 | 1 | 57.106 | 57.802 | 46.58 | 47.061 | 43.53 | 26.316 | 3.169 | 0 | 0 | 59.395 | 56.478 | 50.041 | 17.798 | 0 | 0 | 47.91 | 33.871 | [5 empty] | 0 | 10.045 | 12 | 5.6736 | 5.3178 | 4.9063 | 4.6154 | 0.70244 | 12.3808
2006-03-12 | 8:11 | 0 | 15.651 | 0 | 5 | 0 | 57.062 | 57.735 | 46.603 | 47.061 | 44.07 | 26.365 | 2.764 | 1 | 0 | 59.415 | 56.501 | 49.95 | 17.776 | 0 | 0 | 47.91 | 33.871 | [5 empty] | 0 | 10.001 | 0 | 5.7915 | 5.4299 | 4.9111 | 4.6154 | 0.81454 | 14.0644
2006-03-12 | 8:12 | 0 | 15.687 | 0 | 6 | 0 | 57.117 | 57.767 | 46.589 | 47.117 | 43.681 | 26.399 | 2.648 | 1 | 0 | 59.404 | 56.51 | 49.96 | 17.786 | 0 | 0 | 47.943 | 33.881 | [5 empty] | 0 | 10 | 1 | 5.8253 | 5.462 | 4.5828 | 4.2857 | 1.1763 | 20.1933
2006-03-12 | 8:13 | 1 | 15.709 | 1 | 6 | 0 | 57.117 | 57.745 | 46.613 | 47.117 | 43.704 | 26.47 | 3.004 | 1 | 0 | 59.426 | 56.51 | 50.006 | 17.833 | 0 | 0 | 47.943 | 33.904 | [5 empty] | 15.709 | 10 | 2 | 5.7216 | 5.3635 | 4.5786 | 4.2857 | 1.0778 | 18.8369
2006-03-12 | 8:14 | 0 | 15.687 | 0 | 6 | 0 | 57.138 | 57.745 | 46.498 | 47.094 | 43.539 | 26.35 | 2.978 | 1 | 0 | 59.381 | 56.533 | 50.074 | 17.811 | 0 | 0 | 47.92 | 33.881 | [5 empty] | 0 | 10.044 | 3 | 5.7292 | 5.3707 | 4.5789 | 4.2857 | 1.085 | 18.9376
2006-03-12 | 8:15 | 0 | 15.661 | 0 | 5 | 0 | 56.871 | 57.834 | 46.636 | 47.255 | 42.929 | 26.399 | 3.053 | 1 | 0 | 59.404 | 56.49 | 50.03 | 17.833 | 0 | 0 | 47.943 | 33.928 | [5 empty] | 0 | 9.616 | 4 | 5.7074 | 5.3499 | 4.578 | 4.2857 | 1.0642 | 18.6463
2006-03-12 | 8:16 | 0 | 15.661 | 0 | 6 | 0 | 56.713 | 57.386 | 46.543 | 47.026 | 42.434 | 26.35 | 3.205 | 1 | 0 | 59.404 | 56.444 | 50.006 | 17.811 | 0 | 0 | 47.92 | 33.904 | [5 empty] | 0 | 9.687 | 5 | 5.6631 | 5.3079 | 4.5762 | 4.2857 | 1.0221 | 18.0491
2006-03-12 | 8:17 | 1 | 15.687 | 0 | 6 | 0 | 56.69 | 57.341 | 46.659 | 47.07 | 42.2 | 26.301 | 3.305 | 1 | 0 | 59.381 | 56.444 | 50.03 | 17.884 | 0 | 0 | 47.873 | 33.881 | [5 empty] | 15.687 | 9.62 | 6 | 5.634 | 5.2802 | 4.575 | 4.2857 | 0.99446 | 17.6511
2006-03-12 | 8:18 | 0 | 15.717 | 0 | 6 | 0 | 56.763 | 57.345 | 46.526 | 47.168 | 42.487 | 26.333 | 3.336 | 1 | 0 | 59.388 | 56.496 | 50.013 | 17.889 | 0 | 0 | 47.927 | 33.933 | [5 empty] | 0 | 9.595 | 7 | 5.625 | 5.2716 | 4.5746 | 4.2857 | 0.98588 | 17.5269
2006-03-12 | 8:19 | 0 | 15.714 | 0 | 5 | 0 | 56.761 | 57.322 | 46.386 | 47.098 | 42.439 | 26.208 | 3.511 | 1 | 0 | 59.385 | 56.471 | 50.172 | 17.886 | 0 | 0 | 47.924 | 33.907 | [5 empty] | 0 | 9.663 | 8 | 5.574 | 5.2232 | 4.5726 | 4.2857 | 0.93744 | 16.8181
2006-03-12 | 8:20 | 0 | 15.684 | 0 | 6 | 0 | 56.69 | 57.272 | 46.405 | 46.956 | 42.458 | 26.277 | 3.784 | 1 | 0 | 59.335 | 56.421 | 50.03 | 17.831 | 0 | 0 | 47.873 | 33.857 | [5 empty] | 0 | 9.734 | 9 | 5.4945 | 5.1476 | 4.5694 | 4.2857 | 0.86187 | 15.6861
2006-03-12 | 8:21 | 1 | 15.684 | 0 | 6 | 0 | 56.757 | 57.295 | 46.223 | 46.933 | 42.623 | 26.132 | 3.936 | 1 | 0 | 59.335 | 56.444 | 49.96 | 17.881 | 0 | 0 | 47.85 | 33.833 | [5 empty] | 15.684 | 9.824 | 10 | 5.4502 | 5.1055 | 4.5676 | 4.2857 | 0.8198 | 15.0416
2006-03-12 | 8:22 | 0 | 15.684 | 1 | 6 | 0 | 56.713 | 57.341 | 46.267 | 46.818 | 43.185 | 26.301 | 3.684 | 1 | 0 | 59.335 | 56.444 | 49.913 | 17.831 | 0 | 0 | 47.873 | 33.809 | [5 empty] | 0 | 9.895 | 11 | 5.5236 | 5.1753 | 4.5705 | 4.2857 | 0.88955 | 16.1046
2006-03-12 | 8:23 | 0 | 15.714 | 0 | 5 | 0 | 56.807 | 57.457 | 46.365 | 46.823 | 43.331 | 26.282 | 3.867 | 1 | 0 | 59.385 | 56.426 | 49.941 | 17.861 | 0 | 0 | 47.901 | 33.861 | [5 empty] | 0 | 9.984 | 12 | 5.4703 | 5.1246 | 4.5684 | 4.2857 | 0.8389 | 15.3355
2006-03-12 | 8:24 | 1 | 15.689 | 0 | 6 | 1 | 56.875 | 57.457 | 46.295 | 46.846 | 43.286 | 26.306 | 4.093 | 1 | 0 | 59.363 | 56.448 | 49.92 | 17.886 | 0 | 0 | 47.901 | 33.861 | [5 empty] | 15.689 | 10.029 | 13 | 5.4045 | 5.0621 | 4.5657 | 4.2857 | 0.77634 | 14.3647
2006-03-12 | 8:25 | 0 | 15.689 | 0 | 6 | 0 | 56.896 | 57.48 | 46.251 | 46.87 | 42.745 | 26.233 | 3.411 | 1 | 0 | 59.319 | 56.38 | 49.964 | 17.839 | 0 | 0 | 47.901 | 33.837 | [5 empty] | 0 | 10.026 | 0 | 5.6031 | 5.2508 | 4.5738 | 4.2857 | 0.96512 | 17.2247
2006-03-12 | 8:26 | 0 | 15.684 | 0 | 5 | 0 | 56.757 | 57.453 | 46.291 | 46.704 | 43.044 | 26.252 | 3.303 | 1 | 0 | 59.312 | 56.398 | 49.983 | 17.808 | 0 | 0 | 47.826 | 33.761 | [5 empty] | 0 | 10.053 | 1 | 5.6346 | 5.2807 | 4.9047 | 4.6154 | 0.66534 | 11.8083
2006-03-12 | 8:27 | 0 | 15.689 | 0 | 6 | 0 | 56.875 | 57.457 | 46.386 | 46.799 | 43.262 | 26.208 | 3.207 | 1 | 0 | 59.296 | 56.403 | 49.92 | 17.886 | 0 | 0 | 47.854 | 33.744 | [5 empty] | 0 | 10.076 | 2 | 5.6625 | 5.3073 | 4.9058 | 4.6154 | 0.69192 | 12.2193
2006-03-12 | 8:28 | 1 | 15.684 | 0 | 6 | 0 | 56.713 | 57.407 | 46.244 | 46.68 | 43.327 | 26.203 | 3.707 | 1 | 0 | 59.269 | 56.398 | 49.845 | 17.831 | 0 | 0 | 47.85 | 33.716 | [5 empty] | 15.684 | 10.033 | 3 | 5.5169 | 5.1689 | 4.8999 | 4.6154 | 0.55352 | 10.0331
2006-03-12 | 8:29 | 0 | 15.707 | 0 | 5 | 0 | 56.825 | 57.407 | 46.337 | 46.68 | 42.482 | 26.277 | 3.455 | 1 | 0 | 59.246 | 56.332 | 49.892 | 17.831 | 0 | 0 | 47.85 | 33.737 | [5 empty] | 0 | 10.145 | 4 | 5.5903 | 5.2387 | 4.9029 | 4.6154 | 0.62327 | 11.1492
2006-03-12 | 8:30 | 0 | 15.689 | 0 | 6 | 0 | 56.761 | 57.368 | 46.272 | 46.87 | 42.791 | 26.257 | 3.689 | 1 | 0 | 59.274 | 56.403 | 49.941 | 17.886 | 0 | 0 | 47.878 | 33.79 | [5 empty] | 0 | 9.891 | 5 | 5.5222 | 5.1739 | 4.9002 | 4.6154 | 0.5585 | 10.1138
2006-03-12 | 8:31 | 0 | 15.714 | 1 | 6 | 0 | 56.741 | 57.322 | 46.228 | 46.708 | 42.745 | 26.186 | 3.738 | 1 | 0 | 59.251 | 56.38 | 49.988 | 17.861 | 0 | 0 | 47.854 | 33.837 | [5 empty] | 0 | 10.033 | 6 | 5.5079 | 5.1603 | 4.8996 | 4.6154 | 0.54494 | 9.8937
2006-03-12 | 8:32 | 1 | 15.684 | 0 | 5 | 0 | 56.69 | 57.229 | 46.2 | 46.704 | 42.623 | 26.277 | 3.733 | 0 | 0 | 59.269 | 56.353 | 49.845 | 17.831 | 0 | 0 | 47.826 | 33.785 | [5 empty] | 15.684 | 9.986 | 7 | 5.5094 | 5.1617 | 4.8996 | 4.6154 | 0.54632 | 9.9163
2006-03-12 | 8:33 | 0 | 15.714 | 0 | 6 | 0 | 56.695 | 57.345 | 46.181 | 46.662 | 42.415 | 26.161 | 3.437 | 1 | 0 | 59.274 | 56.337 | 49.988 | 17.861 | 0 | 0 | 47.831 | 33.79 | [5 empty] | 0 | 10.033 | 8 | 5.5955 | 5.2436 | 4.9031 | 4.6154 | 0.62825 | 11.2277
2006-03-12 | 8:34 | 0 | 15.689 | 0 | 6 | 0 | 56.695 | 57.277 | 46.204 | 46.732 | 42.37 | 26.088 | 3.715 | 1 | 0 | 59.228 | 56.314 | 49.964 | 17.861 | 0 | 0 | 47.831 | 33.72 | [5 empty] | 0 | 9.963 | 9 | 5.5146 | 5.1667 | 4.8998 | 4.6154 | 0.5513 | 9.9972
2006-03-12 | 8:35 | 0 | 15.714 | 0 | 5 | 0 | 56.629 | 57.256 | 46.158 | 46.571 | 42.157 | 26.041 | 3.511 | 1 | 0 | 59.251 | 56.314 | 49.85 | 17.886 | 0 | 0 | 47.831 | 33.744 | [5 empty] | 0 | 10.058 | 10 | 5.574 | 5.2232 | 4.9023 | 4.6154 | 0.60777 | 10.9037
2006-03-12 | 8:36 | 1 | 15.762 | 0 | 6 | 0 | 56.741 | 57.391 | 46.228 | 46.708 | 42.298 | 26.161 | 3.437 | 1 | 0 | 59.251 | 56.291 | 49.964 | 17.937 | 0 | 0 | 47.878 | 33.79 | [5 empty] | 15.762 | 10.033 | 11 | 5.5955 | 5.2436 | 4.9031 | 4.6154 | 0.62825 | 11.2277
2006-03-12 | 8:37 | 0 | 15.737 | 0 | 6 | 1 | 56.426 | 57.256 | 46.181 | 46.594 | 41.241 | 26.063 | 4.093 | 1 | 0 | 59.274 | 56.38 | 49.897 | 17.937 | 0 | 0 | 47.878 | 33.79 | [5 empty] | 0 | 9.832 | 12 | 5.4045 | 5.0621 | 4.8954 | 4.6154 | 0.44667 | 8.2648
2006-03-12 | 8:38 | 0 | 15.737 | 0 | 5 | 0 | 56.314 | 57.03 | 46.09 | 46.524 | 41.03 | 26.331 | 4.168 | 1 | 0 | 59.239 | 56.414 | 49.885 | 17.899 | 0 | 0 | 47.866 | 33.802 | [5 empty] | 0 | 9.79 | 0 | 5.3827 | 5.0413 | 4.8945 | 4.6154 | 0.42591 | 7.9127
2006-03-12 | 8:39 | 0 | 15.734 | 0 | 6 | 0 | 56.243 | 56.804 | 46.088 | 46.592 | 41.073 | 26.255 | 3.56 | 1 | 0 | 59.203 | 56.378 | 49.939 | 17.934 | 0 | 0 | 47.852 | 33.763 | [5 empty] | 0 | 9.651 | 1 | 5.5597 | 5.2096 | 4.572 | 4.2857 | 0.92388 | 16.6173
2006-03-12 | 8:40 | 1 | 15.764 | 1 | 6 | 0 | 56.204 | 56.877 | 46.092 | 46.459 | 41.243 | 26.211 | 3.488 | 1 | 0 | 59.253 | 56.339 | 49.99 | 17.939 | 0 | 0 | 47.836 | 33.747 | [5 empty] | 15.764 | 9.745 | 2 | 5.5807 | 5.2295 | 4.5729 | 4.2857 | 0.94381 | 16.912
2006-03-12 | 8:41 | 0 | 15.795 | 0 | 5 | 0 | 56.254 | 56.859 | 46.05 | 46.557 | 41.107 | 26.24 | 3.671 | 1 | 0 | 59.28 | 56.366 | 49.927 | 18.02 | 0 | 0 | 47.864 | 33.751 | [5 empty] | 0 | 9.697 | 3 | 5.5274 | 5.1789 | 4.5707 | 4.2857 | 0.89315 | 16.1586
2006-03-12 | 8:42 | 0 | 15.79 | 0 | 6 | 0 | 56.27 | 56.786 | 46.116 | 46.482 | 40.937 | 26.355 | 3.388 | 1 | 0 | 59.253 | 56.339 | 49.852 | 17.964 | 0 | 0 | 47.857 | 33.699 | [5 empty] | 0 | 9.788 | 4 | 5.6098 | 5.2572 | 4.574 | 4.2857 | 0.97149 | 17.3176
2006-03-12 | 8:43 | 1 | 15.739 | 0 | 5 | 0 | 56.293 | 56.898 | 46.046 | 46.459 | 40.537 | 26.355 | 3.54 | 1 | 0 | 59.276 | 56.316 | 49.852 | 17.964 | 3 | 0 | 55.792 | 22.765 | [5 empty] | 15.739 | 9.834 | 5 | 5.5656 | 5.2151 | 4.5722 | 4.2857 | 0.92941 | 16.6994
2006-03-12 | 8:44 | 0 | 15.764 | 0 | 6 | 0 | 56.316 | 56.898 | 46.046 | 46.391 | 40.726 | 26.284 | 3.462 | 1 | 0 | 59.23 | 56.204 | 49.554 | 17.889 | 0 | 0 | 59.141 | 15.297 | [5 empty] | 0 | 9.925 | 6 | 5.5883 | 5.2367 | 4.5732 | 4.2857 | 0.951 | 17.0179
2006-03-12 | 8:45 | 0 | 15.82 | 0 | 6 | 0 | 56.432 | 56.971 | 46.029 | 46.463 | 40.521 | 26.193 | 3.292 | 1 | 0 | 59.191 | 56.142 | 48.94 | 17.969 | 0 | 0 | 59.842 | 14.49 | [5 empty] | 0 | 9.969 | 7 | 5.6378 | 5.2838 | 4.5752 | 4.2857 | 0.99806 | 17.7031
2006-03-12 | 8:46 | 0 | 15.82 | 0 | 5 | 0 | 56.455 | 56.971 | 46.029 | 46.44 | 41.272 | 26.169 | 3.493 | 1 | 0 | 59.191 | 56.142 | 48.345 | 17.969 | 0 | 0 | 59.976 | 14.885 | [5 empty] | 0 | 10.015 | 8 | 5.5792 | 5.2281 | 4.5728 | 4.2857 | 0.94242 | 16.8916
2006-03-12 | 8:47 | 1 | 15.79 | 0 | 6 | 0 | 56.428 | 57.033 | 45.978 | 46.344 | 41.478 | 26.139 | 3.792 | 1 | 0 | 59.141 | 56.181 | 47.698 | 17.989 | 0 | 0 | 59.972 | 15.616 | [5 empty] | 15.79 | 10.084 | 9 | 5.4922 | 5.1454 | 4.5693 | 4.2857 | 0.85966 | 15.6525
2006-03-12 | 8:48 | 0 | 15.795 | 0 | 5 | 0 | 56.366 | 56.948 | 46.006 | 46.396 | 41.506 | 26.169 | 3.797 | 1 | 0 | 59.169 | 56.096 | 47.152 | 17.994 | 0 | 0 | 59.931 | 16.413 | [5 empty] | 0 | 9.97 | 10 | 5.4907 | 5.144 | 4.5692 | 4.2857 | 0.85828 | 15.6314
2006-03-12 | 8:49 | 0 | 15.82 | 1 | 6 | 0 | 56.389 | 56.948 | 46.074 | 46.349 | 42.119 | 26.289 | 3.823 | 1 | 0 | 59.169 | 56.119 | 46.715 | 17.994 | 0 | 0 | 59.865 | 17.054 | [5 empty] | 0 | 10.04 | 11 | 5.4831 | 5.1368 | 4.5689 | 4.2857 | 0.85108 | 15.5217
2006-03-12 | 8:50 | 0 | 15.82 | 0 | 5 | 0 | 56.412 | 56.994 | 45.983 | 46.51 | 42.188 | 26.24 | 4.457 | 1 | 0 | 59.146 | 56.072 | 46.533 | 17.994 | 0 | 0 | 59.819 | 17.698 | [5 empty] | 0 | 9.902 | 12 | 5.2985 | 4.9613 | 4.5614 | 4.2857 | 0.67559 | 12.7505
2006-03-12 | 8:51 | 1 | 15.795 | 0 | 6 | 1 | 56.432 | 56.925 | 45.959 | 46.326 | 42.071 | 26.289 | 4.178 | 1 | 0 | 59.102 | 56.072 | 46.165 | 18.02 | 0 | 0 | 59.684 | 18.168 | [5 empty] | 15.795 | 10.106 | 13 | 5.3798 | 5.0385 | 4.5647 | 4.2857 | 0.75282 | 13.9935
2006-03-12 | 8:52 | 0 | 15.764 | 0 | 5 | 0 | 56.385 | 56.898 | 45.908 | 46.391 | 41.855 | 25.97 | 4.552 | 1 | 0 | 59.075 | 55.977 | 45.908 | 17.964 | 0 | 0 | 59.591 | 18.558 | [5 empty] | 0 | 9.994 | 0 | 5.2709 | 4.935 | 4.5603 | 4.2857 | 0.64929 | 12.3185
2006-03-12 | 8:53 | 0 | 15.769 | 0 | 6 | 0 | 56.321 | 56.905 | 46.029 | 46.326 | 42.188 | 26.169 | 4.658 | 1 | 0 | 59.102 | 56.026 | 45.754 | 17.994 | 0 | 0 | 59.573 | 18.982 | [5 empty] | 0 | 9.995 | 1 | 5.24 | 4.9057 | 4.559 | 4.2857 | 0.61995 | 11.8312
2006-03-12 | 8:54 | 0 | 15.782 | 0 | 5 | 0 | 56.444 | 56.914 | 45.854 | 46.335 | 42.762 | 26.034 | 4.694 | 1 | 0 | 59.089 | 56.037 | 45.67 | 18.03 | 0 | 0 | 59.515 | 19.362 | [5 empty] | 0 | 10.109 | 2 | 5.2295 | 4.8957 | 4.5586 | 4.2857 | 0.60999 | 11.6643
2006-03-12 | 8:55 | 1 | 15.747 | 0 | 6 | 0 | 56.163 | 56.905 | 45.913 | 46.326 | 42.824 | 26.24 | 4.761 | 1 | 0 | 59.102 | 56.119 | 45.502 | 18.092 | 0 | 0 | 59.438 | 19.674 | [5 empty] | 15.747 | 9.837 | 3 | 5.21 | 4.8772 | 4.5578 | 4.2857 | 0.59144 | 11.352
2006-03-12 | 8:56 | 0 | 15.782 | 0 | 6 | 0 | 56.175 | 56.802 | 45.854 | 46.267 | 43.279 | 26.274 | 4.797 | 1 | 0 | 59.089 | 56.014 | 45.464 | 18.03 | 0 | 0 | 59.381 | 20.031 | [5 empty] | 0 | 9.908 | 4 | 5.1995 | 4.8672 | 4.5574 | 4.2857 | 0.58148 | 11.1833
2006-03-12 | 8:57 | 0 | 15.697 | 0 | 5 | 0 | 56.163 | 56.747 | 45.845 | 46.396 | 42.8 | 26.289 | 4.735 | 1 | 0 | 59.034 | 56.049 | 45.432 | 17.994 | 0 | 0 | 59.258 | 20.291 | [5 empty] | 0 | 9.767 | 5 | 5.2176 | 4.8844 | 4.5581 | 4.2857 | 0.59864 | 11.4735
2006-03-12 | 8:58 | 0 | 15.722 | 1 | 6 | 0 | 56.096 | 56.679 | 45.983 | 46.326 | 42.284 | 26.313 | 4.925 | 1 | 0 | 59.043 | 55.967 | 45.464 | 17.932 | 0 | 0 | 59.132 | 20.591 | [5 empty] | 0 | 9.77 | 6 | 5.1622 | 4.8318 | 4.5559 | 4.2857 | 0.54605 | 10.5777
2006-03-12 | 8:59 | 1 | 15.656 | 0 | 5 | 0 | 55.988 | 56.597 | 45.805 | 46.288 | 41.915 | 26.25 | 4.645 | 1 | 0 | 58.995 | 55.918 | 45.394 | 17.904 | 0 | 0 | 59.018 | 20.877 | [5 empty] | 15.656 | 9.7 | 7 | 5.2438 | 4.9093 | 4.5592 | 4.2857 | 0.62355 | 11.8912
2006-03-12 | 9:00 | 0 | 15.682 | 0 | 6 | 0 | 55.918 | 56.508 | 45.784 | 46.242 | 41.82 | 26.394 | 4.871 | 1 | 0 | 59.018 | 55.942 | 45.233 | 17.904 | 0 | 0 | 58.972 | 21.118 | [5 empty] | 0 | 9.676 | 8 | 5.178 | 4.8467 | 4.5565 | 4.2857 | 0.56099 | 10.8342
2006-03-12 | 9:01 | 0 | 15.712 | 0 | 5 | 0 | 55.946 | 56.49 | 45.812 | 46.246 | 42.037 | 26.279 | 4.977 | 1 | 0 | 59 | 55.923 | 45.261 | 17.984 | 0 | 0 | 58.911 | 21.51 | [5 empty] | 0 | 9.7 | 9 | 5.1471 | 4.8174 | 4.5553 | 4.2857 | 0.53165 | 10.3292
2006-03-12 | 9:02 | 0 | 15.687 | 0 | 6 | 0 | 55.946 | 56.535 | 45.789 | 46.223 | 41.755 | 26.255 | 5.129 | 0 | 0 | 59 | 55.879 | 45.285 | 17.984 | 0 | 0 | 58.845 | 21.775 | [5 empty] | 0 | 9.723 | 10 | 5.1028 | 4.7753 | 4.5535 | 4.2857 | 0.48958 | 9.5942
2006-03-12 | 9:03 | 1 | 15.712 | 0 | 6 | 0 | 55.946 | 56.512 | 45.833 | 46.202 | 42.413 | 26.279 | 4.977 | 1 | 0 | 58.979 | 55.902 | 45.285 | 17.959 | 0 | 0 | 58.845 | 22.135 | [5 empty] | 15.712 | 9.744 | 11 | 5.1471 | 4.8174 | 4.5553 | 4.2857 | 0.53165 | 10.3292
2006-03-12 | 9:04 | 0 | 15.682 | 0 | 5 | 0 | 55.895 | 56.485 | 45.668 | 46.195 | 42.195 | 26.299 | 4.998 | 1 | 0 | 58.972 | 55.918 | 45.301 | 17.929 | 0 | 0 | 58.591 | 22.444 | [5 empty] | 0 | 9.7 | 12 | 5.141 | 4.8116 | 4.555 | 4.2857 | 0.52584 | 10.2284
2006-03-12 | 9:05 | 0 | 15.712 | 0 | 6 | 1 | 55.902 | 56.467 | 45.696 | 46.155 | 42.53 | 26.495 | 4.877 | 1 | 0 | 59 | 55.923 | 45.191 | 17.984 | 0 | 0 | 58.598 | 22.738 | [5 empty] | 0 | 9.747 | 13 | 5.1762 | 4.845 | 4.5565 | 4.2857 | 0.55933 | 10.8058
2006-03-12 | 9:06 | 0 | 15.712 | 0 | 5 | 0 | 55.902 | 56.512 | 45.696 | 46.109 | 42.884 | 26.448 | 4.877 | 1 | 0 | 58.979 | 55.902 | 45.238 | 18.009 | 0 | 0 | 58.575 | 23.003 | [5 empty] | 0 | 9.793 | 0 | 5.1762 | 4.845 | 4.5565 | 4.2857 | 0.55933 | 10.8058
2006-03-12 | 9:07 | 1 | 15.682 | 1 | 6 | 0 | 55.895 | 56.462 | 45.647 | 46.081 | 43.231 | 26.321 | 4.923 | 1 | 0 | 58.952 | 55.827 | 45.278 | 17.979 | 0 | 0 | 58.479 | 23.214 | [5 empty] | 15.682 | 9.814 | 1 | 5.1628 | 4.8323 | 4.2702 | 4 | 0.83231 | 16.1213
2006-03-12 | 9:08 | 0 | 15.762 | 0 | 5 | 0 | 55.879 | 56.467 | 45.789 | 46.041 | 43.212 | 26.424 | 5.258 | 1 | 0 | 59 | 55.855 | 45.168 | 17.984 | 0 | 0 | 58.507 | 23.508 | [5 empty] | 0 | 9.838 | 2 | 5.0653 | 4.7396 | 4.2663 | 4 | 0.73959 | 14.6011
2006-03-12 | 9:09 | 0 | 15.737 | 0 | 6 | 0 | 55.879 | 56.467 | 45.604 | 46.018 | 42.389 | 26.495 | 5.155 | 1 | 0 | 58.956 | 55.832 | 45.285 | 18.009 | 0 | 0 | 58.418 | 23.749 | [5 empty] | 0 | 9.861 | 3 | 5.0953 | 4.7681 | 4.2675 | 4 | 0.7681 | 15.0747
2006-03-12 | 9:10 | 0 | 15.737 | 0 | 5 | 0 | 55.741 | 56.332 | 45.628 | 46.109 | 42.061 | 26.618 | 5.028 | 1 | 0 | 58.956 | 55.832 | 45.215 | 17.984 | 0 | 0 | 58.372 | 23.967 | [5 empty] | 0 | 9.632 | 4 | 5.1322 | 4.8032 | 4.269 | 4 | 0.80325 | 15.651
2006-03-12 | 9:11 | 1 | 15.732 | 0 | 6 | 0 | 55.713 | 56.282 | 45.6 | 45.966 | 41.21 | 26.635 | 4.972 | 1 | 0 | 58.952 | 55.827 | 45.119 | 17.979 | 0 | 0 | 58.457 | 24.273 | [5 empty] | 15.732 | 9.747 | 5 | 5.1486 | 4.8188 | 4.2696 | 4 | 0.81875 | 15.9025
2006-03-12 | 9:12 | 0 | 15.737 | 0 | 5 | 0 | 55.741 | 56.266 | 45.628 | 46.132 | 40.509 | 26.689 | 5.003 | 1 | 0 | 58.979 | 55.855 | 45.261 | 17.984 | 0 | 0 | 58.26 | 24.376 | [5 empty] | 0 | 9.609 | 6 | 5.1395 | 4.8102 | 4.2693 | 4 | 0.81017 | 15.7635
2006-03-12 | 9:13 | 0 | 15.762 | 0 | 6 | 0 | 55.764 | 56.243 | 45.766 | 45.994 | 40.04 | 26.784 | 4.472 | 1 | 0 | 58.979 | 55.809 | 45.1 | 17.984 | 0 | 0 | 58.217 | 24.568 | [5 empty] | 0 | 9.77 | 7 | 5.2942 | 4.9572 | 4.2755 | 4 | 0.95715 | 18.0794
2006-03-12 | 9:14 | 0 | 15.732 | 0 | 5 | 0 | 55.643 | 56.193 | 45.53 | 45.99 | 39.681 | 26.755 | 4.745 | 1 | 0 | 58.906 | 55.781 | 45.072 | 17.979 | 0 | 0 | 58.121 | 24.707 | [5 empty] | 0 | 9.653 | 8 | 5.2147 | 4.8816 | 4.2723 | 4 | 0.88158 | 16.9059
2006-03-12 | 9:15 | 1 | 15.762 | 0 | 6 | 0 | 55.603 | 56.175 | 45.581 | 45.948 | 39.71 | 26.762 | 4.624 | 1 | 0 | 58.911 | 55.809 | 45.1 | 18.057 | 0 | 0 | 58.082 | 24.931 | [5 empty] | 15.762 | 9.655 | 9 | 5.2499 | 4.9151 | 4.2737 | 4 | 0.91508 | 17.4304
2006-03-12 | 9:16 | 0 | 15.785 | 0 | 5 | 0 | 55.65 | 56.197 | 45.513 | 45.903 | 39.968 | 26.713 | 4.624 | 1 | 0 | 58.956 | 55.785 | 45.191 | 18.057 | 0 | 0 | 57.991 | 25.122 | [5 empty] | 0 | 9.747 | 10 | 5.2499 | 4.9151 | 4.2737 | 4 | 0.91508 | 17.4304
2006-03-12 | 9:17 | 0 | 15.785 | 1 | 6 | 0 | 55.65 | 56.175 | 45.513 | 45.88 | 39.782 | 26.738 | 4.75 | 1 | 0 | 58.911 | 55.785 | 45.1 | 18.057 | 0 | 0 | 57.991 | 25.291 | [5 empty] | 0 | 9.77 | 11 | 5.2132 | 4.8802 | 4.2722 | 4 | 0.8802 | 16.8841
2006-03-12 | 9:18 | 0 | 15.707 | 0 | 5 | 0 | 55.622 | 56.126 | 45.348 | 45.761 | 39.894 | 26.733 | 5.075 | 1 | 0 | 58.883 | 55.76 | 45.028 | 18.052 | 0 | 0 | 57.9 | 25.431 | [5 empty] | 0 | 9.861 | 12 | 5.1186 | 4.7902 | 4.2684 | 4 | 0.79024 | 15.4387
2006-03-12 | 9:19 | 1 | 15.777 | 0 | 6 | 0 | 55.687 | 56.147 | 45.39 | 45.759 | 40.76 | 26.728 | 5.348 | 1 | 0 | 58.904 | 55.778 | 45.208 | 18.05 | 0 | 0 | 57.895 | 25.62 | [5 empty] | 15.777 | 9.928 | 13 | 5.0391 | 4.7147 | 4.2652 | 4 | 0.71467 | 14.1827
2006-03-12 | 9:20 | 0 | 15.8 | 0 | 5 | 1 | 55.687 | 56.236 | 45.413 | 45.759 | 40.243 | 26.752 | 4.967 | 1 | 0 | 58.927 | 55.757 | 45.117 | 18.072 | 0 | 0 | 57.895 | 25.813 | [5 empty] | 0 | 9.928 | 14 | 5.15 | 4.8201 | 4.2697 | 4 | 0.82013 | 15.9249
2006-03-12 | 9:21 | 0 | 15.825 | 0 | 6 | 0 | 55.734 | 56.236 | 45.369 | 45.873 | 39.985 | 26.703 | 4.688 | 1 | 0 | 58.904 | 55.778 | 45.047 | 18.05 | 0 | 0 | 57.829 | 26.005 | [5 empty] | 0 | 9.861 | 0 | 5.2313 | 4.8974 | 4.273 | 4 | 0.89736 | 17.1539
2006-03-12 | 9:22 | 0 | 15.777 | 0 | 5 | 0 | 55.711 | 56.259 | 45.345 | 45.712 | 39.751 | 26.728 | 4.688 | 1 | 0 | 58.927 | 55.757 | 45.161 | 18.072 | 0 | 0 | 57.761 | 26.149 | [5 empty] | 0 | 9.999 | 1 | 5.2313 | 4.8974 | 4.5587 | 4.2857 | 0.61165 | 11.6922
2006-03-12 | 9:23 | 1 | 15.8 | 0 | 5 | 0 | 55.687 | 56.236 | 45.369 | 45.712 | 39.538 | 26.657 | 5.044 | 1 | 0 | 58.904 | 55.734 | 45.093 | 18.097 | 0 | 0 | 57.715 | 26.343 | [5 empty] | 15.8 | 9.975 | 2 | 5.1276 | 4.7988 | 4.5545 | 4.2857 | 0.51311 | 10.0068
2006-03-12 | 9:24 | 0 | 15.8 | 0 | 6 | 0 | 55.687 | 56.259 | 45.299 | 45.644 | 39.751 | 26.583 | 5.474 | 1 | 0 | 58.881 | 55.711 | 45.07 | 18.097 | 0 | 0 | 57.694 | 26.463 | [5 empty] | 0 | 10.043 | 3 | 5.0024 | 4.6798 | 4.5494 | 4.2857 | 0.39408 | 7.8779
2006-03-12 | 9:25 | 0 | 15.777 | 0 | 5 | 0 | 55.62 | 56.259 | 45.231 | 45.574 | 39.42 | 26.632 | 5.322 | 1 | 0 | 58.927 | 55.734 | 45.047 | 18.072 | 0 | 0 | 57.672 | 26.559 | [5 empty] | 0 | 10.046 | 4 | 5.0466 | 4.7219 | 4.5512 | 4.2857 | 0.43616 | 8.6425
2006-03-12 | 9:26 | 0 | 15.8 | 1 | 5 | 0 | 55.643 | 56.124 | 45.208 | 45.574 | 39.655 | 26.534 | 5.018 | 1 | 0 | 58.881 | 55.687 | 45.184 | 18.072 | 0 | 0 | 57.603 | 26.703 | [5 empty] | 0 | 10.069 | 5 | 5.1352 | 4.806 | 4.5548 | 4.2857 | 0.5203 | 10.1322
2006-03-12 | 9:27 | 1 | 15.8 | 0 | 6 | 0 | 55.664 | 56.17 | 45.184 | 45.597 | 39.279 | 26.608 | 4.815 | 1 | 0 | 58.904 | 55.711 | 45.023 | 18.097 | 0 | 0 | 57.583 | 26.824 | [5 empty] | 15.8 | 10.067 | 6 | 5.1943 | 4.8622 | 4.5572 | 4.2857 | 0.57649 | 11.0986
2006-03-12 | 9:28 | 0 | 15.8 | 0 | 5 | 0 | 55.687 | 56.236 | 45.275 | 45.644 | 39.045 | 26.679 | 4.766 | 1 | 0 | 58.861 | 55.687 | 45.047 | 18.072 | 0 | 0 | 57.537 | 26.993 | [5 empty] | 0 | 10.043 | 7 | 5.2085 | 4.8758 | 4.5578 | 4.2857 | 0.59006 | 11.3286
2006-03-12 | 9:29 | 0 | 15.777 | 0 | 5 | 0 | 55.711 | 56.243 | 45.285 | 45.628 | 38.911 | 26.495 | 5.381 | 2 | 0 | 58.867 | 55.673 | 45.147 | 18.082 | 0 | 0 | 57.589 | 27.145 | [5 empty] | 0 | 10.083 | 8 | 5.0295 | 4.7055 | 4.5505 | 4.2857 | 0.41982 | 8.3473
2006-03-12 | 9:30 | 0 | 15.777 | 0 | 5 | 0 | 55.734 | 56.213 | 45.254 | 45.644 | 38.928 | 26.392 | 5.397 | 0 | 0 | 58.815 | 55.62 | 45.07 | 18.05 | 0 | 0 | 57.583 | 27.186 | [5 empty] | 0 | 10.09 | 9 | 5.0248 | 4.7011 | 4.5503 | 4.2857 | 0.4154 | 8.2669
2006-03-12 | 9:31 | 1 | 15.825 | 0 | 6 | 0 | 55.734 | 56.282 | 45.208 | 45.574 | 39.162 | 26.512 | 5.752 | 1 | 0 | 58.838 | 55.643 | 45.117 | 18.05 | 0 | 0 | 57.56 | 27.307 | [5 empty] | 15.825 | 10.16 | 10 | 4.9214 | 4.6028 | 4.5461 | 4.2857 | 0.31713 | 6.4439
2006-03-12 | 9:32 | 0 | 15.8 | 0 | 5 | 0 | 55.596 | 56.236 | 45.231 | 45.506 | 39.303 | 26.414 | 6.208 | 1 | 0 | 58.815 | 55.643 | 45.047 | 18.097 | 0 | 0 | 57.583 | 27.378 | [5 empty] | 0 | 10.09 | 11 | 4.7886 | 4.4766 | 4.5408 | 4.2857 | 0.19091 | 3.9868
2006-03-12 | 9:33 | 0 | 15.832 | 0 | 5 | 0 | 55.375 | 56.063 | 45.147 | 45.513 | 39.145 | 26.591 | 6.141 | 1 | 0 | 58.845 | 55.65 | 45.077 | 18.105 | 0 | 0 | 57.567 | 27.532 | [5 empty] | 0 | 9.862 | 12 | 4.8081 | 4.4952 | 4.5416 | 4.2857 | 0.20946 | 4.3563
2006-03-12 | 9:34 | 0 | 15.785 | 0 | 5 | 1 | 55.167 | 55.718 | 45.1 | 45.581 | 38.839 | 26.446 | 6.293 | 1 | 0 | 58.867 | 55.673 | 45.1 | 18.155 | 0 | 0 | 57.544 | 27.652 | [5 empty] | 0 | 9.586 | 13 | 4.7639 | 4.4531 | 4.5398 | 4.2857 | 0.16738 | 3.5136
2006-03-12 | 9:35 | 1 | 15.81 | 1 | 5 | 0 | 55.008 | 55.557 | 45.168 | 45.42 | 38.7 | 26.519 | 6.394 | 1 | 0 | 58.867 | 55.627 | 45.077 | 18.082 | 0 | 0 | 57.478 | 27.723 | [5 empty] | 15.81 | 9.588 | 0 | 4.7345 | 4.4251 | 4.5386 | 4.2857 | 0.13943 | 2.9449
2006-03-12 | 9:36 | 0 | 15.785 | 0 | 5 | 0 | 54.847 | 55.442 | 45.03 | 45.399 | 38.677 | 26.424 | 6.443 | 1 | 0 | 58.845 | 55.627 | 45.1 | 18.13 | 0 | 0 | 57.455 | 27.797 | [5 empty] | 0 | 9.448 | 1 | 4.7202 | 4.4116 | 4.2523 | 4 | 0.41158 | 8.7195
2006-03-12 | 9:37 | 0 | 15.759 | 0 | 6 | 0 | 54.824 | 55.375 | 44.986 | 45.352 | 39.028 | 26.446 | 6.316 | 2 | 0 | 58.845 | 55.603 | 45.009 | 18.105 | 0 | 0 | 57.432 | 27.942 | [5 empty] | 0 | 9.472 | 2 | 4.7572 | 4.4467 | 4.2538 | 4 | 0.44673 | 9.3907
2006-03-12 | 9:38 | 0 | 15.759 | 0 | 5 | 0 | 54.891 | 55.351 | 44.963 | 45.306 | 39.521 | 26.446 | 5.912 | 1 | 0 | 58.797 | 55.601 | 45.054 | 18.105 | 0 | 0 | 57.384 | 28.084 | [5 empty] | 0 | 9.585 | 3 | 4.8748 | 4.5586 | 4.2585 | 4 | 0.55856 | 11.458
2006-03-12 | 9:39 | 0 | 15.777 | 0 | 5 | 0 | 54.952 | 55.365 | 44.771 | 45.229 | 39.42 | 26.439 | 5.881 | 1 | 0 | 58.792 | 55.573 | 45.114 | 18.097 | 0 | 0 | 57.423 | 28.221 | [5 empty] | 0 | 9.723 | 4 | 4.8839 | 4.5671 | 4.2589 | 4 | 0.56714 | 11.6125
2006-03-12 | 9:40 | 1 | 15.747 | 0 | 5 | 0 | 54.901 | 55.407 | 44.767 | 45.086 | 38.992 | 26.507 | 5.976 | 1 | 0 | 58.808 | 55.566 | 45.042 | 18.067 | 0 | 0 | 57.373 | 28.265 | [5 empty] | 15.747 | 9.815 | 5 | 4.8562 | 4.5408 | 4.2578 | 4 | 0.54084 | 11.1372
2006-03-12 | 9:41 | 0 | 15.797 | 0 | 5 | 0 | 54.947 | 55.428 | 44.697 | 45.086 | 38.545 | 26.578 | 5.951 | 1 | 0 | 58.785 | 55.522 | 45.086 | 18.092 | 0 | 0 | 57.352 | 28.336 | [5 empty] | 0 | 9.861 | 6 | 4.8635 | 4.5478 | 4.2581 | 4 | 0.54776 | 11.2628
2006-03-12 | 9:42 | 0 | 15.802 | 0 | 5 | 0 | 54.793 | 55.365 | 44.587 | 45.07 | 38.645 | 26.463 | 6.033 | 0 | 0 | 58.769 | 55.617 | 45.138 | 18.123 | 0 | 0 | 57.311 | 28.464 | [5 empty] | 0 | 9.723 | 7 | 4.8396 | 4.5251 | 4.2571 | 4 | 0.52507 | 10.8494
2006-03-12 | 9:43 | 0 | 15.747 | 0 | 5 | 0 | 54.695 | 55.223 | 44.538 | 44.904 | 38.497 | 26.458 | 5.976 | 2 | 0 | 58.742 | 55.545 | 45.042 | 18.118 | 0 | 0 | 57.329 | 28.457 | [5 empty] | 0 | 9.791 | 8 | 4.8562 | 4.5408 | 4.2578 | 4 | 0.54084 | 11.1372
2006-03-12 | 9:44 | 1 | 15.777 | 1 | 5 | 0 | 54.539 | 55.228 | 44.519 | 44.862 | 38.433 | 26.608 | 5.804 | 0 | 0 | 58.792 | 55.55 | 45.023 | 18.123 | 0 | 0 | 57.357 | 28.51 | [5 empty] | 15.777 | 9.677 | 9 | 4.9063 | 4.5885 | 4.2598 | 4 | 0.58845 | 11.9939
2006-03-12 | 9:45 | 0 | 15.802 | 0 | 5 | 0 | 54.747 | 55.137 | 44.496 | 44.818 | 38.574 | 26.608 | 6.082 | 2 | 0 | 58.813 | 55.55 | 45.023 | 18.173 | 0 | 0 | 57.311 | 28.609 | [5 empty] | 0 | 9.929 | 10 | 4.8253 | 4.5115 | 4.2565 | 4 | 0.5115 | 10.6004
2006-03-12 | 9:46 | 0 | 15.747 | 0 | 5 | 0 | 54.649 | 55.246 | 44.42 | 44.858 | 38.217 | 26.507 | 4.864 | 1 | 0 | 58.696 | 55.522 | 45.042 | 18.143 | 0 | 0 | 57.195 | 28.675 | [5 empty] | 0 | 9.791 | 11 | 5.18 | 4.8486 | 4.2709 | 4 | 0.84864 | 16.3831
2006-03-12 | 9:47 | 0 | 15.802 | 0 | 5 | 0 | 54.747 | 55.16 | 44.379 | 44.748 | 38.363 | 26.463 | 5.325 | 1 | 0 | 58.701 | 55.526 | 45.07 | 18.148 | 0 | 0 | 57.199 | 28.824 | [5 empty] | 0 | 9.999 | 12 | 5.0458 | 4.721 | 4.2655 | 4 | 0.72104 | 14.29
2006-03-12 | 9:48 | 1 | 15.772 | 0 | 5 | 0 | 54.81 | 55.246 | 44.444 | 44.673 | 38.521 | 26.529 | 5.876 | 1 | 0 | 58.719 | 55.475 | 44.995 | 18.118 | 0 | 0 | 57.195 | 28.866 | [5 empty] | 15.772 | 10.137 | 13 | 4.8853 | 4.5685 | 4.259 | 4 | 0.56852 | 11.6374
2006-03-12 | 9:49 | 0 | 15.777 | 0 | 5 | 1 | 55.022 | 55.389 | 44.379 | 44.725 | 38.904 | 26.583 | 6.36 | 1 | 0 | 58.813 | 55.526 | 45.07 | 18.296 | 0 | 0 | 57.222 | 28.944 | [5 empty] | 0 | 10.297 | 14 | 4.7444 | 4.4346 | 4.2533 | 4 | 0.43455 | 9.1593
2006-03-12 | 9:50 | 0 | 15.747 | 0 | 5 | 0 | 54.856 | 55.384 | 44.326 | 44.629 | 38.617 | 26.458 | 6.584 | 1 | 0 | 58.696 | 55.475 | 45.019 | 18.143 | 0 | 0 | 57.195 | 28.94 | [5 empty] | 0 | 10.227 | 0 | 4.6791 | 4.3725 | 4.2506 | 4 | 0.37255 | 7.9619
2006-03-12 | 9:51 | 0 | 15.747 | 0 | 5 | 0 | 54.765 | 55.384 | 44.233 | 44.582 | 38.686 | 26.409 | 6.051 | 1 | 0 | 58.651 | 55.428 | 45.063 | 18.092 | 0 | 0 | 57.195 | 29.035 | [5 empty] | 0 | 10.183 | 1 | 4.8343 | 4.5201 | 4.0069 | 3.75 | 0.77008 | 15.9294
2006-03-12 | 9:52 | 0 | 15.722 | 0 | 5 | 0 | 54.672 | 55.291 | 44.233 | 44.582 | 38.875 | 26.409 | 6.456 | 1 | 0 | 58.696 | 55.428 | 44.972 | 18.092 | 0 | 0 | 57.195 | 29.109 | [5 empty] | 0 | 10.09 | 2 | 4.7164 | 4.408 | 4.0021 | 3.75 | 0.65798 | 13.9508
2006-03-12 | 9:53 | 1 | 15.752 | 1 | 5 | 0 | 54.7 | 55.183 | 44.214 | 44.725 | 39.021 | 26.463 | 6.564 | 1 | 0 | 58.701 | 55.48 | 45.047 | 18.148 | 0 | 0 | 57.222 | 29.234 | [5 empty] | 15.752 | 9.975 | 3 | 4.685 | 4.3781 | 4.0008 | 3.75 | 0.62808 | 13.4064
2006-03-12 | 9:54 | 0 | 15.722 | 0 | 5 | 0 | 54.672 | 55.2 | 44.209 | 44.582 | 39.062 | 26.507 | 6.203 | 1 | 0 | 58.696 | 55.452 | 44.972 | 18.143 | 0 | 0 | 57.172 | 29.276 | [5 empty] | 0 | 10.09 | 4 | 4.7901 | 4.478 | 4.0051 | 3.75 | 0.72801 | 15.1983
2006-03-12 | 9:55 | 0 | 15.747 | 0 | 5 | 0 | 54.628 | 55.176 | 44.209 | 44.491 | 38.686 | 26.458 | 5.42 | 1 | 0 | 58.696 | 55.407 | 45.019 | 18.092 | 0 | 0 | 57.106 | 29.3 | [5 empty] | 0 | 10.137 | 5 | 5.0181 | 4.6947 | 4.0143 | 3.75 | 0.94474 | 18.8267
2006-03-12 | 9:56 | 0 | 15.772 | 0 | 5 | 0 | 54.628 | 55.155 | 44.092 | 44.42 | 38.38 | 26.483 | 5.469 | 1 | 0 | 58.651 | 55.407 | 44.995 | 18.143 | 0 | 0 | 57.149 | 29.3 | [5 empty] | 0 | 10.208 | 6 | 5.0038 | 4.6812 | 4.0138 | 3.75 | 0.93118 | 18.6094
2006-03-12 | 9:57 | 1 | 15.747 | 0 | 5 | 0 | 54.373 | 55.062 | 44.116 | 44.444 | 39.203 | 26.554 | 5.824 | 1 | 0 | 58.63 | 55.428 | 45.063 | 18.143 | 0 | 0 | 57.106 | 29.349 | [5 empty] | 15.747 | 9.929 | 7 | 4.9005 | 4.5829 | 4.0096 | 3.75 | 0.83292 | 16.9967
2006-03-12 | 9:58 | 0 | 15.777 | 0 | 5 | 0 | 54.471 | 54.814 | 44.003 | 44.307 | 406.97 | 26.488 | 6.36 | 1 | 0 | 58.657 | 55.456 | 45.035 | 18.135 | 0 | 0 | 57.099 | 29.462 | [5 empty] | 0 | 10.164 | 8 | 4.7444 | 4.4346 | 4.0033 | 3.75 | 0.68455 | 14.4287
2006-03-12 | 9:59 | 0 | 15.79 | 0 | 5 | 0 | 54.436 | 54.919 | 43.944 | 44.343 | 406.97 | 26.5 | 6.602 | 1 | 0 | 58.646 | 55.447 | 45.058 | 18.211 | 0 | 0 | 57.099 | 29.486 | [5 empty] | 0 | 10.093 | 9 | 4.6739 | 4.3676 | 4.0004 | 3.75 | 0.61757 | 13.2131
2006-03-12 | 10:00 | 0 | 15.764 | 0 | 5 | 0 | 54.483 | 54.964 | 43.874 | 44.178 | 406.97 | 26.645 | 6.525 | 1 | 0 | 58.669 | 55.424 | 45.035 | 18.16 | 0 | 0 | 57.122 | 29.511 | [5 empty] | 0 | 10.305 | 10 | 4.6963 | 4.3889 | 4.0013 | 3.75 | 0.63888 | 13.6038
2006-03-12 | 10:01 | 1 | 15.764 | 0 | 4 | 0 | 54.574 | 55.011 | 43.803 | 44.133 | 318.581 | 26.475 | 6.651 | 1 | 0 | 58.689 | 55.4 | 45.058 | 18.16 | 0 | 0 | 57.076 | 29.631 | [5 empty] | 15.764 | 10.441 | 11 | 4.6596 | 4.354 | 3.9998 | 3.75 | 0.604 | 12.9625
2006-03-12 | 10:02 | 0 | 15.79 | 0 | 5 | 0 | 54.644 | 55.102 | 43.616 | 44.037 | 305.506 | 26.451 | 6.829 | 1 | 0 | 58.646 | 55.354 | 45.149 | 18.185 | 0 | 0 | 57.008 | 29.68 | [5 empty] | 0 | 10.607 | 12 | 4.6078 | 4.3047 | 3.9977 | 3.75 | 0.55473 | 12.039
2006-03-12 | 10:03 | 0 | 15.764 | 1 | 5 | 0 | 54.644 | 55.102 | 43.451 | 43.826 | 282.573 | 26.38 | 6.577 | 1 | 0 | 58.623 | 55.377 | 45.058 | 18.211 | 0 | 0 | 57.008 | 29.751 | [5 empty] | 0 | 10.818 | 13 | 4.6812 | 4.3745 | 4.0007 | 3.75 | 0.62449 | 13.3404
2006-03-12 | 10:04 | 0 | 15.764 | 0 | 4 | 0 | 54.413 | 54.987 | 43.31 | 43.592 | 285.136 | 26.5 | 6.172 | 1 | 0 | 58.646 | 55.377 | 45.035 | 18.211 | 0 | 0 | 57.008 | 29.8 | [5 empty] | 0 | 10.821 | 14 | 4.7991 | 4.4866 | 4.0055 | 3.75 | 0.73659 | 15.3485
2006-03-12 | 10:05 | 0 | 15.79 | 0 | 5 | 1 | 54.392 | 54.919 | 43.262 | 43.544 | 214.106 | 26.595 | 6.121 | 2 | 0 | 58.669 | 55.377 | 45.012 | 18.185 | 0 | 0 | 57.008 | 29.849 | [5 empty] | 0 | 10.848 | 15 | 4.814 | 4.5007 | 4.0061 | 3.75 | 0.75071 | 15.5944
2006-03-12 | 10:06 | 1 | 15.79 | 0 | 4 | 0 | 54.369 | 54.873 | 43.262 | 43.451 | 244.803 | 26.595 | 6.425 | 1 | 0 | 58.623 | 55.4 | 45.012 | 18.236 | 0 | 0 | 56.987 | 29.871 | [5 empty] | 15.79 | 10.918 | 0 | 4.7254 | 4.4166 | 4.0025 | 3.75 | 0.66656 | 14.1058
2006-03-12 | 10:07 | 0 | 15.764 | 0 | 5 | 0 | 54.231 | 54.896 | 43.145 | 43.334 | 342.419 | 26.5 | 6.525 | 1 | 0 | 58.623 | 55.377 | 45.126 | 18.236 | 0 | 0 | 57.008 | 29.92 | [5 empty] | 0 | 10.897 | 1 | 4.6963 | 4.3889 | 4.2513 | 4 | 0.38888 | 8.2805
2006-03-12 | 10:08 | 0 | 15.764 | 0 | 4 | 0 | 54.275 | 54.735 | 43.028 | 43.358 | 346.352 | 26.451 | 6.347 | 1 | 0 | 58.6 | 55.33 | 45.082 | 18.236 | 0 | 0 | 56.941 | 29.969 | [5 empty] | 0 | 10.917 | 2 | 4.7482 | 4.4382 | 4.2534 | 4 | 0.43815 | 9.2278
2006-03-12 | 10:09 | 0 | 15.764 | 0 | 5 | 0 | 54.299 | 54.735 | 42.934 | 43.217 | 406.97 | 26.451 | 6.651 | 1 | 0 | 58.578 | 55.354 | 44.988 | 18.258 | 0 | 0 | 56.941 | 30.016 | [5 empty] | 0 | 11.082 | 3 | 4.6596 | 4.354 | 4.2498 | 4 | 0.354 | 7.5972
2006-03-12 | 10:10 | 1 | 15.764 | 0 | 4 | 0 | 54.322 | 54.758 | 42.886 | 43.097 | 340.283 | 26.451 | 6.93 | 1 | 0 | 58.6 | 55.354 | 45.058 | 18.258 | 0 | 0 | 56.919 | 30.09 | [5 empty] | 15.764 | 11.225 | 4 | 4.5784 | 4.2768 | 4.2465 | 4 | 0.27678 | 6.0453
2006-03-12 | 10:11 | 0 | 15.764 | 0 | 5 | 0 | 54.369 | 54.873 | 42.817 | 43.075 | 328.56 | 26.475 | 6.955 | 1 | 0 | 58.6 | 55.309 | 45.012 | 18.258 | 0 | 0 | 56.83 | 30.136 | [5 empty] | 0 | 11.294 | 5 | 4.5711 | 4.2699 | 4.2462 | 4 | 0.26986 | 5.9035
2006-03-12 | 10:12 | 0 | 15.714 | 1 | 4 | 0 | 54.345 | 54.803 | 42.745 | 43.004 | 256.415 | 26.475 | 6.803 | 1 | 0 | 58.623 | 55.309 | 45.035 | 18.258 | 0 | 0 | 56.83 | 30.185 | [5 empty] | 0 | 11.341 | 6 | 4.6154 | 4.3119 | 4.248 | 4 | 0.31193 | 6.7585
2006-03-12 | 10:13 | 0 | 15.692 | 0 | 5 | 0 | 54.254 | 54.758 | 42.676 | 42.98 | 251.499 | 26.451 | 6.829 | 1 | 0 | 58.534 | 55.309 | 44.988 | 18.258 | 0 | 0 | 56.784 | 30.259 | [5 empty] | 0 | 11.274 | 7 | 4.6078 | 4.3047 | 4.2477 | 4 | 0.30473 | 6.6134
2006-03-12 | 10:14 | 1 | 15.666 | 0 | 5 | 0 | 54.275 | 54.688 | 42.604 | 42.98 | 204.769 | 26.451 | 6.881 | 1 | 0 | 58.555 | 55.286 | 45.126 | 18.258 | 0 | 0 | 56.718 | 30.259 | [5 empty] | 15.666 | 11.295 | 8 | 4.5927 | 4.2903 | 4.2471 | 4 | 0.29034 | 6.3218
2006-03-12 | 10:15 | 0 | 15.714 | 0 | 4 | 0 | 54.231 | 54.644 | 42.745 | 42.956 | 217.931 | 26.62 | 6.906 | 1 | 0 | 58.555 | 55.286 | 44.988 | 18.258 | 0 | 0 | 56.741 | 30.305 | [5 empty] | 0 | 11.275 | 9 | 4.5854 | 4.2834 | 4.2468 | 4 | 0.28342 | 6.1809
2006-03-12 | 10:16 | 0 | 15.692 | 0 | 5 | 0 | 54.184 | 54.688 | 42.628 | 43.004 | 262.353 | 26.595 | 7.133 | 1 | 0 | 58.555 | 55.309 | 45.012 | 18.258 | 0 | 0 | 56.718 | 30.305 | [5 empty] | 0 | 11.18 | 10 | 4.5193 | 4.2206 | 4.2441 | 4 | 0.22059 | 4.881
2006-03-12 | 10:17 | 0 | 15.714 | 0 | 4 | 0 | 54.184 | 54.665 | 42.628 | 42.98 | 251.85 | 26.62 | 6.551 | 2 | 0 | 58.534 | 55.263 | 45.035 | 18.236 | 0 | 0 | 56.741 | 30.33 | [5 empty] | 0 | 11.204 | 11 | 4.6887 | 4.3817 | 4.251 | 4 | 0.38168 | 8.1404
2006-03-12 | 10:18 | 0 | 15.764 | 0 | 5 | 0 | 54.184 | 54.665 | 42.721 | 42.886 | 249.915 | 26.691 | 6.855 | 1 | 0 | 58.555 | 55.263 | 45.012 | 18.236 | 0 | 0 | 56.761 | 30.403 | [5 empty] | 0 | 11.298 | 12 | 4.6002 | 4.2975 | 4.2474 | 4 | 0.29754 | 6.4679
2006-03-12 | 10:19 | 1 | 15.78 | 0 | 5 | 0 | 54.084 | 54.544 | 42.642 | 42.97 | 249.662 | 26.684 | 7.022 | 1 | 0 | 58.525 | 55.253 | 45.072 | 18.251 | 0 | 0 | 56.775 | 30.44 | [5 empty] | 15.78 | 11.114 | 13 | 4.5516 | 4.2513 | 4.2454 | 4 | 0.25131 | 5.5214
2006-03-12 | 10:20 | 0 | 15.724 | 0 | 4 | 1 | 54.056 | 54.492 | 42.683 | 42.824 | 252.806 | 26.75 | 6.865 | 1 | 0 | 58.52 | 55.225 | 45.021 | 18.221 | 0 | 0 | 56.77 | 30.435 | [5 empty] | 0 | 11.232 | 14 | 4.5973 | 4.2948 | 4.2473 | 4 | 0.29477 | 6.4117
2006-03-12 | 10:21 | 0 | 15.749 | 1 | 5 | 0 | 54.009 | 54.583 | 42.638 | 42.848 | 237.96 | 26.774 | 6.662 | 1 | 0 | 58.52 | 55.34 | 45.135 | 18.366 | 0 | 0 | 56.77 | 30.46 | [5 empty] | 0 | 11.161 | 0 | 4.6564 | 4.351 | 4.2497 | 4 | 0.35096 | 7.5371
2006-03-12 | 10:22 | 0 | 15.754 | 0 | 4 | 0 | 54.016 | 54.52 | 42.619 | 42.925 | 228.154 | 26.828 | 6.77 | 1 | 0 | 58.568 | 55.277 | 44.979 | 18.273 | 0 | 0 | 56.754 | 30.465 | [5 empty] | 0 | 11.091 | 1 | 4.625 | 4.3211 | 4.2484 | 4 | 0.32106 | 6.942
2006-03-12 | 10:23 | 1 | 15.805 | 0 | 5 | 0 | 53.993 | 54.497 | 42.595 | 42.925 | 259.656 | 26.85 | 6.389 | 1 | 0 | 58.548 | 55.253 | 45.026 | 18.299 | 0 | 0 | 56.754 | 30.489 | [5 empty] | 15.805 | 11.068 | 2 | 4.7359 | 4.4265 | 4.2529 | 4 | 0.42652 | 9.0062
2006-03-12 | 10:24 | 0 | 15.724 | 0 | 5 | 0 | 53.965 | 54.537 | 42.542 | 42.824 | 289.656 | 26.701 | 6.739 | 1 | 0 | 58.498 | 55.225 | 44.998 | 18.294 | 0 | 0 | 56.747 | 30.509 | [5 empty] | 0 | 11.141 | 3 | 4.634 | 4.3296 | 4.2488 | 4 | 0.32964 | 7.1136
2006-03-12 | 10:25 | 0 | 15.749 | 0 | 4 | 0 | 54.033 | 54.446 | 42.542 | 42.872 | 299.335 | 26.63 | 6.865 | 1 | 0 | 58.475 | 55.158 | 45.044 | 18.268 | 0 | 0 | 56.681 | 30.555 | [5 empty] | 0 | 11.161 | 4 | 4.5973 | 4.2948 | 4.2473 | 4 | 0.29477 | 6.4117
2006-03-12 | 10:26 | 0 | 15.754 | 0 | 5 | 0 | 54.037 | 54.565 | 42.525 | 42.853 | 308.465 | 26.706 | 6.618 | 1 | 0 | 58.502 | 55.23 | 45.002 | 18.299 | 0 | 0 | 56.686 | 30.609 | [5 empty] | 0 | 11.184 | 5 | 4.6692 | 4.3631 | 4.2502 | 4 | 0.36314 | 7.7772
2006-03-12 | 10:27 | 1 | 15.749 | 0 | 4 | 0 | 54.079 | 54.516 | 42.52 | 42.896 | 359.793 | 26.605 | 6.435 | 1 | 0 | 58.475 | 55.134 | 45.068 | 18.294 | 0 | 0 | 56.658 | 30.604 | [5 empty] | 15.749 | 11.183 | 6 | 4.7225 | 4.4138 | 4.2524 | 4 | 0.41379 | 8.7621
2006-03-12 | 10:28 | 0 | 15.754 | 0 | 5 | 0 | 54.131 | 54.588 | 42.477 | 42.807 | 372.259 | 26.706 | 6.566 | 2 | 0 | 58.525 | 55.23 | 45.117 | 18.349 | 0 | 0 | 56.663 | 30.683 | [5 empty] | 0 | 11.324 | 7 | 4.6844 | 4.3775 | 4.2508 | 4 | 0.37753 | 8.0594
2006-03-12 | 10:29 | 0 | 15.724 | 0 | 5 | 0 | 54.033 | 54.56 | 42.566 | 42.731 | 342.819 | 26.605 | 6.561 | 1 | 0 | 58.541 | 55.225 | 45.021 | 18.319 | 0 | 0 | 56.681 | 30.7 | [5 empty] | 0 | 11.302 | 8 | 4.6858 | 4.3789 | 4.2509 | 4 | 0.37892 | 8.0864
2006-03-12 | 10:30 | 0 | 15.729 | 1 | 4 | 0 | 54.061 | 54.497 | 42.619 | 42.831 | 356.075 | 26.755 | 6.314 | 1 | 0 | 58.502 | 55.162 | 45.072 | 18.299 | 0 | 0 | 56.686 | 30.779 | [5 empty] | 0 | 11.23 | 9 | 4.7578 | 4.4473 | 4.2538 | 4 | 0.44728 | 9.4012
2006-03-12 | 10:31 | 0 | 15.724 | 0 | 5 | 0 | 54.056 | 54.516 | 42.497 | 42.872 | 366.116 | 26.581 | 6.814 | 1 | 0 | 58.452 | 55.179 | 45.044 | 18.294 | 0 | 0 | 56.636 | 30.798 | [5 empty] | 0 | 11.184 | 10 | 4.6122 | 4.3089 | 4.2479 | 4 | 0.30888 | 6.6972
2006-03-12 | 10:32 | 1 | 15.729 | 0 | 4 | 0 | 54.061 | 54.497 | 42.525 | 42.831 | 342.02 | 26.635 | 6.896 | 1 | 0 | 58.479 | 55.139 | 45.117 | 18.349 | 0 | 0 | 56.663 | 30.828 | [5 empty] | 15.729 | 11.23 | 11 | 4.5883 | 4.2862 | 4.2469 | 4 | 0.28619 | 6.2373
2006-03-12 | 10:33 | 0 | 15.724 | 0 | 5 | 0 | 53.988 | 54.516 | 42.566 | 42.848 | 355.892 | 26.701 | 6.966 | 1 | 0 | 58.452 | 55.158 | 45.044 | 18.319 | 0 | 0 | 56.613 | 30.803 | [5 empty] | 0 | 11.14 | 12 | 4.5679 | 4.2668 | 4.2461 | 4 | 0.26681 | 5.841
2006-03-12 | 10:34 | 0 | 15.729 | 0 | 5 | 0 | 54.037 | 54.588 | 42.571 | 42.853 | 384.62 | 26.61 | 7.123 | 1 | 0 | 58.479 | 55.162 | 45.072 | 18.299 | 0 | 0 | 56.62 | 30.828 | [5 empty] | 0 | 11.184 | 13 | 4.5222 | 4.2234 | 4.2442 | 4 | 0.22335 | 4.9391
2006-03-12 | 10:35 | 0 | 15.724 | 0 | 4 | 1 | 54.079 | 54.492 | 42.566 | 42.965 | 341.014 | 26.556 | 6.839 | 1 | 0 | 58.429 | 55.088 | 45.112 | 18.268 | 0 | 0 | 56.569 | 30.82 | [5 empty] | 0 | 11.114 | 14 | 4.6049 | 4.302 | 4.2476 | 4 | 0.30196 | 6.5575
2006-03-12 | 10:36 | 1 | 15.78 | 0 | 5 | 0 | 54.084 | 54.544 | 42.642 | 42.994 | 321.841 | 26.564 | 6.793 | 2 | 0 | 58.434 | 55.116 | 45.096 | 18.324 | 0 | 0 | 56.663 | 30.899 | [5 empty] | 15.78 | 11.09 | 0 | 4.6183 | 4.3147 | 4.2481 | 4 | 0.3147 | 6.8142
2006-03-12 | 10:37 | 0 | 15.78 | 0 | 4 | 0 | 54.107 | 54.565 | 42.666 | 42.925 | 358.678 | 26.684 | 6.44 | 1 | 0 | 58.479 | 55.139 | 45.233 | 18.447 | 0 | 0 | 56.62 | 31.019 | [5 empty] | 0 | 11.182 | 1 | 4.7211 | 4.4124 | 4.2523 | 4 | 0.41241 | 8.7355
2006-03-12 | 10:38 | 0 | 15.749 | 0 | 5 | 0 | 54.147 | 54.537 | 42.614 | 42.989 | 406.97 | 26.461 | 6.662 | 1 | 0 | 58.406 | 55.043 | 45.112 | 18.319 | 0 | 0 | 56.592 | 30.918 | [5 empty] | 0 | 11.158 | 2 | 4.6564 | 4.351 | 4.2497 | 4 | 0.35096 | 7.5371
2006-03-12 | 10:39 | 0 | 15.697 | 0 | 5 | 0 | 54.1 | 54.537 | 42.635 | 42.941 | 389.646 | 26.578 | 6.533 | 1 | 0 | 58.429 | 55.088 | 45.089 | 18.316 | 0 | 0 | 56.569 | 30.987 | [5 empty] | 0 | 11.159 | 3 | 4.694 | 4.3867 | 4.2512 | 4 | 0.38667 | 8.2375
2006-03-12 | 10:40 | 1 | 15.752 | 1 | 4 | 0 | 54.128 | 54.611 | 42.619 | 42.901 | 283.618 | 26.561 | 6.842 | 1 | 0 | 58.479 | 55.069 | 45.093 | 18.321 | 0 | 0 | 56.551 | 31.016 | [5 empty] | 15.752 | 11.227 | 4 | 4.604 | 4.3011 | 4.2476 | 4 | 0.30113 | 6.5407
2006-03-12 | 10:41 | 0 | 15.697 | 0 | 5 | 0 | 54.056 | 54.492 | 42.707 | 42.941 | 270.338 | 26.652 | 7.015 | 2 | 0 | 58.452 | 55.064 | 45.042 | 18.341 | 0 | 0 | 56.501 | 31.036 | [5 empty] | 0 | 11.115 | 5 | 4.5536 | 4.2532 | 4.2455 | 4 | 0.25325 | 5.5615
2006-03-12 | 10:42 | 0 | 15.697 | 0 | 5 | 0 | 54.079 | 54.492 | 42.659 | 42.941 | 284.793 | 26.532 | 7.064 | 1 | 0 | 58.386 | 55.041 | 45.135 | 18.341 | 0 | 0 | 56.458 | 31.11 | [5 empty] | 0 | 11.138 | 6 | 4.5394 | 4.2397 | 4.2449 | 4 | 0.23968 | 5.2801
2006-03-12 | 10:43 | 0 | 15.674 | 0 | 4 | 0 | 53.986 | 54.537 | 42.635 | 43.059 | 350.772 | 26.434 | 7.19 | 1 | 0 | 58.386 | 55.018 | 45.226 | 18.316 | 0 | 0 | 56.412 | 31.11 | [5 empty] | 0 | 10.927 | 7 | 4.5027 | 4.2048 | 4.2435 | 4 | 0.20481 | 4.5486
2006-03-12 | 10:44 | 1 | 15.697 | 0 | 5 | 0 | 53.942 | 54.422 | 42.752 | 42.989 | 285.477 | 26.627 | 7.316 | 1 | 0 | 58.406 | 55.018 | 45.089 | 18.316 | 0 | 0 | 56.435 | 31.132 | [5 empty] | 15.697 | 10.953 | 8 | 4.466 | 4.1699 | 4.242 | 4 | 0.16993 | 3.805
2006-03-12 | 10:45 | 0 | 15.722 | 0 | 5 | 0 | 53.872 | 54.446 | 42.731 | 42.989 | 265.485 | 26.458 | 7.393 | 1 | 0 | 58.34 | 55.018 | 45.25 | 18.439 | 0 | 0 | 56.501 | 31.23 | [5 empty] | 0 | 10.883 | 9 | 4.4436 | 4.1486 | 4.2411 | 4 | 0.14862 | 3.3446
2006-03-12 | 10:46 | 0 | 15.722 | 0 | 4 | 0 | 53.71 | 54.238 | 42.683 | 43.083 | 300.95 | 26.483 | 6.886 | 1 | 0 | 58.34 | 55.041 | 45.203 | 18.341 | 0 | 0 | 56.458 | 31.132 | [5 empty] | 0 | 10.627 | 10 | 4.5912 | 4.289 | 4.247 | 4 | 0.28896 | 6.2937
2006-03-12 | 10:47 | 0 | 15.722 | 0 | 5 | 0 | 53.78 | 54.147 | 42.707 | 42.965 | 281.717 | 26.532 | 6.711 | 1 | 0 | 58.363 | 55.018 | 45.25 | 18.341 | 0 | 0 | 56.435 | 31.181 | [5 empty] | 0 | 10.815 | 11 | 4.6422 | 4.3374 | 4.2491 | 4 | 0.3374 | 7.2681
2006-03-12 | 10:48 | 0 | 15.722 | 0 | 5 | 0 | 53.666 | 54.147 | 42.752 | 43.013 | 253.606 | 26.507 | 6.685 | 1 | 0 | 58.34 | 54.973 | 45.18 | 18.341 | 0 | 0 | 56.412 | 31.205 | [5 empty] | 0 | 10.653 | 12 | 4.6497 | 4.3446 | 4.2494 | 4 | 0.34459 | 7.411
2006-03-12 | 10:49 | 1 | 15.722 | 1 | 4 | 0 | 53.596 | 54.17 | 42.731 | 42.989 | 255.712 | 26.723 | 6.533 | 1 | 0 | 58.363 | 54.997 | 45.135 | 18.366 | 0 | 0 | 56.524 | 31.181 | [5 empty] | 15.722 | 10.607 | 13 | 4.694 | 4.3867 | 4.2512 | 4 | 0.38667 | 8.2375
2006-03-12 | 10:50 | 0 | 15.772 | 0 | 5 | 1 | 53.643 | 54.17 | 42.752 | 42.965 | 241.96 | 26.723 | 6.203 | 1 | 0 | 58.363 | 55.018 | 45.112 | 18.341 | 0 | 0 | 56.501 | 31.23 | [5 empty] | 0 | 10.678 | 14 | 4.7901 | 4.478 | 4.2551 | 4 | 0.47801 | 9.9791
2006-03-12 | 10:51 | 0 | 15.772 | 0 | 5 | 0 | 53.643 | 54.079 | 42.707 | 43.035 | 261.827 | 26.556 | 6.533 | 2 | 0 | 58.317 | 54.95 | 45.156 | 18.341 | 0 | 0 | 56.458 | 31.254 | [5 empty] | 0 | 10.608 | 0 | 4.694 | 4.3867 | 4.2512 | 4 | 0.38667 | 8.2375
2006-03-12 | 10:52 | 0 | 15.772 | 0 | 4 | 0 | 53.619 | 54.1 | 42.707 | 42.941 | 278.963 | 26.556 | 7.115 | 1 | 0 | 58.34 | 54.973 | 45.135 | 18.341 | 0 | 0 | 56.458 | 31.254 | [5 empty] | 0 | 10.678 | 1 | 4.5245 | 4.2256 | 4.2443 | 4 | 0.22557 | 4.9855
2006-03-12 | 10:53 | 1 | 15.747 | 0 | 5 | 0 | 53.573 | 54.079 | 42.731 | 42.941 | 270.511 | 26.578 | 7.141 | 1 | 0 | 58.34 | 54.95 | 45.135 | 18.366 | 0 | 0 | 56.458 | 31.301 | [5 empty] | 15.747 | 10.632 | 2 | 4.5169 | 4.2184 | 4.244 | 4 | 0.21837 | 4.8345
2006-03-12 | 10:54 | 0 | 15.772 | 0 | 4 | 0 | 53.666 | 54.056 | 42.59 | 42.965 | 273.281 | 26.532 | 6.76 | 1 | 0 | 58.317 | 54.926 | 45.203 | 18.341 | 0 | 0 | 56.343 | 31.325 | [5 empty] | 0 | 10.701 | 3 | 4.6279 | 4.3238 | 4.2485 | 4 | 0.32383 | 6.9974
2006-03-12 | 10:55 | 0 | 15.772 | 0 | 5 | 0 | 53.643 | 54.1 | 42.59 | 42.918 | 273.626 | 26.507 | 6.28 | 1 | 0 | 58.295 | 54.973 | 45.135 | 18.389 | 0 | 0 | 56.366 | 31.301 | [5 empty] | 0 | 10.725 | 4 | 4.7677 | 4.4567 | 4.2542 | 4 | 0.4567 | 9.579
2006-03-12 | 10:56 | 0 | 15.772 | 0 | 5 | 0 | 53.573 | 54.1 | 42.683 | 42.894 | 255.538 | 26.532 | 6.177 | 1 | 0 | 58.295 | 54.903 | 45.203 | 18.341 | 0 | 0 | 56.343 | 31.301 | [5 empty] | 0 | 10.679 | 5 | 4.7977 | 4.4852 | 4.2554 | 4 | 0.48521 | 10.1134
2006-03-12 | 10:57 | 1 | 15.772 | 0 | 4 | 0 | 53.643 | 54.033 | 42.752 | 42.894 | 280.512 | 26.556 | 6.154 | 1 | 0 | 58.295 | 54.903 | 45.18 | 18.341 | 0 | 0 | 56.323 | 31.325 | [5 empty] | 15.772 | 10.749 | 6 | 4.8044 | 4.4916 | 4.2557 | 4 | 0.49157 | 10.2318
2006-03-12 | 10:58 | 0 | 15.764 | 1 | 5 | 0 | 53.727 | 54.093 | 42.58 | 42.91 | 266.674 | 26.451 | 6.399 | 1 | 0 | 58.242 | 54.873 | 45.184 | 18.296 | 0 | 0 | 56.282 | 31.281 | [5 empty] | 0 | 10.817 | 7 | 4.733 | 4.4238 | 4.2528 | 4 | 0.42376 | 8.9532
2006-03-12 | 10:59 | 0 | 15.815 | 0 | 5 | 0 | 53.911 | 54.233 | 42.652 | 42.889 | 259.228 | 26.524 | 6.551 | 1 | 0 | 58.288 | 54.898 | 45.243 | 18.384 | 0 | 0 | 56.316 | 31.318 | [5 empty] | 0 | 11.022 | 8 | 4.6887 | 4.3817 | 4.251 | 4 | 0.38168 | 8.1404
2006-03-12 | 11:00 | 0 | 15.815 | 0 | 4 | 0 | 53.888 | 54.278 | 42.535 | 42.889 | 246.242 | 26.429 | 6.474 | 1 | 0 | 58.288 | 54.875 | 45.289 | 18.384 | 0 | 0 | 56.248 | 31.343 | [5 empty] | 0 | 10.999 | 9 | 4.7112 | 4.403 | 4.2519 | 4 | 0.403 | 8.5541
2006-03-12 | 11:01 | 0 | 15.847 | 0 | 5 | 0 | 54.012 | 54.401 | 42.59 | 42.848 | 262.047 | 26.485 | 6.636 | 1 | 0 | 58.317 | 54.882 | 45.226 | 18.417 | 0 | 0 | 56.369 | 31.47 | [5 empty] | 0 | 11.164 | 10 | 4.664 | 4.3582 | 4.25 | 4 | 0.35816 | 7.6791
2006-03-12 | 11:02 | 1 | 15.815 | 0 | 5 | 0 | 54.026 | 54.348 | 42.607 | 42.817 | 335.2 | 26.524 | 6.651 | 1 | 0 | 58.288 | 54.828 | 45.152 | 18.334 | 0 | 0 | 56.27 | 31.367 | [5 empty] | 15.815 | 11.209 | 11 | 4.6596 | 4.354 | 4.2498 | 4 | 0.354 | 7.5972
2006-03-12 | 11:03 | 0 | 15.822 | 0 | 4 | 0 | 54.103 | 54.539 | 42.638 | 42.824 | 345.905 | 26.507 | 6.736 | 2 | 0 | 58.317 | 54.882 | 45.182 | 18.341 | 0 | 0 | 56.323 | 31.448 | [5 empty] | 0 | 11.279 | 12 | 4.6349 | 4.3305 | 4.2488 | 4 | 0.33048 | 7.1302
2006-03-12 | 11:04 | 0 | 15.79 | 0 | 5 | 0 | 53.958 | 54.576 | 42.465 | 42.841 | 406.97 | 26.355 | 5.994 | 1 | 0 | 58.244 | 54.805 | 45.219 | 18.334 | 0 | 0 | 56.248 | 31.438 | [5 empty] | 0 | 11.117 | 13 | 4.8509 | 4.5359 | 4.2576 | 4 | 0.53586 | 11.0465
2006-03-12 | 11:05 | 0 | 15.714 | 0 | 4 | 1 | 53.981 | 54.462 | 42.465 | 42.772 | 356.007 | 26.404 | 6.399 | 1 | 0 | 58.267 | 54.852 | 45.266 | 18.359 | 0 | 0 | 56.248 | 31.438 | [5 empty] | 0 | 11.209 | 14 | 4.733 | 4.4238 | 4.2528 | 4 | 0.42376 | 8.9532
2006-03-12 | 11:06 | 1 | 15.797 | 0 | 5 | 0 | 54.012 | 54.516 | 42.52 | 42.872 | 312.27 | 26.363 | 6.332 | 1 | 0 | 58.274 | 54.835 | 45.296 | 18.392 | 0 | 0 | 56.257 | 31.495 | [5 empty] | 15.797 | 11.14 | 0 | 4.7525 | 4.4423 | 4.2536 | 4 | 0.4423 | 9.3067
2006-03-12 | 11:07 | 0 | 15.739 | 0 | 5 | 0 | 54.049 | 54.53 | 42.511 | 42.793 | 362.176 | 26.429 | 6.626 | 1 | 0 | 58.244 | 54.828 | 45.243 | 18.359 | 0 | 0 | 56.181 | 31.438 | [5 empty] | 0 | 11.256 | 1 | 4.6669 | 4.3609 | 4.2501 | 4 | 0.36092 | 7.7337
2006-03-12 | 11:08 | 0 | 15.747 | 1 | 4 | 0 | 54.103 | 54.583 | 42.566 | 42.824 | 323.457 | 26.387 | 6.659 | 1 | 0 | 58.274 | 54.859 | 45.273 | 18.417 | 0 | 0 | 56.234 | 31.448 | [5 empty] | 0 | 11.279 | 2 | 4.6573 | 4.3518 | 4.2497 | 4 | 0.35179 | 7.5535
2006-03-12 | 11:09 | 0 | 15.747 | 0 | 5 | 0 | 53.965 | 54.583 | 42.59 | 42.803 | 294.722 | 26.387 | 6.685 | 1 | 0 | 58.251 | 54.814 | 45.182 | 18.392 | 0 | 0 | 56.3 | 31.448 | [5 empty] | 0 | 11.162 | 3 | 4.6497 | 4.3446 | 4.2494 | 4 | 0.34459 | 7.411
2006-03-12 | 11:10 | 1 | 15.739 | 0 | 4 | 0 | 53.958 | 54.324 | 42.535 | 42.982 | 307.048 | 26.475 | 6.778 | 1 | 0 | 58.222 | 54.805 | 45.196 | 18.384 | 0 | 0 | 56.27 | 31.438 | [5 empty] | 15.739 | 10.976 | 4 | 4.6226 | 4.3188 | 4.2483 | 4 | 0.31885 | 6.8976
2006-03-12 | 11:11 | 0 | 15.772 | 0 | 5 | 0 | 53.851 | 54.516 | 42.638 | 42.92 | 280.21 | 26.507 | 6.458 | 1 | 0 | 58.251 | 54.814 | 45.32 | 18.392 | 0 | 0 | 56.211 | 31.495 | [5 empty] | 0 | 10.931 | 5 | 4.7158 | 4.4074 | 4.2521 | 4 | 0.40743 | 8.6395
2006-03-12 | 11:12 | 0 | 15.747 | 0 | 4 | 0 | 53.736 | 54.24 | 42.614 | 42.896 | 295.742 | 26.556 | 6.206 | 1 | 0 | 58.251 | 54.835 | 45.226 | 18.366 | 0 | 0 | 56.234 | 31.495 | [5 empty] | 0 | 10.84 | 6 | 4.7892 | 4.4772 | 4.2551 | 4 | 0.47718 | 9.9636
2006-03-12 | 11:13 | 0 | 15.739 | 0 | 5 | 0 | 53.935 | 54.21 | 42.652 | 42.865 | 329.576 | 26.549 | 6.45 | 2 | 0 | 58.244 | 54.784 | 45.243 | 18.359 | 0 | 0 | 56.227 | 31.487 | [5 empty] | 0 | 11.07 | 7 | 4.7182 | 4.4096 | 4.2522 | 4 | 0.40964 | 8.6822
2006-03-12 | 11:14 | 0 | 15.739 | 0 | 5 | 0 | 53.911 | 54.439 | 42.7 | 42.91 | 327.09 | 26.429 | 6.729 | 1 | 0 | 58.244 | 54.761 | 45.175 | 18.507 | 0 | 0 | 56.248 | 31.463 | [5 empty] | 0 | 11.001 | 8 | 4.6369 | 4.3324 | 4.2489 | 4 | 0.33241 | 7.1688
2006-03-12 | 11:15 | 1 | 15.772 | 0 | 4 | 0 | 53.988 | 54.401 | 42.683 | 42.896 | 293.874 | 26.412 | 6.811 | 1 | 0 | 58.274 | 54.768 | 45.205 | 18.392 | 0 | 0 | 56.234 | 31.495 | [5 empty] | 15.772 | 11.092 | 9 | 4.613 | 4.3097 | 4.2479 | 4 | 0.30972 | 6.7139
2006-03-12 | 11:16 | 0 | 15.797 | 0 | 5 | 0 | 53.988 | 54.355 | 42.566 | 42.941 | 316.291 | 26.387 | 6.837 | 1 | 0 | 58.206 | 54.791 | 45.226 | 18.417 | 0 | 0 | 56.188 | 31.519 | [5 empty] | 0 | 11.047 | 10 | 4.6055 | 4.3025 | 4.2476 | 4 | 0.30252 | 6.5687
2006-03-12 | 11:17 | 0 | 15.772 | 1 | 4 | 0 | 53.918 | 54.446 | 42.566 | 42.872 | 290.988 | 26.461 | 6.507 | 1 | 0 | 58.206 | 54.744 | 45.296 | 18.417 | 0 | 0 | 56.234 | 31.568 | [5 empty] | 0 | 11.046 | 11 | 4.7016 | 4.3939 | 4.2515 | 4 | 0.39386 | 8.3773
2006-03-12 | 11:18 | 0 | 15.714 | 0 | 5 | 0 | 53.981 | 54.324 | 42.676 | 42.865 | 321.101 | 26.429 | 6.474 | 1 | 0 | 58.155 | 54.691 | 45.243 | 18.384 | 0 | 0 | 56.179 | 31.512 | [5 empty] | 0 | 11.116 | 12 | 4.7112 | 4.403 | 4.2519 | 4 | 0.403 | 8.5541
2006-03-12 | 11:19 | 1 | 15.722 | 0 | 5 | 0 | 53.939 | 54.306 | 42.611 | 42.822 | 292.621 | 26.507 | 6.912 | 1 | 0 | 58.158 | 54.649 | 45.133 | 18.291 | 0 | 0 | 56.117 | 31.517 | [5 empty] | 15.722 | 11.117 | 13 | 4.5836 | 4.2818 | 4.2467 | 4 | 0.28176 | 6.1471
2006-03-12 | 11:20 | 0 | 15.722 | 0 | 4 | 1 | 53.825 | 54.534 | 42.494 | 42.894 | 278.253 | 26.603 | 7.241 | 1 | 0 | 58.114 | 54.672 | 45.201 | 18.364 | 0 | 0 | 56.117 | 31.541 | [5 empty] | 0 | 10.931 | 14 | 4.4878 | 4.1907 | 4.2429 | 4 | 0.19069 | 4.2491
2006-03-12 | 11:21 | 0 | 15.722 | 0 | 5 | 0 | 53.755 | 54.215 | 42.635 | 42.798 | 310.864 | 26.554 | 7.393 | 1 | 0 | 58.158 | 54.649 | 45.18 | 18.316 | 0 | 0 | 56.163 | 31.517 | [5 empty] | 0 | 10.957 | 0 | 4.4436 | 4.1486 | 4.2411 | 4 | 0.14862 | 3.3446
2006-03-12 | 11:22 | 0 | 15.697 | 0 | 4 | 0 | 53.664 | 54.191 | 42.494 | 42.752 | 273.262 | 26.529 | 7.795 | 1 | 0 | 58.135 | 54.672 | 45.156 | 18.364 | 0 | 0 | 56.163 | 31.517 | [5 empty] | 0 | 10.912 | 1 | 4.3265 | 4.0373 | 3.9863 | 3.75 | 0.28734 | 6.6415
2006-03-12 | 11:23 | 1 | 15.747 | 0 | 5 | 0 | 53.755 | 54.191 | 42.54 | 42.822 | 269.971 | 26.747 | 8.117 | 1 | 0 | 58.135 | 54.628 | 45.18 | 18.364 | 0 | 0 | 56.186 | 31.541 | [5 empty] | 15.747 | 10.933 | 2 | 4.2327 | 3.9482 | 3.9825 | 3.75 | 0.19821 | 4.6829
2006-03-12 | 11:24 | 0 | 15.722 | 0 | 5 | 0 | 53.664 | 54.191 | 42.54 | 42.798 | 310.697 | 26.554 | 7.393 | 1 | 0 | 58.135 | 54.628 | 45.18 | 18.364 | 0 | 0 | 56.117 | 31.541 | [5 empty] | 0 | 10.866 | 3 | 4.4436 | 4.1486 | 3.9911 | 3.75 | 0.39862 | 8.9707
2006-03-12 | 11:25 | 0 | 15.697 | 0 | 4 | 0 | 53.664 | 54.1 | 42.518 | 42.822 | 353.357 | 26.627 | 7.845 | 1 | 0 | 58.069 | 54.628 | 45.201 | 18.389 | 0 | 0 | 56.093 | 31.566 | [5 empty] | 0 | 10.842 | 4 | 4.3119 | 4.0235 | 3.9857 | 3.75 | 0.2735 | 6.343
2006-03-12 | 11:26 | 0 | 15.671 | 1 | 5 | 0 | 53.731 | 54.121 | 42.281 | 42.87 | 343.383 | 26.674 | 8.117 | 2 | 0 | 58.091 | 54.628 | 45.338 | 18.439 | 0 | 0 | 56.002 | 31.615 | [5 empty] | 0 | 10.861 | 5 | 4.2327 | 3.9482 | 3.9825 | 3.75 | 0.19821 | 4.6829
2006-03-12 | 11:27 | 0 | 15.727 | 0 | 4 | 0 | 53.738 | 54.149 | 42.265 | 42.851 | 342.911 | 26.657 | 8.197 | 1 | 0 | 58.096 | 54.609 | 45.252 | 18.444 | 0 | 0 | 56.054 | 31.62 | [5 empty] | 0 | 10.887 | 6 | 4.2094 | 3.9261 | 3.9816 | 3.75 | 0.17607 | 4.1828
2006-03-12 | 11:28 | 1 | 15.671 | 0 | 5 | 0 | 53.71 | 54.145 | 42.377 | 42.752 | 286.141 | 26.772 | 8.24 | 1 | 0 | 58.069 | 54.628 | 45.201 | 18.364 | 0 | 0 | 56.049 | 31.566 | [5 empty] | 15.671 | 10.958 | 7 | 4.1969 | 3.9142 | 3.9811 | 3.75 | 0.16417 | 3.9116
2006-03-12 | 11:29 | 0 | 15.649 | 0 | 4 | 0 | 53.687 | 54.168 | 42.119 | 42.659 | 270.144 | 26.698 | 7.368 | 1 | 0 | 58.046 | 54.628 | 45.18 | 18.414 | 0 | 0 | 55.956 | 31.566 | [5 empty] | 0 | 11.028 | 8 | 4.4508 | 4.1555 | 3.9914 | 3.75 | 0.40554 | 9.1115
2006-03-12 | 11:30 | 0 | 15.727 | 0 | 4 | 0 | 53.806 | 54.173 | 42.217 | 42.523 | 245.512 | 26.873 | 7.85 | 1 | 0 | 58.096 | 54.609 | 45.208 | 18.47 | 0 | 0 | 55.984 | 31.62 | [5 empty] | 0 | 11.283 | 9 | 4.3105 | 4.0221 | 3.9857 | 3.75 | 0.27212 | 6.313
2006-03-12 | 11:31 | 0 | 15.697 | 0 | 4 | 0 | 53.687 | 54.168 | 42.023 | 42.305 | 253.939 | 26.772 | 7.943 | 1 | 0 | 58.069 | 54.558 | 45.18 | 18.439 | 0 | 0 | 55.935 | 31.566 | [5 empty] | 0 | 11.382 | 10 | 4.2834 | 3.9964 | 3.9846 | 3.75 | 0.24638 | 5.7519
2006-03-12 | 11:32 | 1 | 15.752 | 0 | 4 | 0 | 53.806 | 54.149 | 41.887 | 42.265 | 259.909 | 26.728 | 8.172 | 1 | 0 | 58.05 | 54.539 | 45.229 | 18.47 | 0 | 0 | 55.963 | 31.666 | [5 empty] | 15.752 | 11.541 | 11 | 4.2167 | 3.933 | 3.9819 | 3.75 | 0.18299 | 4.3396
2006-03-12 | 11:33 | 0 | 15.727 | 0 | 4 | 0 | 53.944 | 54.173 | 41.7 | 42.123 | 242.673 | 26.752 | 8.22 | 1 | 0 | 58.05 | 54.539 | 45.229 | 18.419 | 0 | 0 | 55.963 | 31.691 | [5 empty] | 0 | 11.821 | 12 | 4.2027 | 3.9197 | 3.9813 | 3.75 | 0.1697 | 4.0379
2006-03-12 | 11:34 | 0 | 15.752 | 0 | 4 | 0 | 53.991 | 54.357 | 41.607 | 41.841 | 301.962 | 26.801 | 7.999 | 1 | 0 | 58.05 | 54.539 | 45.208 | 18.419 | 0 | 0 | 56.007 | 31.666 | [5 empty] | 0 | 12.15 | 13 | 4.2671 | 3.9809 | 3.9839 | 3.75 | 0.23088 | 5.4106
2006-03-12 | 11:35 | 0 | 15.702 | 0 | 4 | 0 | 54.012 | 54.357 | 41.324 | 41.769 | 266.699 | 26.777 | 8.295 | 1 | 0 | 58.05 | 54.539 | 45.299 | 18.419 | 0 | 0 | 55.984 | 31.666 | [5 empty] | 0 | 12.243 | 14 | 4.1809 | 3.8989 | 3.9804 | 3.75 | 0.14894 | 3.5625
2006-03-12 | 11:36 | 0 | 15.649 | 1 | 4 | 1 | 54.352 | 54.329 | 41.083 | 41.482 | 297.205 | 26.797 | 7.795 | 2 | 0 | 58.002 | 54.467 | 45.133 | 18.414 | 0 | 0 | 55.935 | 31.661 | [5 empty] | 0 | 12.87 | 15 | 4.3265 | 4.0373 | 3.9863 | 3.75 | 0.28734 | 6.6415
2006-03-12 | 11:37 | 1 | 15.679 | 0 | 4 | 0 | 54.31 | 54.747 | 41.066 | 41.37 | 269.647 | 26.848 | 8.22 | 1 | 0 | 58.03 | 54.518 | 45.161 | 18.419 | 0 | 0 | 55.963 | 31.691 | [5 empty] | 15.679 | 12.94 | 0 | 4.2027 | 3.9197 | 3.9813 | 3.75 | 0.1697 | 4.0379
2006-03-12 | 11:38 | 0 | 15.654 | 0 | 3 | 0 | 54.266 | 54.609 | 40.76 | 41.135 | 406.97 | 26.728 | 8.049 | 1 | 0 | 58.03 | 54.539 | 45.114 | 18.482 | 0 | 0 | 55.928 | 31.728 | [5 empty] | 0 | 13.131 | 1 | 4.2525 | 3.967 | 3.7627 | 3.5294 | 0.43763 | 10.2909
2006-03-12 | 11:39 | 0 | 15.656 | 0 | 4 | 0 | 54.544 | 54.658 | 40.573 | 41.114 | 406.97 | 26.61 | 7.878 | 1 | 0 | 58.032 | 54.474 | 45.254 | 18.497 | 0 | 0 | 55.918 | 31.791 | [5 empty] | 0 | 13.43 | 2 | 4.3023 | 4.0144 | 3.7648 | 3.5294 | 0.48496 | 11.272
2006-03-12 | 11:40 | 0 | 15.682 | 0 | 3 | 0 | 54.52 | 54.954 | 40.573 | 40.832 | 306.615 | 26.659 | 7.828 | 1 | 0 | 58.032 | 54.497 | 45.14 | 18.447 | 0 | 0 | 55.851 | 31.838 | [5 empty] | 0 | 13.688 | 3 | 4.3169 | 4.0282 | 3.7653 | 3.5294 | 0.4988 | 11.5546
2006-03-12 | 11:41 | 1 | 15.682 | 0 | 4 | 0 | 54.406 | 54.863 | 40.621 | 40.81 | 264.891 | 26.73 | 7.656 | 1 | 0 | 58.009 | 54.497 | 45.187 | 18.472 | 0 | 0 | 55.851 | 31.862 | [5 empty] | 15.682 | 13.596 | 4 | 4.367 | 4.0758 | 3.7674 | 3.5294 | 0.54641 | 12.5123
2006-03-12 | 11:42 | 0 | 15.682 | 0 | 3 | 0 | 54.474 | 54.749 | 40.456 | 40.738 | 286.087 | 26.659 | 8.124 | 1 | 0 | 58.009 | 54.474 | 45.21 | 18.472 | 0 | 0 | 55.872 | 31.838 | [5 empty] | 0 | 13.736 | 5 | 4.2307 | 3.9463 | 3.7618 | 3.5294 | 0.41687 | 9.8534
2006-03-12 | 11:43 | 0 | 15.739 | 0 | 4 | 0 | 54.642 | 54.894 | 40.346 | 40.604 | 308.32 | 26.691 | 7.86 | 1 | 0 | 58.082 | 54.481 | 45.147 | 18.505 | 0 | 0 | 55.881 | 31.87 | [5 empty] | 0 | 14.038 | 6 | 4.3076 | 4.0194 | 3.765 | 3.5294 | 0.48994 | 11.3739
2006-03-12 | 11:44 | 0 | 15.714 | 0 | 3 | 0 | 54.733 | 55.008 | 40.418 | 40.559 | 316.53 | 26.907 | 7.911 | 2 | 0 | 58.128 | 54.527 | 45.308 | 18.578 | 0 | 0 | 55.925 | 31.845 | [5 empty] | 0 | 14.174 | 7 | 4.2927 | 4.0052 | 3.7644 | 3.5294 | 0.47582 | 11.0844
2006-03-12 | 11:45 | 0 | 15.682 | 1 | 3 | 0 | 54.863 | 55.025 | 40.291 | 40.48 | 297.831 | 26.706 | 7.951 | 1 | 0 | 58.032 | 54.427 | 45.096 | 18.447 | 0 | 0 | 55.872 | 31.838 | [5 empty] | 0 | 14.383 | 8 | 4.2811 | 3.9942 | 3.7639 | 3.5294 | 0.46475 | 10.856
2006-03-12 | 11:46 | 1 | 15.656 | 0 | 3 | 0 | 54.91 | 55.23 | 40.174 | 40.411 | 291.04 | 26.73 | 7.803 | 1 | 0 | 58.009 | 54.474 | 45.233 | 18.472 | 0 | 0 | 55.895 | 31.791 | [5 empty] | 15.656 | 14.499 | 9 | 4.3242 | 4.0351 | 3.7656 | 3.5294 | 0.50572 | 11.6952
2006-03-12 | 11:47 | 0 | 15.714 | 0 | 4 | 0 | 54.847 | 55.237 | 40.205 | 40.418 | 259.855 | 26.716 | 8.207 | 1 | 0 | 58.039 | 54.457 | 45.24 | 18.505 | 0 | 0 | 55.925 | 31.823 | [5 empty] | 0 | 14.429 | 10 | 4.2065 | 3.9233 | 3.7609 | 3.5294 | 0.39389 | 9.3638
2006-03-12 | 11:48 | 0 | 15.714 | 0 | 3 | 0 | 54.826 | 55.237 | 40.205 | 40.418 | 265.26 | 26.811 | 7.984 | 1 | 0 | 58.016 | 54.481 | 45.103 | 18.505 | 0 | 0 | 55.925 | 31.845 | [5 empty] | 0 | 14.408 | 11 | 4.2715 | 3.985 | 3.7635 | 3.5294 | 0.45562 | 10.6665
2006-03-12 | 11:49 | 0 | 15.707 | 0 | 3 | 0 | 54.817 | 55.162 | 40.222 | 40.363 | 255.289 | 26.85 | 7.478 | 1 | 0 | 58.032 | 54.427 | 45.14 | 18.472 | 0 | 0 | 55.918 | 31.813 | [5 empty] | 0 | 14.454 | 12 | 4.4188 | 4.1251 | 3.7695 | 3.5294 | 0.59568 | 13.4805
2006-03-12 | 11:50 | 0 | 15.707 | 0 | 3 | 0 | 54.796 | 55.139 | 40.081 | 40.315 | 238.87 | 26.804 | 7.679 | 1 | 0 | 58.009 | 54.45 | 45.072 | 18.522 | 0 | 0 | 55.942 | 31.791 | [5 empty] | 0 | 14.481 | 13 | 4.3603 | 4.0695 | 3.7671 | 3.5294 | 0.54004 | 12.3855
2006-03-12 | 11:51 | 1 | 15.707 | 0 | 4 | 0 | 54.978 | 55.162 | 40.033 | 40.246 | 275.445 | 26.804 | 7.755 | 1 | 0 | 58.009 | 54.427 | 45.072 | 18.497 | 0 | 0 | 55.872 | 31.791 | [5 empty] | 15.707 | 14.732 | 14 | 4.3381 | 4.0484 | 3.7662 | 3.5294 | 0.519 | 11.9637
2006-03-12 | 11:52 | 0 | 15.707 | 0 | 3 | 0 | 55.139 | 55.323 | 40.033 | 40.174 | 259.832 | 26.779 | 8.099 | 2 | 0 | 57.964 | 54.427 | 45.117 | 18.522 | 0 | 0 | 55.872 | 31.813 | [5 empty] | 0 | 14.965 | 15 | 4.238 | 3.9532 | 3.7621 | 3.5294 | 0.42379 | 9.9997
2006-03-12 | 11:53 | 0 | 15.707 | 0 | 3 | 1 | 55.186 | 55.461 | 39.87 | 40.174 | 295.624 | 26.61 | 8.001 | 1 | 0 | 57.941 | 54.359 | 45.14 | 18.472 | 0 | 0 | 55.827 | 31.838 | [5 empty] | 0 | 15.012 | 16 | 4.2665 | 3.9803 | 3.7633 | 3.5294 | 0.45091 | 10.5686
2006-03-12 | 11:54 | 0 | 15.682 | 1 | 3 | 0 | 55.3 | 55.461 | 39.822 | 40.15 | 312.152 | 26.635 | 7.527 | 1 | 0 | 57.964 | 54.359 | 45.14 | 18.497 | 0 | 0 | 55.851 | 31.813 | [5 empty] | 0 | 15.15 | 0 | 4.4045 | 4.1115 | 3.7689 | 3.5294 | 0.58211 | 13.2162
2006-03-12 | 11:55 | 0 | 15.707 | 0 | 3 | 0 | 55.186 | 55.596 | 39.846 | 39.987 | 275.445 | 26.706 | 8.026 | 1 | 0 | 57.964 | 54.359 | 45.117 | 18.497 | 0 | 0 | 55.827 | 31.791 | [5 empty] | 0 | 15.199 | 1 | 4.2592 | 3.9734 | 3.9836 | 3.75 | 0.2234 | 5.2452
2006-03-12 | 11:56 | 1 | 15.739 | 0 | 3 | 0 | 55.216 | 55.559 | 39.901 | 40.064 | 253.731 | 26.882 | 8.109 | 1 | 0 | 58.016 | 54.413 | 45.126 | 18.555 | 0 | 0 | 55.858 | 31.845 | [5 empty] | 15.739 | 15.152 | 2 | 4.2351 | 3.9504 | 3.9826 | 3.75 | 0.20043 | 4.7326
2006-03-12 | 11:57 | 0 | 15.714 | 0 | 4 | 0 | 55.237 | 55.559 | 39.829 | 40.088 | 251.443 | 26.716 | 8.132 | 1 | 0 | 57.971 | 54.39 | 45.24 | 18.53 | 0 | 0 | 55.902 | 31.823 | [5 empty] | 0 | 15.149 | 3 | 4.2284 | 3.9441 | 3.9823 | 3.75 | 0.19406 | 4.5895
2006-03-12 | 11:58 | 0 | 15.707 | 0 | 3 | 0 | 55.253 | 55.482 | 39.87 | 39.963 | 279.059 | 26.73 | 8.052 | 1 | 0 | 57.964 | 54.336 | 45.163 | 18.522 | 0 | 0 | 55.872 | 31.816 | [5 empty] | 0 | 15.29 | 4 | 4.2517 | 3.9662 | 3.9833 | 3.75 | 0.21621 | 5.0852
2006-03-12 | 11:59 | 0 | 15.702 | 0 | 3 | 0 | 55.344 | 55.617 | 39.796 | 40.006 | 268.4 | 26.777 | 7.971 | 2 | 0 | 57.961 | 54.38 | 45.229 | 18.542 | 0 | 0 | 55.963 | 31.811 | [5 empty] | 0 | 15.338 | 5 | 4.2752 | 3.9886 | 3.9842 | 3.75 | 0.23863 | 5.5816
2006-03-12 | 12:00 | 1 | 15.722 | 0 | 3 | 0 | 55.27 | 55.613 | 39.837 | 40.002 | 264.565 | 26.77 | 8.313 | 1 | 0 | 57.957 | 54.352 | 45.156 | 18.635 | 0 | 0 | 55.865 | 31.83 | [5 empty] | 15.722 | 15.268 | 6 | 4.1757 | 3.894 | 3.9802 | 3.75 | 0.14396 | 3.4476
2006-03-12 | 12:01 | 0 | 15.697 | 0 | 3 | 0 | 55.132 | 55.636 | 39.861 | 39.978 | 248.275 | 26.747 | 7.918 | 1 | 0 | 57.934 | 54.352 | 45.086 | 18.512 | 0 | 0 | 55.958 | 31.855 | [5 empty] | 0 | 15.154 | 7 | 4.2907 | 4.0033 | 3.9849 | 3.75 | 0.2533 | 5.9034
2006-03-12 | 12:02 | 0 | 15.752 | 0 | 3 | 0 | 55.251 | 55.573 | 39.889 | 40.126 | 222.236 | 26.752 | 7.898 | 1 | 0 | 57.984 | 54.357 | 45.275 | 18.542 | 0 | 0 | 55.825 | 31.884 | [5 empty] | 0 | 15.125 | 8 | 4.2965 | 4.0088 | 3.9851 | 3.75 | 0.25883 | 6.0243
2006-03-12 | 12:03 | 0 | 15.744 | 0 | 3 | 0 | 55.179 | 55.545 | 39.861 | 39.932 | 262.647 | 26.77 | 7.795 | 1 | 0 | 57.957 | 54.352 | 45.18 | 18.512 | 0 | 0 | 55.774 | 31.806 | [5 empty] | 0 | 15.247 | 9 | 4.3265 | 4.0373 | 3.9863 | 3.75 | 0.28734 | 6.6415
2006-03-12 | 12:04 | 0 | 15.722 | 1 | 4 | 0 | 55.132 | 55.522 | 39.815 | 39.956 | 284.227 | 26.747 | 7.918 | 1 | 0 | 57.934 | 54.306 | 45.133 | 18.512 | 0 | 0 | 55.75 | 31.855 | [5 empty] | 0 | 15.176 | 10 | 4.2907 | 4.0033 | 3.9849 | 3.75 | 0.2533 | 5.9034
2006-03-12 | 12:05 | 1 | 15.744 | 0 | 3 | 0 | 54.947 | 55.475 | 39.743 | 40.073 | 241.375 | 26.698 | 7.77 | 2 | 0 | 57.934 | 54.329 | 45.11 | 18.585 | 0 | 0 | 55.75 | 31.855 | [5 empty] | 15.744 | 14.874 | 11 | 4.3338 | 4.0443 | 3.9866 | 3.75 | 0.29426 | 6.79
2006-03-12 | 12:06 | 0 | 15.697 | 0 | 3 | 0 | 54.81 | 55.27 | 39.696 | 39.932 | 240.842 | 26.868 | 7.795 | 1 | 0 | 57.934 | 54.306 | 45.11 | 18.56 | 0 | 0 | 55.727 | 31.806 | [5 empty] | 0 | 14.878 | 12 | 4.3265 | 4.0373 | 3.9863 | 3.75 | 0.28734 | 6.6415
2006-03-12 | 12:07 | 0 | 15.727 | 0 | 3 | 0 | 54.817 | 55.183 | 39.772 | 39.913 | 233.56 | 26.848 | 7.923 | 1 | 0 | 57.961 | 54.31 | 45.184 | 18.59 | 0 | 0 | 55.778 | 31.907 | [5 empty] | 0 | 14.904 | 13 | 4.2892 | 4.0019 | 3.9848 | 3.75 | 0.25191 | 5.8732
2006-03-12 | 12:08 | 0 | 15.727 | 0 | 3 | 0 | 54.861 | 55.16 | 39.655 | 39.889 | 302.438 | 26.848 | 7.923 | 1 | 0 | 57.961 | 54.334 | 45.275 | 18.716 | 0 | 0 | 55.778 | 31.907 | [5 empty] | 0 | 14.972 | 14 | 4.2892 | 4.0019 | 3.9848 | 3.75 | 0.25191 | 5.8732
2006-03-12 | 12:09 | 0 | 15.671 | 0 | 3 | 1 | 54.742 | 55.223 | 39.65 | 39.743 | 266.471 | 26.794 | 7.745 | 1 | 0 | 57.934 | 54.261 | 45.133 | 18.537 | 0 | 0 | 55.75 | 31.877 | [5 empty] | 0 | 14.999 | 15 | 4.3411 | 4.0512 | 3.9869 | 3.75 | 0.30118 | 6.938
2006-03-12 | 12:10 | 1 | 15.722 | 0 | 4 | 0 | 54.604 | 55.155 | 39.602 | 39.719 | 225.104 | 26.77 | 7.468 | 2 | 0 | 57.891 | 54.282 | 45.065 | 18.537 | 0 | 0 | 55.75 | 31.877 | [5 empty] | 15.722 | 14.885 | 0 | 4.4217 | 4.1279 | 3.9902 | 3.75 | 0.37786 | 8.5455
2006-03-12 | 12:11 | 0 | 15.697 | 0 | 3 | 0 | 54.628 | 55.018 | 39.533 | 39.791 | 227.271 | 26.698 | 7.416 | 1 | 0 | 57.891 | 54.261 | 45.11 | 18.56 | 0 | 0 | 55.683 | 31.902 | [5 empty] | 0 | 14.837 | 1 | 4.4369 | 4.1423 | 3.9908 | 3.75 | 0.39225 | 8.8407
2006-03-12 | 12:12 | 0 | 15.744 | 0 | 3 | 0 | 54.719 | 54.994 | 39.578 | 39.626 | 260.202 | 26.649 | 6.96 | 1 | 0 | 57.891 | 54.238 | 45.133 | 18.585 | 0 | 0 | 55.683 | 31.951 | [5 empty] | 0 | 15.093 | 2 | 4.5696 | 4.2685 | 3.9962 | 3.75 | 0.51847 | 11.346
2006-03-12 | 12:13 | 0 | 15.769 | 1 | 3 | 0 | 54.537 | 55.041 | 39.557 | 39.626 | 268.724 | 26.794 | 7.543 | 1 | 0 | 57.891 | 54.238 | 45.065 | 18.585 | 0 | 0 | 55.706 | 31.877 | [5 empty] | 0 | 14.911 | 3 | 4.3999 | 4.1071 | 3.9893 | 3.75 | 0.3571 | 8.1161
2006-03-12 | 12:14 | 1 | 15.744 | 0 | 3 | 0 | 54.49 | 54.903 | 39.602 | 39.626 | 291.062 | 26.843 | 7.239 | 1 | 0 | 57.913 | 54.215 | 45.133 | 18.537 | 0 | 0 | 55.727 | 31.902 | [5 empty] | 15.744 | 14.864 | 4 | 4.4884 | 4.1912 | 3.9929 | 3.75 | 0.44124 | 9.8308
2006-03-12 | 12:15 | 0 | 15.744 | 0 | 4 | 0 | 54.282 | 54.903 | 39.509 | 39.602 | 258.804 | 26.77 | 7.468 | 1 | 0 | 57.868 | 54.238 | 45.11 | 18.56 | 0 | 0 | 55.727 | 31.926 | [5 empty] | 0 | 14.68 | 5 | 4.4217 | 4.1279 | 3.9902 | 3.75 | 0.37786 | 8.5455
2006-03-12 | 12:16 | 0 | 15.795 | 0 | 3 | 0 | 54.376 | 54.651 | 39.437 | 39.602 | 251.794 | 26.649 | 7.646 | 2 | 0 | 57.845 | 54.168 | 45.156 | 18.585 | 0 | 0 | 55.75 | 32.022 | [5 empty] | 0 | 14.774 | 6 | 4.3699 | 4.0786 | 3.9881 | 3.75 | 0.32859 | 7.5194
2006-03-12 | 12:17 | 0 | 15.769 | 0 | 3 | 0 | 54.261 | 54.695 | 39.437 | 39.557 | 256.358 | 26.649 | 7.064 | 1 | 0 | 57.822 | 54.191 | 45.18 | 18.56 | 0 | 0 | 55.683 | 31.902 | [5 empty] | 0 | 14.704 | 7 | 4.5394 | 4.2397 | 3.9949 | 3.75 | 0.48968 | 10.7875
2006-03-12 | 12:18 | 0 | 15.769 | 0 | 3 | 0 | 54.282 | 54.604 | 39.416 | 39.461 | 238.357 | 26.649 | 7.442 | 1 | 0 | 57.822 | 54.191 | 45.133 | 18.56 | 0 | 0 | 55.706 | 31.889 | [5 empty] | 0 | 14.821 | 8 | 4.4293 | 4.1351 | 3.9905 | 3.75 | 0.38505 | 8.6934
2006-03-12 | 12:19 | 1 | 15.782 | 0 | 3 | 0 | 54.25 | 54.616 | 39.404 | 39.473 | 237.293 | 26.806 | 7.455 | 1 | 0 | 57.856 | 54.18 | 45.03 | 18.55 | 0 | 0 | 55.671 | 31.889 | [5 empty] | 15.782 | 14.777 | 9 | 4.4255 | 4.1315 | 3.9903 | 3.75 | 0.38146 | 8.6195
2006-03-12 | 12:20 | 0 | 15.782 | 0 | 4 | 0 | 54.294 | 54.616 | 39.263 | 39.38 | 251.97 | 26.735 | 7.83 | 1 | 0 | 57.856 | 54.18 | 45.03 | 18.573 | 0 | 0 | 55.671 | 31.865 | [5 empty] | 0 | 14.914 | 10 | 4.3163 | 4.0277 | 3.9859 | 3.75 | 0.27766 | 6.4327
2006-03-12 | 12:21 | 0 | 15.787 | 0 | 3 | 0 | 54.208 | 54.712 | 39.291 | 39.385 | 283.907 | 26.787 | 7.409 | 1 | 0 | 57.815 | 54.184 | 45.082 | 18.603 | 0 | 0 | 55.676 | 31.872 | [5 empty] | 0 | 14.823 | 11 | 4.4389 | 4.1442 | 3.9909 | 3.75 | 0.39419 | 8.8803
2006-03-12 | 12:22 | 0 | 15.787 | 1 | 3 | 0 | 54.322 | 54.621 | 39.361 | 39.432 | 323.884 | 26.667 | 7.612 | 2 | 0 | 57.838 | 54.184 | 45.035 | 18.628 | 0 | 0 | 55.699 | 31.919 | [5 empty] | 0 | 14.89 | 12 | 4.3798 | 4.088 | 3.9885 | 3.75 | 0.338 | 7.7172
2006-03-12 | 12:23 | 0 | 15.757 | 0 | 3 | 0 | 54.18 | 54.663 | 39.286 | 39.286 | 317.531 | 26.637 | 7.953 | 1 | 0 | 57.788 | 54.135 | 45.168 | 18.573 | 0 | 0 | 55.624 | 31.889 | [5 empty] | 0 | 14.894 | 13 | 4.2805 | 3.9936 | 3.9845 | 3.75 | 0.24361 | 5.6912
2006-03-12 | 12:24 | 1 | 15.787 | 0 | 4 | 0 | 54.208 | 54.574 | 39.315 | 39.385 | 280.652 | 26.642 | 7.282 | 1 | 0 | 57.795 | 54.14 | 45.103 | 18.603 | 0 | 0 | 55.676 | 31.992 | [5 empty] | 15.787 | 14.823 | 14 | 4.4759 | 4.1793 | 3.9924 | 3.75 | 0.42934 | 9.5924
2006-03-12 | 12:25 | 0 | 15.757 | 0 | 3 | 1 | 54.203 | 54.593 | 39.191 | 39.308 | 302.924 | 26.591 | 7.177 | 1 | 0 | 57.767 | 54.135 | 45.121 | 18.573 | 0 | 0 | 55.533 | 31.865 | [5 empty] | 0 | 14.895 | 15 | 4.5065 | 4.2084 | 3.9936 | 3.75 | 0.45841 | 10.1722
2006-03-12 | 12:26 | 0 | 15.782 | 0 | 3 | 0 | 54.163 | 54.553 | 39.337 | 39.315 | 293.969 | 26.74 | 7.538 | 1 | 0 | 57.815 | 54.093 | 45.082 | 18.58 | 0 | 0 | 55.585 | 31.919 | [5 empty] | 0 | 14.848 | 0 | 4.4013 | 4.1085 | 3.9894 | 3.75 | 0.35848 | 8.1448
2006-03-12 | 12:27 | 0 | 15.812 | 0 | 3 | 0 | 54.184 | 54.53 | 39.267 | 39.337 | 288.694 | 26.62 | 7.36 | 2 | 0 | 57.772 | 54.093 | 45.126 | 18.603 | 0 | 0 | 55.585 | 31.919 | [5 empty] | 0 | 14.847 | 1 | 4.4532 | 4.1578 | 3.9915 | 3.75 | 0.40775 | 9.1564
2006-03-12 | 12:28 | 1 | 15.837 | 0 | 3 | 0 | 54.278 | 54.553 | 39.219 | 39.385 | 280.308 | 26.62 | 7.486 | 1 | 0 | 57.772 | 54.093 | 45.173 | 18.603 | 0 | 0 | 55.561 | 31.919 | [5 empty] | 15.837 | 14.893 | 2 | 4.4165 | 4.1229 | 3.99 | 3.75 | 0.37288 | 8.4428
2006-03-12 | 12:29 | 0 | 15.807 | 0 | 4 | 0 | 54.273 | 54.546 | 39.215 | 39.332 | 272.017 | 26.637 | 7.757 | 1 | 0 | 57.745 | 54.089 | 45.145 | 18.598 | 0 | 0 | 55.533 | 31.843 | [5 empty] | 0 | 14.941 | 3 | 4.3376 | 4.0479 | 3.9868 | 3.75 | 0.29786 | 6.867
2006-03-12 | 12:30 | 0 | 15.812 | 0 | 3 | 0 | 54.254 | 54.553 | 39.337 | 39.315 | 275.144 | 26.811 | 7.538 | 1 | 0 | 57.772 | 54.047 | 45.103 | 18.58 | 0 | 0 | 55.629 | 31.872 | [5 empty] | 0 | 14.939 | 4 | 4.4013 | 4.1085 | 3.9894 | 3.75 | 0.35848 | 8.1448
2006-03-12 | 12:31 | 0 | 15.812 | 1 | 3 | 0 | 54.184 | 54.597 | 39.267 | 39.361 | 266.84 | 26.909 | 7.409 | 1 | 0 | 57.772 | 54.093 | 45.058 | 18.628 | 0 | 0 | 55.629 | 31.894 | [5 empty] | 0 | 14.823 | 5 | 4.4389 | 4.1442 | 3.9909 | 3.75 | 0.39419 | 8.8803
2006-03-12 | 12:32 | 0 | 15.812 | 0 | 3 | 0 | 54.184 | 54.644 | 39.243 | 39.291 | 274.798 | 26.765 | 7.282 | 1 | 0 | 57.726 | 54.07 | 45.035 | 18.603 | 0 | 0 | 55.608 | 31.992 | [5 empty] | 0 | 14.893 | 6 | 4.4759 | 4.1793 | 3.9924 | 3.75 | 0.42934 | 9.5924
2006-03-12 | 12:33 | 1 | 15.837 | 0 | 4 | 0 | 54.163 | 54.574 | 39.337 | 39.337 | 312.531 | 26.787 | 7.46 | 2 | 0 | 57.749 | 54.026 | 45.058 | 18.555 | 0 | 0 | 55.561 | 31.919 | [5 empty] | 15.837 | 14.826 | 7 | 4.424 | 4.1301 | 3.9903 | 3.75 | 0.38007 | 8.591
2006-03-12 | 12:34 | 0 | 15.812 | 0 | 3 | 0 | 54.208 | 54.53 | 39.243 | 39.337 | 271.693 | 26.931 | 7.687 | 1 | 0 | 57.749 | 54.047 | 45.058 | 18.603 | 0 | 0 | 55.515 | 31.919 | [5 empty] | 0 | 14.871 | 8 | 4.3579 | 4.0672 | 3.9876 | 3.75 | 0.31724 | 7.2795
2006-03-12 | 12:35 | 0 | 15.812 | 0 | 3 | 0 | 54.184 | 54.553 | 39.243 | 39.385 | 262.32 | 26.765 | 7.234 | 1 | 0 | 57.704 | 54.002 | 45.173 | 18.603 | 0 | 0 | 55.47 | 31.919 | [5 empty] | 0 | 14.799 | 9 | 4.4899 | 4.1926 | 3.9929 | 3.75 | 0.44263 | 9.8584
2006-03-12 | 12:36 | 0 | 15.812 | 0 | 3 | 0 | 54.14 | 54.506 | 39.267 | 39.291 | 246.539 | 26.811 | 7.712 | 1 | 0 | 57.683 | 53.979 | 45.196 | 18.603 | 0 | 0 | 55.424 | 31.919 | [5 empty] | 0 | 14.849 | 10 | 4.3507 | 4.0603 | 3.9873 | 3.75 | 0.31032 | 7.1327
2006-03-12 | 12:37 | 0 | 15.837 | 0 | 3 | 0 | 54.208 | 54.553 | 39.267 | 39.291 | 246.89 | 26.836 | 7.156 | 1 | 0 | 57.704 | 53.979 | 45.058 | 18.58 | 0 | 0 | 55.47 | 31.894 | [5 empty] | 0 | 14.917 | 11 | 4.5126 | 4.2142 | 3.9939 | 3.75 | 0.46422 | 10.2872
2006-03-12 | 12:38 | 1 | 15.87 | 0 | 4 | 0 | 54.215 | 54.56 | 39.251 | 39.368 | 244.08 | 26.941 | 8.016 | 1 | 0 | 57.733 | 54.009 | 45.042 | 18.635 | 0 | 0 | 55.501 | 31.904 | [5 empty] | 15.87 | 14.847 | 12 | 4.2621 | 3.9762 | 3.9837 | 3.75 | 0.22617 | 5.3065
2006-03-12 | 12:39 | 0 | 15.837 | 0 | 3 | 0 | 54.231 | 54.506 | 39.243 | 39.267 | 262.494 | 26.86 | 8.132 | 2 | 0 | 57.683 | 54.002 | 44.988 | 18.628 | 0 | 0 | 55.447 | 31.848 | [5 empty] | 0 | 14.964 | 13 | 4.2284 | 3.9441 | 3.9823 | 3.75 | 0.19406 | 4.5895
2006-03-12 | 12:40 | 0 | 15.812 | 0 | 3 | 0 | 54.163 | 54.553 | 39.243 | 39.315 | 268.92 | 26.931 | 8.034 | 1 | 0 | 57.704 | 53.932 | 45.058 | 18.603 | 0 | 0 | 55.447 | 31.894 | [5 empty] | 0 | 14.848 | 14 | 4.2569 | 3.9712 | 3.9835 | 3.75 | 0.22119 | 5.196
2006-03-12 | 12:41 | 0 | 15.787 | 1 | 3 | 1 | 54.254 | 54.483 | 39.15 | 39.315 | 271.693 | 26.765 | 8.207 | 1 | 0 | 57.66 | 53.932 | 45.103 | 18.58 | 0 | 0 | 55.424 | 31.894 | [5 empty] | 0 | 14.939 | 15 | 4.2065 | 3.9233 | 3.9815 | 3.75 | 0.1733 | 4.1199
2006-03-12 | 12:42 | 1 | 15.762 | 0 | 4 | 0 | 54.231 | 54.553 | 39.267 | 39.337 | 292.951 | 26.787 | 7.835 | 1 | 0 | 57.66 | 53.956 | 45.012 | 18.603 | 0 | 0 | 55.377 | 31.872 | [5 empty] | 15.762 | 14.894 | 0 | 4.3148 | 4.0263 | 3.9858 | 3.75 | 0.27627 | 6.4028
2006-03-12 | 12:43 | 0 | 15.787 | 0 | 3 | 0 | 54.208 | 54.483 | 39.126 | 39.385 | 301.425 | 26.74 | 8.28 | 1 | 0 | 57.66 | 53.909 | 45.149 | 18.628 | 0 | 0 | 55.377 | 31.894 | [5 empty] | 0 | 14.823 | 1 | 4.1853 | 3.9031 | 3.76 | 3.5294 | 0.37368 | 8.9286
2006-03-12 | 12:44 | 0 | 15.795 | 0 | 3 | 0 | 54.238 | 54.537 | 39.227 | 39.322 | 290.084 | 26.868 | 8.338 | 2 | 0 | 57.69 | 53.939 | 45.065 | 18.635 | 0 | 0 | 55.384 | 31.926 | [5 empty] | 0 | 14.916 | 2 | 4.1684 | 3.887 | 3.7593 | 3.5294 | 0.35763 | 8.5796
2006-03-12 | 12:45 | 0 | 15.795 | 0 | 3 | 0 | 54.194 | 54.604 | 39.157 | 39.322 | 211.195 | 26.868 | 8.016 | 1 | 0 | 57.69 | 53.963 | 45.065 | 18.661 | 0 | 0 | 55.501 | 31.904 | [5 empty] | 0 | 14.872 | 3 | 4.2621 | 3.9762 | 3.7631 | 3.5294 | 0.44676 | 10.482
2006-03-12 | 12:46 | 0 | 15.795 | 0 | 3 | 0 | 54.308 | 54.537 | 39.157 | 39.416 | 229.65 | 26.698 | 7.72 | 1 | 0 | 57.644 | 53.963 | 45.112 | 18.661 | 0 | 0 | 55.34 | 31.926 | [5 empty] | 0 | 14.892 | 4 | 4.3483 | 4.0581 | 3.7666 | 3.5294 | 0.52869 | 12.1585
2006-03-12 | 12:47 | 1 | 15.739 | 0 | 4 | 0 | 54.163 | 54.597 | 39.219 | 39.267 | 241.75 | 26.86 | 7.813 | 1 | 0 | 57.683 | 53.909 | 45.035 | 18.628 | 0 | 0 | 55.333 | 31.894 | [5 empty] | 15.739 | 14.896 | 5 | 4.3213 | 4.0324 | 3.7655 | 3.5294 | 0.50295 | 11.639
2006-03-12 | 12:48 | 0 | 15.82 | 0 | 3 | 0 | 54.238 | 54.583 | 39.251 | 39.298 | 283.93 | 26.723 | 7.745 | 1 | 0 | 57.667 | 53.895 | 45.042 | 18.661 | 0 | 0 | 55.34 | 31.951 | [5 empty] | 0 | 14.94 | 6 | 4.3411 | 4.0512 | 3.7663 | 3.5294 | 0.52177 | 12.0195
2006-03-12 | 12:49 | 0 | 15.795 | 0 | 3 | 0 | 54.194 | 54.583 | 39.251 | 39.368 | 282.392 | 26.843 | 7.62 | 1 | 0 | 57.667 | 53.918 | 45.019 | 18.686 | 0 | 0 | 55.363 | 31.926 | [5 empty] | 0 | 14.826 | 7 | 4.3775 | 4.0858 | 3.7678 | 3.5294 | 0.55637 | 12.7099
2006-03-12 | 12:50 | 0 | 15.82 | 1 | 3 | 0 | 54.261 | 54.56 | 39.275 | 39.44 | 254.981 | 26.642 | 7.984 | 2 | 0 | 57.569 | 53.865 | 45.035 | 18.653 | 0 | 0 | 55.263 | 31.919 | [5 empty] | 0 | 14.821 | 8 | 4.2715 | 3.985 | 3.7635 | 3.5294 | 0.45562 | 10.6665
2006-03-12 | 12:51 | 0 | 15.82 | 0 | 3 | 0 | 54.215 | 54.628 | 39.368 | 39.368 | 228.398 | 26.747 | 8.265 | 1 | 0 | 57.644 | 53.872 | 45.019 | 18.635 | 0 | 0 | 55.27 | 31.975 | [5 empty] | 0 | 14.847 | 9 | 4.1896 | 3.9072 | 3.7602 | 3.5294 | 0.37784 | 9.0184
2006-03-12 | 12:52 | 1 | 15.845 | 0 | 4 | 0 | 54.238 | 54.583 | 39.346 | 39.463 | 239.289 | 26.674 | 7.994 | 1 | 0 | 57.578 | 53.872 | 45.065 | 18.635 | 0 | 0 | 55.27 | 31.926 | [5 empty] | 15.845 | 14.775 | 10 | 4.2685 | 3.9823 | 3.7634 | 3.5294 | 0.45285 | 10.609
2006-03-12 | 12:53 | 0 | 15.845 | 0 | 3 | 0 | 54.238 | 54.56 | 39.298 | 39.509 | 256.578 | 26.698 | 7.089 | 1 | 0 | 57.599 | 53.918 | 45.065 | 18.686 | 0 | 0 | 55.316 | 31.926 | [5 empty] | 0 | 14.729 | 11 | 4.5321 | 4.2328 | 3.7741 | 3.5294 | 0.70335 | 15.5194
2006-03-12 | 12:54 | 0 | 15.87 | 0 | 3 | 0 | 54.446 | 54.583 | 39.368 | 39.44 | 249.729 | 26.723 | 7.594 | 1 | 0 | 57.621 | 53.872 | 45.042 | 18.661 | 0 | 0 | 55.293 | 31.926 | [5 empty] | 0 | 15.006 | 12 | 4.385 | 4.093 | 3.7681 | 3.5294 | 0.56357 | 12.8521
2006-03-12 | 12:55 | 0 | 15.825 | 0 | 3 | 0 | 54.427 | 54.749 | 39.351 | 39.444 | 252.915 | 26.728 | 7.651 | 1 | 0 | 57.626 | 53.9 | 45.093 | 18.691 | 0 | 0 | 55.298 | 31.956 | [5 empty] | 0 | 14.983 | 13 | 4.3684 | 4.0772 | 3.7674 | 3.5294 | 0.54779 | 12.5398
2006-03-12 | 12:56 | 1 | 15.845 | 0 | 3 | 0 | 54.422 | 54.721 | 39.44 | 39.485 | 248.848 | 26.627 | 7.918 | 2 | 0 | 57.578 | 53.825 | 45.089 | 18.635 | 0 | 0 | 55.293 | 31.951 | [5 empty] | 15.845 | 14.937 | 14 | 4.2907 | 4.0033 | 3.7643 | 3.5294 | 0.47389 | 11.0445
2006-03-12 | 12:57 | 0 | 15.845 | 0 | 4 | 0 | 54.422 | 54.742 | 39.533 | 39.463 | 243.37 | 26.772 | 8.24 | 1 | 0 | 57.555 | 53.825 | 45.089 | 18.661 | 0 | 0 | 55.225 | 31.975 | [5 empty] | 0 | 14.959 | 15 | 4.1969 | 3.9142 | 3.7605 | 3.5294 | 0.38476 | 9.1676
2006-03-12 | 12:58 | 0 | 15.87 | 0 | 3 | 1 | 54.513 | 54.789 | 39.509 | 39.485 | 215.367 | 26.797 | 8.142 | 1 | 0 | 57.621 | 53.825 | 45.042 | 18.661 | 0 | 0 | 55.249 | 31.975 | [5 empty] | 0 | 15.028 | 16 | 4.2254 | 3.9413 | 3.7616 | 3.5294 | 0.41188 | 9.7477
2006-03-12 | 12:59 | 0 | 15.883 | 1 | 3 | 0 | 54.642 | 54.894 | 39.523 | 39.499 | 230.562 | 26.713 | 7.833 | 1 | 0 | 57.589 | 53.839 | 45.056 | 18.648 | 0 | 0 | 55.307 | 31.941 | [5 empty] | 0 | 15.143 | 0 | 4.3154 | 4.0268 | 3.7653 | 3.5294 | 0.49741 | 11.5264
2006-03-12 | 13:00 | 0 | 15.883 | 0 | 3 | 0 | 54.756 | 55.008 | 39.523 | 39.593 | 222.821 | 26.689 | 7.633 | 1 | 0 | 57.569 | 53.792 | 45.194 | 18.648 | 0 | 0 | 55.284 | 31.941 | [5 empty] | 0 | 15.163 | 1 | 4.3737 | 4.0822 | 3.9882 | 3.75 | 0.33219 | 7.5951
2006-03-12 | 13:01 | 1 | 15.915 | 0 | 3 | 0 | 54.763 | 55.132 | 39.554 | 39.648 | 213.405 | 26.721 | 7.888 | 2 | 0 | 57.576 | 53.869 | 45.154 | 18.731 | 0 | 0 | 55.27 | 31.899 | [5 empty] | 15.915 | 15.115 | 2 | 4.2994 | 4.0116 | 3.9852 | 3.75 | 0.2616 | 6.0846
2006-03-12 | 13:02 | 0 | 15.883 | 0 | 3 | 0 | 54.917 | 55.146 | 39.64 | 39.617 | 211.195 | 26.76 | 7.406 | 1 | 0 | 57.612 | 53.909 | 45.1 | 18.673 | 0 | 0 | 55.193 | 31.892 | [5 empty] | 0 | 15.3 | 3 | 4.4398 | 4.145 | 3.9909 | 3.75 | 0.39502 | 8.8973
2006-03-12 | 13:03 | 0 | 15.915 | 0 | 3 | 0 | 54.786 | 55.153 | 39.648 | 39.624 | 186.56 | 26.865 | 7.136 | 1 | 0 | 57.599 | 53.801 | 45.086 | 18.706 | 0 | 0 | 55.223 | 31.997 | [5 empty] | 0 | 15.162 | 4 | 4.5184 | 4.2198 | 3.9941 | 3.75 | 0.46976 | 10.3965
2006-03-12 | 13:04 | 0 | 15.915 | 0 | 3 | 0 | 54.833 | 55.132 | 39.578 | 39.672 | 159.033 | 26.767 | 7.913 | 1 | 0 | 57.576 | 53.778 | 45.201 | 18.706 | 0 | 0 | 55.176 | 31.948 | [5 empty] | 0 | 15.161 | 5 | 4.2921 | 4.0047 | 3.9849 | 3.75 | 0.25468 | 5.9337
2006-03-12 | 13:05 | 0 | 15.89 | 0 | 3 | 0 | 54.971 | 55.176 | 39.53 | 39.6 | 180.185 | 26.745 | 8.062 | 1 | 0 | 57.53 | 53.801 | 45.131 | 18.706 | 0 | 0 | 55.153 | 31.948 | [5 empty] | 0 | 15.371 | 6 | 4.2487 | 3.9634 | 3.9832 | 3.75 | 0.21344 | 5.0236
2006-03-12 | 13:06 | 1 | 15.915 | 0 | 3 | 0 | 54.947 | 55.291 | 39.672 | 39.624 | 177.224 | 26.745 | 7.033 | 1 | 0 | 57.576 | 53.755 | 45.086 | 18.681 | 0 | 0 | 55.2 | 31.948 | [5 empty] | 15.915 | 15.323 | 7 | 4.5484 | 4.2483 | 3.9953 | 3.75 | 0.49827 | 10.9548
2006-03-12 | 13:07 | 0 | 15.915 | 0 | 3 | 0 | 55.085 | 55.361 | 39.624 | 39.648 | 201.854 | 26.816 | 7.641 | 2 | 0 | 57.553 | 53.778 | 45.04 | 18.681 | 0 | 0 | 55.2 | 31.924 | [5 empty] | 0 | 15.437 | 8 | 4.3713 | 4.08 | 3.9881 | 3.75 | 0.32997 | 7.5485
2006-03-12 | 13:08 | 0 | 15.94 | 1 | 3 | 0 | 55.176 | 55.475 | 39.53 | 39.578 | 188.586 | 26.767 | 7.54 | 1 | 0 | 57.553 | 53.755 | 45.04 | 18.681 | 0 | 0 | 55.153 | 31.924 | [5 empty] | 0 | 15.598 | 9 | 4.4008 | 4.1079 | 3.9893 | 3.75 | 0.35793 | 8.1333
2006-03-12 | 13:09 | 0 | 15.971 | 0 | 3 | 0 | 55.274 | 55.526 | 39.511 | 39.559 | 188.309 | 26.75 | 7.571 | 1 | 0 | 57.535 | 53.759 | 45.205 | 18.688 | 0 | 0 | 55.16 | 32.002 | [5 empty] | 0 | 15.715 | 10 | 4.3917 | 4.0993 | 3.989 | 3.75 | 0.34935 | 7.9547
2006-03-12 | 13:10 | 1 | 15.971 | 0 | 3 | 0 | 55.365 | 55.617 | 39.466 | 39.629 | 185.494 | 26.846 | 7.597 | 1 | 0 | 57.512 | 53.759 | 45.182 | 18.711 | 0 | 0 | 55.181 | 31.978 | [5 empty] | 15.971 | 15.736 | 11 | 4.3842 | 4.0922 | 3.9887 | 3.75 | 0.34215 | 7.8043
2006-03-12 | 13:11 | 0 | 15.94 | 0 | 3 | 0 | 55.384 | 55.636 | 39.389 | 39.554 | 168.706 | 26.745 | 7.311 | 1 | 0 | 57.484 | 53.687 | 45.063 | 18.681 | 0 | 0 | 55.062 | 31.973 | [5 empty] | 0 | 15.83 | 12 | 4.4674 | 4.1713 | 3.992 | 3.75 | 0.42132 | 9.4308
2006-03-12 | 13:12 | 0 | 15.996 | 0 | 3 | 0 | 55.526 | 55.687 | 39.325 | 39.511 | 176.924 | 26.75 | 8.29 | 2 | 0 | 57.512 | 53.692 | 45.138 | 18.711 | 0 | 0 | 55.113 | 32.002 | [5 empty] | 0 | 16.015 | 13 | 4.1824 | 3.9003 | 3.9805 | 3.75 | 0.15033 | 3.5943
2006-03-12 | 13:13 | 0 | 15.945 | 0 | 3 | 0 | 56.03 | 55.778 | 39.16 | 39.277 | 193.907 | 26.797 | 8.635 | 1 | 0 | 57.512 | 53.715 | 45.205 | 18.711 | 0 | 0 | 55.113 | 31.953 | [5 empty] | 0 | 16.753 | 14 | 4.0819 | 3.8048 | 3.9764 | 3.75 | 0.054832 | 1.3433
2006-03-12 | 13:14 | 0 | 15.945 | 0 | 3 | 1 | 52.499 | 56.257 | 38.877 | 39.229 | 30.026 | 26.701 | 8.486 | 1 | 0 | 57.491 | 53.715 | 45.063 | 18.681 | 0 | 0 | 55.132 | 31.924 | [5 empty] | 0 | 13.27 | 15 | 4.1253 | 3.8461 | 3.9782 | 3.75 | 0.096075 | 2.3289
2006-03-12 | 13:15 | 0 | 15.92 | 0 | 2 | 0 | 43.908 | 54.287 | 38.76 | 38.995 | 24.05 | 26.676 | 8.192 | 0 | 0 | 57.491 | 53.692 | 45.182 | 18.736 | 0 | 0 | 55.113 | 31.953 | [5 empty] | 0 | 4.913 | 0 | 4.2109 | 3.9275 | 3.9816 | 3.75 | 0.17745 | 4.2142
2006-03-12 | 13:16 | 0 | 15.895 | 0 | 3 | 0 | 41.37 | 45.296 | 38.571 | 38.808 | 20.461 | 26.725 | 8.341 | 1 | 0 | 57.535 | 53.692 | 45.091 | 18.711 | 0 | 0 | 55.16 | 31.953 | [5 empty] | 0 | 2.562 | 1 | 4.1675 | 3.8862 | 1.1823 | 0.95238 | 2.9338 | 70.3978
2006-03-12 | 13:17 | 0 | 15.895 | 0 | 3 | 0 | 40.406 | 42.169 | 38.361 | 38.643 | 19.156 | 26.725 | 8.341 | 0 | 0 | 57.468 | 53.692 | 45.114 | 18.736 | 0 | 0 | 55.09 | 31.953 | [5 empty] | 0 | 1.763 | 2 | 4.1675 | 3.8862 | 1.1823 | 0.95238 | 2.9338 | 70.3978
2006-03-12 | 13:18 | 0 | 15.87 | 0 | 2 | 0 | 39.794 | 40.97 | 37.985 | 38.547 | 16.217 | 26.774 | 8.117 | 0 | 0 | 57.557 | 53.759 | 45.252 | 18.736 | 0 | 0 | 55.022 | 31.904 | [5 empty] | 0 | 1.247 | 3 | 4.2327 | 3.9482 | 1.1849 | 0.95238 | 2.9958 | 70.7778
2006-03-12 | 13:19 | 0 | 15.885 | 1 | 3 | 0 | 39.337 | 40.253 | 37.736 | 38.136 | 15.737 | 26.738 | 8.454 | 0 | 0 | 57.455 | 53.654 | 44.965 | 18.701 | 0 | 0 | 55.032 | 31.87 | [5 empty] | 0 | 1.201 | 4 | 4.1346 | 3.8549 | 1.1809 | 0.95238 | 2.9026 | 70.2016
2006-03-12 | 13:20 | 0 | 15.86 | 0 | 3 | 0 | 38.913 | 39.758 | 37.337 | 37.784 | 15.44 | 26.593 | 8.75 | 0 | 0 | 57.409 | 53.61 | 45.079 | 18.726 | 0 | 0 | 54.961 | 31.845 | [5 empty] | 0 | 1.129 | 5 | 4.0484 | 3.773 | 1.1774 | 0.95238 | 2.8206 | 69.6724
2006-03-12 | 13:21 | 0 | 15.885 | 0 | 3 | 0 | 38.514 | 39.265 | 36.751 | 37.409 | 14.875 | 26.762 | 8.798 | 0 | 0 | 57.366 | 53.631 | 44.918 | 18.726 | 0 | 0 | 55.008 | 31.821 | [5 empty] | 0 | 1.105 | 6 | 4.0344 | 3.7597 | 1.1769 | 0.95238 | 2.8073 | 69.5845
2006-03-12 | 13:22 | 0 | 15.83 | 0 | 2 | 0 | 38.038 | 38.767 | 36.11 | 36.816 | 12.944 | 26.539 | 8.3 | 0 | 0 | 57.316 | 53.535 | 44.918 | 18.726 | 0 | 0 | 54.985 | 31.821 | [5 empty] | 0 | 1.222 | 7 | 4.1794 | 3.8976 | 1.1827 | 0.95238 | 2.9452 | 70.4683
2006-03-12 | 13:23 | 0 | 15.885 | 0 | 3 | 0 | 37.55 | 38.397 | 35.598 | 36.256 | 11.194 | 26.522 | 7.788 | 0 | 0 | 57.343 | 53.587 | 44.872 | 18.726 | 0 | 0 | 54.961 | 31.821 | [5 empty] | 0 | 1.294 | 8 | 4.3285 | 4.0393 | 1.1888 | 0.95238 | 3.0869 | 71.3151
2006-03-12 | 13:24 | 0 | 15.91 | 0 | 2 | 0 | 38.09 | 37.832 | 35.036 | 35.739 | 26.907 | 26.377 | 7.409 | 0 | 0 | 57.277 | 53.563 | 44.895 | 18.701 | 0 | 0 | 54.94 | 31.87 | [5 empty] | 0 | 2.351 | 9 | 4.4389 | 4.1442 | 1.1933 | 0.95238 | 3.1918 | 71.9054
2006-03-12 | 13:25 | 1 | 15.91 | 0 | 3 | 0 | 51.661 | 37.691 | 34.613 | 35.081 | 24.955 | 26.377 | 7.737 | 0 | 0 | 57.254 | 53.54 | 44.827 | 18.701 | 0 | 0 | 54.94 | 31.821 | [5 empty] | 15.91 | 16.58 | 10 | 4.3434 | 4.0534 | 1.1894 | 0.95238 | 3.101 | 71.3963
2006-03-12 | 13:26 | 0 | 15.935 | 0 | 3 | 0 | 53.587 | 49.941 | 34.237 | 34.706 | 25.629 | 26.304 | 8.454 | 1 | 0 | 57.208 | 53.631 | 44.895 | 18.726 | 0 | 0 | 54.961 | 31.845 | [5 empty] | 0 | 18.881 | 11 | 4.1346 | 3.8549 | 1.1809 | 0.95238 | 2.9026 | 70.2016
2006-03-12 | 13:27 | 0 | 15.91 | 0 | 2 | 0 | 53.54 | 53.22 | 33.976 | 34.4 | 25.992 | 26.304 | 7.661 | 1 | 0 | 57.163 | 53.517 | 44.734 | 18.824 | 0 | 0 | 54.94 | 31.894 | [5 empty] | 0 | 19.14 | 12 | 4.3655 | 4.0744 | 1.1903 | 0.95238 | 3.1221 | 71.5163
2006-03-12 | 13:28 | 0 | 15.935 | 0 | 2 | 0 | 53.93 | 53.54 | 33.672 | 34.024 | 26.473 | 26.282 | 8.034 | 2 | 0 | 57.142 | 53.517 | 44.804 | 18.751 | 0 | 0 | 54.961 | 31.845 | [5 empty] | 0 | 19.906 | 13 | 4.2569 | 3.9712 | 1.1859 | 0.95238 | 3.0188 | 70.9157
2006-03-12 | 13:29 | 0 | 15.935 | 1 | 2 | 0 | 55.351 | 53.517 | 33.46 | 33.742 | 24.69 | 26.184 | 8.132 | 1 | 0 | 57.119 | 53.496 | 44.757 | 18.701 | 0 | 0 | 54.961 | 31.845 | [5 empty] | 0 | 21.609 | 14 | 4.2284 | 3.9441 | 1.1847 | 0.95238 | 2.9917 | 70.7527
2006-03-12 | 13:30 | 0 | 15.94 | 0 | 2 | 0 | 44.9 | 54.303 | 33.395 | 33.56 | 18.163 | 26.237 | 8.361 | 1 | 0 | 57.124 | 53.477 | 44.762 | 18.731 | 0 | 0 | 54.985 | 31.845 | [5 empty] | 0 | 11.34 | 15 | 4.1617 | 3.8807 | 1.182 | 0.95238 | 2.9283 | 70.3633
2006-03-12 | 13:31 | 0 | 15.91 | 0 | 2 | 0 | 38.373 | 53.358 | 33.273 | 33.39 | 15.541 | 26.159 | 8.378 | 0 | 0 | 57.097 | 53.472 | 44.713 | 18.726 | 0 | 0 | 54.985 | 31.87 | [5 empty] | 0 | 4.983 | 16 | 4.1567 | 3.876 | 1.1818 | 0.95238 | 2.9236 | 70.3339
2006-03-12 | 13:32 | 0 | 15.935 | 0 | 1 | 0 | 36.256 | 43.779 | 33.084 | 33.273 | 14.284 | 26.088 | 8.157 | 0 | 0 | 57.097 | 53.449 | 44.734 | 18.701 | 0 | 0 | 54.94 | 31.799 | [5 empty] | 0 | 2.983 | 17 | 4.2211 | 3.9371 | 1.1844 | 0.95238 | 2.9848 | 70.7108
2006-03-12 | 13:33 | 0 | 15.966 | 0 | 2 | 0 | 35.344 | 38.684 | 33.019 | 33.23 | 14.56 | 26.117 | 8.31 | 0 | 0 | 57.147 | 53.43 | 44.694 | 18.731 | 0 | 0 | 54.945 | 31.804 | [5 empty] | 0 | 2.114 | 18 | 4.1765 | 3.8948 | 1.1826 | 0.95238 | 2.9424 | 70.4511
2006-03-12 | 13:34 | 0 | 15.94 | 0 | 2 | 0 | 34.852 | 36.756 | 32.737 | 32.972 | 14.56 | 25.997 | 8.73 | 0 | 0 | 57.236 | 53.545 | 44.785 | 18.781 | 0 | 0 | 54.922 | 31.779 | [5 empty] | 0 | 1.88 | 19 | 4.0542 | 3.7785 | 1.1777 | 0.95238 | 2.8262 | 69.7089
2006-03-12 | 13:35 | 0 | 15.89 | 0 | 2 | 0 | 34.383 | 35.768 | 32.502 | 32.854 | 14.535 | 26.022 | 8.557 | 0 | 0 | 57.147 | 53.43 | 44.624 | 18.731 | 0 | 0 | 54.898 | 31.779 | [5 empty] | 0 | 1.529 | 20 | 4.1046 | 3.8264 | 1.1797 | 0.95238 | 2.874 | 70.02
2006-03-12 | 13:36 | 0 | 15.915 | 0 | 2 | 0 | 34.101 | 35.065 | 32.333 | 32.761 | 13.497 | 25.948 | 8.557 | 0 | 0 | 57.101 | 53.386 | 44.648 | 18.706 | 0 | 0 | 54.922 | 31.804 | [5 empty] | 0 | 1.34 | 21 | 4.1046 | 3.8264 | 1.1797 | 0.95238 | 2.874 | 70.02
2006-03-12 | 13:37 | 0 | 15.915 | 0 | 2 | 0 | 33.653 | 34.593 | 32.093 | 32.548 | 12.262 | 25.948 | 7.543 | 1 | 0 | 57.101 | 53.407 | 44.58 | 18.731 | 0 | 0 | 54.852 | 31.754 | [5 empty] | 0 | 1.105 | 22 | 4.3999 | 4.1071 | 1.1917 | 0.95238 | 3.1547 | 71.7001
2006-03-12 | 13:38 | 0 | 15.94 | 0 | 2 | 0 | 33.347 | 34.077 | 31.948 | 32.309 | 9.942 | 26.022 | 7.592 | 0 | 0 | 57.035 | 53.363 | 44.603 | 18.706 | 0 | 0 | 54.852 | 31.779 | [5 empty] | 0 | 1.038 | 23 | 4.3856 | 4.0935 | 1.1911 | 0.95238 | 3.1412 | 71.6241
2006-03-12 | 13:39 | 1 | 15.983 | 0 | 2 | 0 | 33.156 | 33.79 | 31.725 | 32.208 | 23.822 | 25.968 | 7.558 | 0 | 0 | 57.076 | 53.381 | 44.599 | 18.774 | 0 | 0 | 54.919 | 31.845 | [5 empty] | 15.983 | 0.948 | 24 | 4.3955 | 4.1029 | 1.1915 | 0.95238 | 3.1506 | 71.6769
2006-03-12 | 13:40 | 0 | 16.016 | 0 | 2 | 0 | 50.27 | 33.445 | 31.757 | 31.926 | 20.239 | 26.095 | 8.288 | 0 | 0 | 57.128 | 53.391 | 44.606 | 18.784 | 0 | 0 | 54.926 | 31.83 | [5 empty] | 0 | 18.344 | 25 | 4.1829 | 3.9009 | 1.1829 | 0.95238 | 2.9485 | 70.4888
2006-03-12 | 13:41 | 0 | 16.041 | 1 | 2 | 0 | 39.509 | 42.8 | 31.566 | 31.806 | 14.314 | 25.975 | 7.966 | 0 | 0 | 57.083 | 53.391 | 44.561 | 18.784 | 0 | 0 | 54.88 | 31.781 | [5 empty] | 0 | 7.703 | 26 | 4.2767 | 3.99 | 1.1867 | 0.95238 | 3.0376 | 71.0274
2006-03-12 | 13:42 | 0 | 16.041 | 0 | 2 | 0 | 34.526 | 44.538 | 31.492 | 31.686 | 12.511 | 25.926 | 8.263 | 0 | 0 | 57.106 | 53.391 | 44.629 | 18.806 | 0 | 0 | 54.88 | 31.757 | [5 empty] | 0 | 2.84 | 27 | 4.1902 | 3.9078 | 1.1832 | 0.95238 | 2.9554 | 70.5315
2006-03-12 | 13:43 | 0 | 15.991 | 0 | 2 | 0 | 33.139 | 36.572 | 31.443 | 31.661 | 10.583 | 25.902 | 7.991 | 1 | 0 | 56.971 | 53.344 | 44.538 | 18.806 | 0 | 0 | 54.835 | 31.781 | [5 empty] | 0 | 1.478 | 28 | 4.2694 | 3.9831 | 1.1864 | 0.95238 | 3.0307 | 70.9864
2006-03-12 | 13:44 | 0 | 15.991 | 0 | 2 | 0 | 32.646 | 34.055 | 31.227 | 31.517 | 9.595 | 25.975 | 7.742 | 0 | 0 | 56.971 | 53.321 | 44.444 | 18.784 | 0 | 0 | 54.859 | 31.71 | [5 empty] | 0 | 1.129 | 29 | 4.3419 | 4.052 | 1.1893 | 0.95238 | 3.0996 | 71.3884
2006-03-12 | 13:45 | 0 | 16.016 | 0 | 2 | 0 | 32.431 | 33.211 | 31.156 | 31.443 | 9.102 | 25.735 | 7.543 | 0 | 0 | 56.928 | 53.276 | 44.561 | 18.784 | 0 | 0 | 54.835 | 31.757 | [5 empty] | 0 | 0.988 | 30 | 4.3999 | 4.1071 | 1.1917 | 0.95238 | 3.1547 | 71.7001
2006-03-12 | 13:46 | 0 | 15.991 | 0 | 2 | 0 | 32.191 | 32.787 | 31.107 | 31.252 | 8.831 | 25.637 | 7.916 | 0 | 0 | 56.882 | 53.276 | 44.444 | 18.759 | 0 | 0 | 54.812 | 31.732 | [5 empty] | 0 | 0.939 | 31 | 4.2913 | 4.0039 | 1.1873 | 0.95238 | 3.0515 | 71.1089
2006-03-12 | 13:47 | 0 | 16.049 | 0 | 2 | 0 | 31.958 | 32.536 | 31.139 | 31.259 | 8.788 | 25.669 | 7.901 | 0 | 0 | 56.912 | 53.283 | 44.475 | 18.766 | 0 | 0 | 54.842 | 31.742 | [5 empty] | 0 | 0.699 | 32 | 4.2956 | 4.008 | 1.1874 | 0.95238 | 3.0556 | 71.1333
2006-03-12 | 13:48 | 0 | 15.991 | 0 | 2 | 0 | 31.781 | 32.264 | 30.722 | 31.156 | 9.298 | 25.566 | 7.818 | 0 | 0 | 56.836 | 53.276 | 44.491 | 18.806 | 0 | 0 | 54.765 | 31.686 | [5 empty] | 0 | 0.625 | 33 | 4.3198 | 4.031 | 1.1884 | 0.95238 | 3.0786 | 71.2671
2006-03-12 | 13:49 | 0 | 16.023 | 0 | 2 | 0 | 31.742 | 32.029 | 30.536 | 31.09 | 10.073 | 25.428 | 7.923 | 0 | 0 | 56.866 | 53.237 | 44.498 | 18.816 | 0 | 0 | 54.819 | 31.718 | [5 empty] | 0 | 0.652 | 34 | 4.2892 | 4.0019 | 1.1872 | 0.95238 | 3.0495 | 71.0976
2006-03-12 | 13:50 | 0 | 15.991 | 0 | 2 | 0 | 31.492 | 31.855 | 30.335 | 30.673 | 18.09 | 25.396 | 7.818 | 0 | 0 | 56.77 | 53.183 | 44.374 | 18.832 | 0 | 0 | 54.765 | 31.732 | [5 empty] | 0 | 0.819 | 35 | 4.3198 | 4.031 | 1.1884 | 0.95238 | 3.0786 | 71.2671
2006-03-12 | 13:51 | 0 | 15.943 | 0 | 2 | 0 | 48.506 | 31.686 | 30.144 | 30.673 | 21.373 | 25.132 | 7.991 | 0 | 0 | 56.747 | 53.139 | 44.35 | 18.759 | 0 | 0 | 54.742 | 31.661 | [5 empty] | 0 | 17.833 | 36 | 4.2694 | 3.9831 | 1.1864 | 0.95238 | 3.0307 | 70.9864
2006-03-12 | 13:52 | 0 | 15.951 | 1 | 2 | 0 | 41.162 | 35.545 | 30.2 | 30.536 | 16.913 | 25.092 | 7.825 | 0 | 0 | 56.754 | 53.169 | 44.453 | 18.791 | 0 | 0 | 54.705 | 31.742 | [5 empty] | 0 | 10.626 | 37 | 4.3178 | 4.029 | 1.1883 | 0.95238 | 3.0767 | 71.2559
2006-03-12 | 13:53 | 0 | 15.918 | 0 | 2 | 0 | 33.986 | 46.762 | 30.144 | 30.359 | 13.474 | 25.156 | 7.793 | 1 | 0 | 56.725 | 53.16 | 44.305 | 18.759 | 0 | 0 | 54.674 | 31.71 | [5 empty] | 0 | 3.627 | 38 | 4.3271 | 4.0379 | 1.1887 | 0.95238 | 3.0855 | 71.3072
2006-03-12 | 13:54 | 0 | 15.868 | 0 | 2 | 0 | 32.022 | 37.887 | 30.07 | 30.457 | 11.795 | 25.156 | 7.543 | 0 | 0 | 56.658 | 53.139 | 44.35 | 18.759 | 0 | 0 | 54.674 | 31.71 | [5 empty] | 0 | 1.565 | 39 | 4.3999 | 4.1071 | 1.1917 | 0.95238 | 3.1547 | 71.7001
2006-03-12 | 13:55 | 0 | 15.951 | 0 | 2 | 0 | 31.453 | 33.524 | 30.126 | 30.391 | 11.061 | 25.259 | 7.85 | 0 | 0 | 56.688 | 53.146 | 44.358 | 18.766 | 0 | 0 | 54.681 | 31.764 | [5 empty] | 0 | 1.062 | 40 | 4.3105 | 4.0221 | 1.1881 | 0.95238 | 3.0697 | 71.2157
2006-03-12 | 13:56 | 0 | 15.918 | 0 | 2 | 0 | 31.132 | 32.142 | 30.168 | 30.193 | 10.684 | 25.227 | 7.568 | 0 | 0 | 56.681 | 53.069 | 44.305 | 18.734 | 0 | 0 | 54.674 | 31.71 | [5 empty] | 0 | 0.939 | 41 | 4.3926 | 4.1002 | 1.1914 | 0.95238 | 3.1478 | 71.6614
2006-03-12 | 13:57 | 0 | 15.918 | 0 | 2 | 0 | 30.962 | 31.637 | 30.048 | 30.144 | 11.672 | 25.132 | 7.669 | 0 | 0 | 56.658 | 53.092 | 44.444 | 18.759 | 0 | 0 | 54.651 | 31.71 | [5 empty] | 0 | 0.818 | 42 | 4.3632 | 4.0722 | 1.1902 | 0.95238 | 3.1198 | 71.5037
2006-03-12 | 13:58 | 0 | 15.925 | 0 | 1 | 0 | 30.801 | 31.428 | 29.862 | 30.271 | 11.383 | 25.019 | 7.45 | 0 | 0 | 56.688 | 53.122 | 44.312 | 18.94 | 0 | 0 | 54.772 | 31.764 | [5 empty] | 0 | 0.53 | 43 | 4.427 | 4.1328 | 1.1928 | 0.95238 | 3.1805 | 71.843
2006-03-12 | 13:59 | 0 | 15.865 | 0 | 2 | 0 | 30.671 | 31.08 | 29.707 | 30.212 | 10.063 | 24.864 | 7.084 | 0 | 0 | 56.585 | 52.996 | 44.276 | 18.731 | 0 | 0 | 54.716 | 31.705 | [5 empty] | 0 | 0.459 | 44 | 4.5335 | 4.2341 | 1.1971 | 0.95238 | 3.2818 | 72.3887
2006-03-12 | 14:00 | 0 | 15.92 | 0 | 2 | 0 | 30.555 | 30.94 | 29.543 | 30.023 | 8.881 | 25.085 | 6.711 | 0 | 0 | 56.636 | 53.069 | 44.212 | 18.786 | 0 | 0 | 54.744 | 31.71 | [5 empty] | 0 | 0.532 | 45 | 4.6422 | 4.3374 | 1.2015 | 0.95238 | 3.385 | 72.919
2006-03-12 | 14:01 | 0 | 15.92 | 0 | 2 | 0 | 30.433 | 30.771 | 29.398 | 29.783 | 12.167 | 24.894 | 7.064 | 0 | 0 | 56.613 | 53.024 | 44.374 | 18.736 | 0 | 0 | 54.628 | 31.686 | [5 empty] | 0 | 0.65 | 46 | 4.5394 | 4.2397 | 1.1973 | 0.95238 | 3.2873 | 72.4177
2006-03-12 | 14:02 | 0 | 15.865 | 0 | 2 | 0 | 44.204 | 30.693 | 29.32 | 29.584 | 20.792 | 24.815 | 7.007 | 1 | 0 | 56.563 | 52.973 | 44.324 | 18.681 | 0 | 0 | 54.555 | 31.634 | [5 empty] | 0 | 14.62 | 47 | 4.556 | 4.2555 | 1.198 | 0.95238 | 3.3031 | 72.5002
2006-03-12 | 14:03 | 0 | 15.92 | 1 | 2 | 0 | 42.707 | 32.169 | 29.278 | 29.469 | 14.342 | 24.796 | 7.064 | 0 | 0 | 56.547 | 52.978 | 44.212 | 18.686 | 0 | 0 | 54.583 | 31.615 | [5 empty] | 0 | 13.238 | 48 | 4.5394 | 4.2397 | 1.1973 | 0.95238 | 3.2873 | 72.4177
2006-03-12 | 14:04 | 0 | 15.945 | 0 | 2 | 0 | 33.706 | 46.281 | 29.229 | 29.398 | 10.983 | 24.869 | 6.963 | 0 | 0 | 56.569 | 52.978 | 44.164 | 18.736 | 0 | 0 | 54.56 | 31.59 | [5 empty] | 0 | 4.308 | 49 | 4.5688 | 4.2676 | 1.1985 | 0.95238 | 3.3153 | 72.5635
2006-03-12 | 14:05 | 0 | 15.92 | 0 | 2 | 0 | 31.205 | 37.677 | 29.133 | 29.447 | 10.364 | 24.725 | 7.167 | 1 | 0 | 56.524 | 52.954 | 44.305 | 18.736 | 0 | 0 | 54.537 | 31.639 | [5 empty] | 0 | 1.758 | 50 | 4.5094 | 4.2112 | 1.1961 | 0.95238 | 3.2588 | 72.2672
2006-03-12 | 14:06 | 0 | 15.938 | 0 | 2 | 0 | 30.381 | 32.641 | 29.03 | 29.175 | 9.816 | 24.766 | 7.159 | 0 | 0 | 56.496 | 52.926 | 44.276 | 18.681 | 0 | 0 | 54.509 | 31.681 | [5 empty] | 0 | 1.206 | 51 | 4.5117 | 4.2134 | 1.1962 | 0.95238 | 3.261 | 72.2789
2006-03-12 | 14:07 | 0 | 15.945 | 0 | 2 | 0 | 30.097 | 31.132 | 29.038 | 29.278 | 10.017 | 24.749 | 7.089 | 0 | 0 | 56.524 | 52.954 | 44.212 | 18.736 | 0 | 0 | 54.651 | 31.615 | [5 empty] | 0 | 0.819 | 52 | 4.5321 | 4.2328 | 1.197 | 0.95238 | 3.2804 | 72.3814
2006-03-12 | 14:08 | 0 | 15.89 | 0 | 2 | 0 | 29.778 | 30.526 | 28.864 | 29.199 | 9.371 | 24.6 | 6.984 | 0 | 0 | 56.474 | 52.926 | 44.135 | 18.706 | 0 | 0 | 54.67 | 31.634 | [5 empty] | 0 | 0.579 | 53 | 4.5627 | 4.2618 | 1.1983 | 0.95238 | 3.3094 | 72.5333
2006-03-12 | 14:09 | 0 | 15.895 | 0 | 2 | 0 | 29.592 | 30.242 | 28.868 | 29.084 | 8.783 | 24.771 | 7.089 | 0 | 0 | 56.547 | 52.954 | 44.14 | 18.736 | 0 | 0 | 54.607 | 31.541 | [5 empty] | 0 | 0.508 | 54 | 4.5321 | 4.2328 | 1.197 | 0.95238 | 3.2804 | 72.3814
2006-03-12 | 14:10 | 0 | 15.89 | 0 | 3 | 0 | 29.464 | 29.874 | 28.839 | 29.079 | 8.431 | 24.742 | 6.906 | 0 | 0 | 56.451 | 52.859 | 44.135 | 18.681 | 0 | 0 | 54.579 | 31.512 | [5 empty] | 0 | 0.385 | 55 | 4.5854 | 4.2834 | 1.1992 | 0.95238 | 3.331 | 72.6449
2006-03-12 | 14:11 | 0 | 15.92 | 0 | 2 | 0 | 29.374 | 29.712 | 28.604 | 28.94 | 8.461 | 24.629 | 7.216 | 0 | 0 | 56.435 | 52.863 | 44.164 | 18.736 | 0 | 0 | 54.607 | 31.519 | [5 empty] | 0 | 0.434 | 56 | 4.4951 | 4.1976 | 1.1955 | 0.95238 | 3.2452 | 72.1948
2006-03-12 | 14:12 | 0 | 15.895 | 0 | 3 | 0 | 29.253 | 29.614 | 28.579 | 28.724 | 8.265 | 24.58 | 7.064 | 0 | 0 | 56.435 | 52.863 | 44.094 | 18.711 | 0 | 0 | 54.651 | 31.541 | [5 empty] | 0 | 0.529 | 57 | 4.5394 | 4.2397 | 1.1973 | 0.95238 | 3.2873 | 72.4177
2006-03-12 | 14:13 | 1 | 15.92 | 0 | 2 | 0 | 40.238 | 29.518 | 28.459 | 28.699 | 20.068 | 24.651 | 7.468 | 0 | 0 | 56.501 | 52.863 | 44.07 | 18.736 | 0 | 0 | 54.651 | 31.495 | [5 empty] | 15.92 | 11.539 | 58 | 4.4217 | 4.1279 | 1.1926 | 0.95238 | 3.1755 | 71.8154
2006-03-12 | 14:14 | 0 | 15.945 | 1 | 3 | 0 | 50.272 | 34.598 | 28.484 | 28.604 | 24.965 | 24.506 | 7.545 | 1 | 0 | 56.435 | 52.84 | 44.07 | 18.711 | 0 | 0 | 54.607 | 31.566 | [5 empty] | 0 | 21.668 | 59 | 4.3993 | 4.1065 | 1.1916 | 0.95238 | 3.1542 | 71.697
2006-03-12 | 14:15 | 0 | 15.89 | 0 | 2 | 0 | 51.757 | 48.478 | 28.356 | 28.574 | 25.73 | 24.526 | 7.21 | 2 | 0 | 56.407 | 52.835 | 44.159 | 18.706 | 0 | 0 | 54.509 | 31.561 | [5 empty] | 0 | 23.183 | 60 | 4.4968 | 4.1993 | 1.1956 | 0.95238 | 3.2469 | 72.2037
2006-03-12 | 14:16 | 0 | 15.915 | 0 | 3 | 0 | 52.492 | 51.414 | 28.525 | 28.574 | 26.093 | 24.526 | 6.906 | 2 | 0 | 56.407 | 52.789 | 44.018 | 18.706 | 0 | 0 | 54.532 | 31.561 | [5 empty] | 0 | 23.918 | 61 | 4.5854 | 4.2834 | 1.1992 | 0.95238 | 3.331 | 72.6449
2006-03-12 | 14:17 | 1 | 15.938 | 0 | 2 | 1 | 52.721 | 52.284 | 28.645 | 28.55 | 26.019 | 24.646 | 7.54 | 1 | 0 | 56.385 | 52.812 | 44.159 | 18.731 | 0 | 0 | 54.485 | 31.561 | [5 empty] | 15.938 | 24.171 | 62 | 4.4008 | 4.1079 | 1.1917 | 0.95238 | 3.1555 | 71.7047
2006-03-12 | 14:18 | 0 | 15.963 | 0 | 2 | 0 | 53.017 | 52.56 | 28.67 | 28.621 | 26.188 | 24.526 | 7.514 | 2 | 0 | 56.385 | 52.835 | 44.087 | 18.731 | 0 | 0 | 54.485 | 31.512 | [5 empty] | 0 | 24.396 | 0 | 4.4083 | 4.1151 | 1.192 | 0.95238 | 3.1627 | 71.7448
2006-03-12 | 14:19 | 0 | 15.988 | 0 | 2 | 0 | 53.157 | 53.043 | 28.743 | 28.574 | 24.6 | 24.551 | 7.765 | 1 | 0 | 56.453 | 52.861 | 44.042 | 18.731 | 0 | 0 | 54.488 | 31.49 | [5 empty] | 0 | 24.583 | 1 | 4.3352 | 4.0456 | 3.9867 | 3.75 | 0.29565 | 6.8197
2006-03-12 | 14:20 | 0 | 15.963 | 0 | 2 | 0 | 53.02 | 53.251 | 28.815 | 28.792 | 24.045 | 24.501 | 7.913 | 2 | 0 | 56.453 | 52.838 | 44.09 | 18.756 | 0 | 0 | 54.443 | 31.514 | [5 empty] | 0 | 24.228 | 2 | 4.2921 | 4.0047 | 3.9849 | 3.75 | 0.25468 | 5.9337
2006-03-12 | 14:21 | 1 | 16.044 | 0 | 2 | 0 | 52.728 | 53.162 | 28.964 | 28.893 | 24.195 | 24.58 | 7.795 | 1 | 0 | 56.503 | 52.842 | 44.188 | 18.761 | 0 | 0 | 54.471 | 31.519 | [5 empty] | 16.044 | 23.835 | 3 | 4.3265 | 4.0373 | 3.9863 | 3.75 | 0.28734 | 6.6415
2006-03-12 | 14:22 | 0 | 16.069 | 0 | 2 | 0 | 52.52 | 53.027 | 29.013 | 28.893 | 24.484 | 24.604 | 7.82 | 2 | 0 | 56.549 | 52.889 | 44.212 | 18.786 | 0 | 0 | 54.516 | 31.495 | [5 empty] | 0 | 23.627 | 4 | 4.3192 | 4.0304 | 3.986 | 3.75 | 0.28042 | 6.4925
2006-03-12 | 14:23 | 0 | 16.038 | 1 | 2 | 0 | 52.378 | 52.7 | 28.984 | 28.864 | 24.864 | 24.501 | 7.863 | 1 | 0 | 56.544 | 52.861 | 44.207 | 18.731 | 0 | 0 | 54.42 | 31.441 | [5 empty] | 0 | 23.514 | 5 | 4.3067 | 4.0185 | 3.9855 | 3.75 | 0.26852 | 6.235
2006-03-12 | 14:24 | 0 | 16.069 | 0 | 2 | 0 | 52.705 | 52.658 | 28.942 | 28.964 | 24.653 | 24.509 | 7.697 | 1 | 0 | 56.592 | 52.842 | 44.212 | 18.786 | 0 | 0 | 54.401 | 31.47 | [5 empty] | 0 | 23.741 | 6 | 4.355 | 4.0645 | 3.9875 | 3.75 | 0.31447 | 7.2208
2006-03-12 | 14:25 | 0 | 16.094 | 0 | 2 | 0 | 53.3 | 52.819 | 28.893 | 28.942 | 24.58 | 24.509 | 7.445 | 2 | 0 | 56.615 | 52.866 | 44.166 | 18.786 | 0 | 0 | 54.378 | 31.47 | [5 empty] | 0 | 24.358 | 7 | 4.4284 | 4.1342 | 3.9904 | 3.75 | 0.38422 | 8.6763
2006-03-12 | 14:26 | 1 | 16.044 | 0 | 2 | 0 | 53.598 | 53.118 | 28.822 | 28.918 | 24.653 | 24.629 | 7.393 | 1 | 0 | 56.661 | 52.889 | 44.118 | 18.786 | 0 | 0 | 54.401 | 31.47 | [5 empty] | 16.044 | 24.68 | 8 | 4.4436 | 4.1486 | 3.9911 | 3.75 | 0.39862 | 8.9707
2006-03-12 | 14:27 | 0 | 16.094 | 0 | 2 | 0 | 54.035 | 53.437 | 28.844 | 28.844 | 24.629 | 24.509 | 7.267 | 2 | 0 | 56.661 | 52.866 | 44.166 | 18.786 | 0 | 0 | 54.355 | 31.47 | [5 empty] | 0 | 25.191 | 9 | 4.4802 | 4.1835 | 3.9925 | 3.75 | 0.43349 | 9.6757
2006-03-12 | 14:28 | 0 | 16.116 | 0 | 2 | 0 | 54.264 | 53.806 | 28.699 | 28.844 | 24.749 | 24.555 | 7.82 | 1 | 0 | 56.661 | 52.819 | 44.212 | 18.736 | 0 | 0 | 54.334 | 31.495 | [5 empty] | 0 | 25.42 | 10 | 4.3192 | 4.0304 | 3.986 | 3.75 | 0.28042 | 6.4925
2006-03-12 | 14:29 | 0 | 16.149 | 0 | 1 | 0 | 54.639 | 54.156 | 28.78 | 28.731 | 24.901 | 24.756 | 8.074 | 1 | 0 | 56.69 | 52.873 | 44.219 | 18.769 | 0 | 0 | 54.341 | 31.526 | [5 empty] | 0 | 25.908 | 11 | 4.2453 | 3.9601 | 3.983 | 3.75 | 0.21012 | 4.9495
2006-03-12 | 14:30 | 0 | 16.101 | 0 | 2 | 0 | 54.983 | 54.294 | 28.731 | 28.586 | 25.19 | 24.661 | 7.926 | 1 | 0 | 56.713 | 52.873 | 44.291 | 18.769 | 0 | 0 | 54.341 | 31.502 | [5 empty] | 0 | 26.397 | 12 | 4.2883 | 4.0011 | 3.9848 | 3.75 | 0.25108 | 5.855
2006-03-12 | 14:31 | 1 | 16.126 | 0 | 2 | 0 | 55.326 | 54.754 | 28.685 | 28.586 | 25.311 | 24.685 | 8.15 | 2 | 0 | 56.757 | 52.849 | 44.219 | 18.794 | 0 | 0 | 54.364 | 31.526 | [5 empty] | 16.126 | 26.74 | 13 | 4.2231 | 3.9391 | 3.9821 | 3.75 | 0.18908 | 4.4773
2006-03-12 | 14:32 | 0 | 16.126 | 0 | 1 | 0 | 55.533 | 55.074 | 28.78 | 28.611 | 25.311 | 24.806 | 8.124 | 1 | 0 | 56.713 | 52.826 | 44.173 | 18.794 | 0 | 0 | 54.317 | 31.526 | [5 empty] | 0 | 26.922 | 14 | 4.2307 | 3.9463 | 3.9824 | 3.75 | 0.19628 | 4.6394
2006-03-12 | 14:33 | 0 | 16.126 | 1 | 2 | 1 | 55.601 | 55.349 | 28.829 | 28.564 | 25.985 | 24.732 | 7.903 | 2 | 0 | 56.757 | 52.803 | 44.197 | 18.794 | 0 | 0 | 54.317 | 31.502 | [5 empty] | 0 | 27.037 | 15 | 4.295 | 4.0074 | 3.985 | 3.75 | 0.25745 | 5.9941
2006-03-12 | 14:34 | 0 | 16.109 | 0 | 2 | 0 | 49.943 | 55.564 | 28.741 | 28.741 | 21.15 | 24.764 | 7.762 | 0 | 0 | 56.766 | 52.903 | 44.204 | 18.801 | 0 | 0 | 54.324 | 31.512 | [5 empty] | 0 | 21.202 | 0 | 4.3361 | 4.0465 | 3.9867 | 3.75 | 0.29648 | 6.8374
2006-03-12 | 14:35 | 0 | 16.084 | 0 | 2 | 0 | 37.153 | 55.678 | 28.837 | 28.692 | 16.059 | 24.982 | 7.638 | 1 | 0 | 56.766 | 52.88 | 44.346 | 18.801 | 0 | 0 | 54.324 | 31.512 | [5 empty] | 0 | 8.461 | 1 | 4.3722 | 4.0808 | 2.5459 | 2.3077 | 1.7731 | 40.554
2006-03-12 | 14:36 | 0 | 16.109 | 0 | 1 | 0 | 32.969 | 47.124 | 29.006 | 28.741 | 12.63 | 24.862 | 7.36 | 0 | 0 | 56.766 | 52.856 | 44.346 | 18.751 | 0 | 0 | 54.301 | 31.534 | [5 empty] | 0 | 4.228 | 2 | 4.4532 | 4.1578 | 2.5491 | 2.3077 | 1.8501 | 41.5448
2006-03-12 | 14:37 | 0 | 16.134 | 0 | 2 | 0 | 31.534 | 37.435 | 29.077 | 28.861 | 12.134 | 24.884 | 7.712 | 0 | 0 | 56.786 | 52.88 | 44.322 | 18.776 | 0 | 0 | 54.278 | 31.512 | [5 empty] | 0 | 2.673 | 3 | 4.3507 | 4.0603 | 2.545 | 2.3077 | 1.7526 | 40.2841
2006-03-12 | 14:38 | 0 | 16.084 | 0 | 2 | 0 | 30.909 | 33.699 | 29.101 | 28.932 | 11.616 | 24.958 | 7.561 | 0 | 0 | 56.766 | 52.833 | 44.181 | 18.751 | 0 | 0 | 54.278 | 31.534 | [5 empty] | 0 | 1.977 | 4 | 4.3946 | 4.1021 | 2.5468 | 2.3077 | 1.7944 | 40.8321
2006-03-12 | 14:39 | 0 | 16.069 | 0 | 2 | 0 | 30.484 | 32.122 | 28.989 | 29.038 | 12.021 | 25.087 | 7.671 | 1 | 0 | 56.772 | 52.842 | 44.142 | 18.761 | 0 | 0 | 54.308 | 31.47 | [5 empty] | 0 | 1.446 | 5 | 4.3626 | 4.0717 | 2.5455 | 2.3077 | 1.764 | 40.434
2006-03-12 | 14:40 | 0 | 16.054 | 0 | 2 | 0 | 30.298 | 31.382 | 29.02 | 29.119 | 12.25 | 25.046 | 7.53 | 0 | 0 | 56.757 | 52.849 | 44.219 | 18.794 | 0 | 0 | 54.338 | 31.526 | [5 empty] | 0 | 1.179 | 6 | 4.4037 | 4.1107 | 2.5471 | 2.3077 | 1.803 | 40.9433
2006-03-12 | 14:41 | 0 | 16.059 | 0 | 2 | 0 | 30.087 | 30.857 | 28.979 | 29.219 | 11.936 | 25.075 | 7.785 | 0 | 0 | 56.784 | 52.854 | 44.106 | 18.824 | 0 | 0 | 54.322 | 31.485 | [5 empty] | 0 | 0.868 | 7 | 4.3294 | 4.0401 | 2.5441 | 2.3077 | 1.7324 | 40.0152
2006-03-12 | 14:42 | 0 | 16.059 | 0 | 2 | 0 | 29.967 | 30.546 | 28.785 | 29.099 | 10.897 | 25.051 | 7.712 | 0 | 0 | 56.695 | 52.831 | 44.247 | 18.799 | 0 | 0 | 54.299 | 31.509 | [5 empty] | 0 | 0.868 | 8 | 4.3507 | 4.0603 | 2.545 | 2.3077 | 1.7526 | 40.2841
2006-03-12 | 14:43 | 0 | 16.054 | 0 | 3 | 0 | 29.768 | 30.298 | 28.756 | 29.02 | 10.99 | 25.119 | 7.404 | 0 | 0 | 56.668 | 52.756 | 44.008 | 18.746 | 0 | 0 | 54.271 | 31.455 | [5 empty] | 0 | 0.748 | 9 | 4.4404 | 4.1456 | 2.5486 | 2.3077 | 1.8379 | 41.3904
2006-03-12 | 14:44 | 0 | 16.028 | 1 | 2 | 0 | 42.738 | 30.058 | 28.709 | 28.876 | 22.709 | 24.855 | 7.604 | 0 | 0 | 56.599 | 52.712 | 44.054 | 18.746 | 0 | 0 | 54.201 | 31.48 | [5 empty] | 0 | 13.862 | 10 | 4.3821 | 4.0902 | 2.5463 | 2.3077 | 1.7825 | 40.6772
2006-03-12 | 14:45 | 1 | 16.084 | 0 | 3 | 0 | 50.697 | 35.598 | 28.859 | 29.05 | 26.353 | 25.004 | 7.785 | 1 | 0 | 56.604 | 52.74 | 43.989 | 18.799 | 0 | 0 | 54.184 | 31.509 | [5 empty] | 16.084 | 21.647 | 11 | 4.3294 | 4.0401 | 2.5441 | 2.3077 | 1.7324 | 40.0152
2006-03-12 | 14:46 | 0 | 16.003 | 0 | 2 | 0 | 51.862 | 48.881 | 29.02 | 29.19 | 26.637 | 24.95 | 6.845 | 2 | 0 | 56.553 | 52.641 | 43.96 | 18.721 | 0 | 0 | 54.156 | 31.431 | [5 empty] | 0 | 22.672 | 12 | 4.6031 | 4.3003 | 2.5552 | 2.3077 | 1.9926 | 43.2881
2006-03-12 | 14:47 | 0 | 16.033 | 0 | 3 | 0 | 52.373 | 51.547 | 29.244 | 29.339 | 26.039 | 24.835 | 7.179 | 1 | 0 | 56.492 | 52.67 | 43.989 | 18.776 | 0 | 0 | 54.299 | 31.436 | [5 empty] | 0 | 23.034 | 13 | 4.5059 | 4.2079 | 2.5513 | 2.3077 | 1.9002 | 42.1707
2006-03-12 | 14:48 | 0 | 16.008 | 0 | 2 | 0 | 52.508 | 52.051 | 29.099 | 29.413 | 25.389 | 24.761 | 7.205 | 2 | 0 | 56.446 | 52.693 | 44.082 | 18.776 | 0 | 0 | 54.138 | 31.436 | [5 empty] | 0 | 23.095 | 14 | 4.4983 | 4.2007 | 2.551 | 2.3077 | 1.893 | 42.0817
2006-03-12 | 14:49 | 1 | 16.033 | 0 | 2 | 0 | 52.532 | 52.35 | 29.148 | 29.268 | 24.786 | 24.98 | 7.661 | 1 | 0 | 56.446 | 52.646 | 44.037 | 18.751 | 0 | 0 | 54.208 | 31.485 | [5 empty] | 16.033 | 23.264 | 15 | 4.3655 | 4.0744 | 2.5456 | 2.3077 | 1.7667 | 40.4704
2006-03-12 | 14:50 | 0 | 16.033 | 0 | 1 | 0 | 52.968 | 52.487 | 29.268 | 29.219 | 24.33 | 24.835 | 7.409 | 1 | 0 | 56.469 | 52.67 | 44.013 | 18.751 | 0 | 0 | 54.208 | 31.46 | [5 empty] | 0 | 23.749 | 16 | 4.4389 | 4.1442 | 2.5486 | 2.3077 | 1.8365 | 41.3728
2006-03-12 | 14:51 | 0 | 16.059 | 0 | 2 | 0 | 53.542 | 52.693 | 29.437 | 29.268 | 24.425 | 24.906 | 7.331 | 2 | 0 | 56.426 | 52.67 | 44.037 | 18.751 | 0 | 0 | 54.208 | 31.436 | [5 empty] | 0 | 24.274 | 17 | 4.4616 | 4.1658 | 2.5495 | 2.3077 | 1.8581 | 41.6461
2006-03-12 | 14:52 | 0 | 16.059 | 0 | 2 | 0 | 53.953 | 53.129 | 29.533 | 29.315 | 24.474 | 25.004 | 7.105 | 1 | 0 | 56.446 | 52.646 | 44.061 | 18.751 | 0 | 0 | 54.229 | 31.46 | [5 empty] | 0 | 24.638 | 18 | 4.5274 | 4.2283 | 2.5522 | 2.3077 | 1.9206 | 42.4224
2006-03-12 | 14:53 | 0 | 16.094 | 1 | 2 | 0 | 54.583 | 53.666 | 29.592 | 29.494 | 24.749 | 24.965 | 7.445 | 1 | 0 | 56.478 | 52.679 | 44.094 | 18.786 | 0 | 0 | 54.217 | 31.495 | [5 empty] | 0 | 25.089 | 19 | 4.4284 | 4.1342 | 2.5481 | 2.3077 | 1.8265 | 41.2457
2006-03-12 | 14:54 | 1 | 16.059 | 0 | 1 | 0 | 54.917 | 54.114 | 29.582 | 29.459 | 24.955 | 25.029 | 7.409 | 1 | 0 | 56.469 | 52.646 | 44.061 | 18.726 | 0 | 0 | 54.161 | 31.436 | [5 empty] | 16.059 | 25.458 | 20 | 4.4389 | 4.1442 | 2.5486 | 2.3077 | 1.8365 | 41.3728
2006-03-12 | 14:55 | 0 | 16.033 | 0 | 2 | 0 | 55.263 | 54.597 | 29.484 | 29.678 | 25.075 | 25.051 | 7.434 | 2 | 0 | 56.515 | 52.693 | 44.082 | 18.751 | 0 | 0 | 54.091 | 31.411 | [5 empty] | 0 | 25.585 | 21 | 4.4316 | 4.1373 | 2.5483 | 2.3077 | 1.8296 | 41.2846
2006-03-12 | 14:56 | 0 | 16.033 | 0 | 2 | 0 | 55.445 | 54.94 | 29.604 | 29.629 | 25.22 | 25.195 | 7.635 | 1 | 0 | 56.56 | 52.67 | 44.037 | 18.751 | 0 | 0 | 54.091 | 31.387 | [5 empty] | 0 | 25.816 | 22 | 4.3731 | 4.0816 | 2.5459 | 2.3077 | 1.7739 | 40.5649
2006-03-12 | 14:57 | 0 | 16.033 | 0 | 2 | 0 | 55.629 | 55.284 | 29.678 | 29.727 | 25.365 | 25.171 | 7.61 | 1 | 0 | 56.492 | 52.67 | 44.178 | 18.874 | 0 | 0 | 54.114 | 31.387 | [5 empty] | 0 | 25.902 | 23 | 4.3804 | 4.0886 | 2.5462 | 2.3077 | 1.7809 | 40.6555
2006-03-12 | 14:58 | 0 | 16.008 | 0 | 1 | 0 | 48.863 | 55.491 | 29.847 | 29.678 | 21.799 | 25.22 | 7.661 | 1 | 0 | 56.537 | 52.646 | 44.13 | 18.751 | 0 | 0 | 54.114 | 31.411 | [5 empty] | 0 | 19.185 | 24 | 4.3655 | 4.0744 | 2.5456 | 2.3077 | 1.7667 | 40.4704
2006-03-12 | 14:59 | 0 | 16.021 | 0 | 2 | 1 | 37.442 | 55.501 | 29.857 | 29.881 | 18.615 | 25.134 | 7.674 | 1 | 0 | 56.547 | 52.656 | 44.14 | 18.739 | 0 | 0 | 54.124 | 31.399 | [5 empty] | 0 | 7.561 | 25 | 4.3617 | 4.0708 | 2.5454 | 2.3077 | 1.7631 | 40.423
2006-03-12 | 15:00 | 0 | 15.996 | 0 | 2 | 0 | 33.706 | 46.785 | 30.026 | 29.81 | 16.539 | 25.232 | 7.772 | 0 | 0 | 56.547 | 52.634 | 44.14 | 18.713 | 0 | 0 | 54.1 | 31.423 | [5 empty] | 0 | 3.896 | 0 | 4.3332 | 4.0437 | 2.5443 | 2.3077 | 1.736 | 40.0632
2006-03-12 | 15:01 | 0 | 15.996 | 0 | 1 | 0 | 32.434 | 37.937 | 30.05 | 29.857 | 15.108 | 25.232 | 7.7 | 0 | 0 | 56.569 | 52.611 | 44.14 | 18.713 | 0 | 0 | 54.1 | 31.423 | [5 empty] | 0 | 2.577 | 1 | 4.3542 | 4.0636 | 2.8461 | 2.6087 | 1.4549 | 33.415
2006-03-12 | 15:02 | 0 | 15.996 | 0 | 2 | 0 | 31.88 | 34.412 | 30.075 | 30.026 | 12.071 | 25.303 | 7.066 | 0 | 0 | 56.569 | 52.611 | 44.14 | 18.761 | 0 | 0 | 54.147 | 31.448 | [5 empty] | 0 | 1.854 | 2 | 4.5388 | 4.2391 | 2.8536 | 2.6087 | 1.6304 | 35.9223
2006-03-12 | 15:03 | 0 | 15.971 | 1 | 2 | 0 | 31.544 | 33.024 | 30.146 | 30.075 | 10.291 | 25.303 | 7.017 | 0 | 0 | 56.547 | 52.634 | 44.188 | 18.739 | 0 | 0 | 54.079 | 31.399 | [5 empty] | 0 | 1.469 | 3 | 4.553 | 4.2527 | 2.8542 | 2.6087 | 1.644 | 36.1076
2006-03-12 | 15:04 | 0 | 15.996 | 0 | 2 | 0 | 31.23 | 32.338 | 30.195 | 30.195 | 9.972 | 25.352 | 7.471 | 0 | 0 | 56.547 | 52.634 | 44.094 | 18.713 | 0 | 0 | 54.1 | 31.399 | [5 empty] | 0 | 1.035 | 4 | 4.4208 | 4.127 | 2.8488 | 2.6087 | 1.5183 | 34.3448
2006-03-12 | 15:05 | 0 | 15.996 | 0 | 2 | 0 | 31.134 | 31.857 | 29.952 | 30.242 | 10.143 | 25.257 | 7.522 | 0 | 0 | 56.569 | 52.634 | 44.118 | 18.761 | 0 | 0 | 54.1 | 31.423 | [5 empty] | 0 | 0.892 | 5 | 4.406 | 4.1129 | 2.8482 | 2.6087 | 1.5042 | 34.1402
2006-03-12 | 15:06 | 0 | 15.996 | 0 | 3 | 0 | 30.965 | 31.47 | 30.097 | 30.121 | 8.909 | 25.328 | 7.192 | 0 | 0 | 56.501 | 52.564 | 44.094 | 18.713 | 0 | 0 | 54.079 | 31.423 | [5 empty] | 0 | 0.844 | 6 | 4.5021 | 4.2043 | 2.8521 | 2.6087 | 1.5956 | 35.4404
2006-03-12 | 15:07 | 0 | 15.966 | 0 | 2 | 0 | 30.815 | 31.274 | 30.092 | 30.212 | 12.139 | 25.083 | 7.391 | 0 | 0 | 56.428 | 52.536 | 44.042 | 18.708 | 0 | 0 | 54.005 | 31.394 | [5 empty] | 0 | 0.603 | 7 | 4.4441 | 4.1492 | 2.8498 | 2.6087 | 1.5405 | 34.6631
2006-03-12 | 15:08 | 0 | 15.971 | 0 | 3 | 0 | 44.561 | 31.038 | 30.121 | 30.315 | 23.594 | 25.063 | 7.522 | 1 | 0 | 56.412 | 52.541 | 44.023 | 18.688 | 0 | 0 | 53.986 | 31.423 | [5 empty] | 0 | 14.246 | 8 | 4.406 | 4.1129 | 2.8482 | 2.6087 | 1.5042 | 34.1402
2006-03-12 | 15:09 | 1 | 15.996 | 0 | 3 | 0 | 50.501 | 39.935 | 29.977 | 30.46 | 26.701 | 25.014 | 7.623 | 1 | 0 | 56.389 | 52.497 | 43.999 | 18.739 | 0 | 0 | 53.965 | 31.399 | [5 empty] | 15.996 | 20.041 | 9 | 4.3766 | 4.085 | 2.847 | 2.6087 | 1.4763 | 33.7308
2006-03-12 | 15:10 | 0 | 15.971 | 0 | 2 | 0 | 51.923 | 49.813 | 29.832 | 30.315 | 27.954 | 24.918 | 7.244 | 1 | 0 | 56.343 | 52.473 | 43.977 | 18.713 | 0 | 0 | 53.986 | 31.448 | [5 empty] | 0 | 21.608 | 10 | 4.4869 | 4.1899 | 2.8515 | 2.6087 | 1.5812 | 35.2392
2006-03-12 | 15:11 | 0 | 15.971 | 0 | 3 | 0 | 52.221 | 51.671 | 29.641 | 30.195 | 28.17 | 24.918 | 7.674 | 2 | 0 | 56.323 | 52.473 | 44.023 | 18.713 | 0 | 0 | 54.009 | 31.448 | [5 empty] | 0 | 22.026 | 11 | 4.3617 | 4.0708 | 2.8464 | 2.6087 | 1.4621 | 33.522
2006-03-12 | 15:12 | 1 | 15.996 | 0 | 2 | 0 | 52.52 | 52.037 | 29.567 | 30.026 | 27.834 | 24.967 | 7.27 | 1 | 0 | 56.323 | 52.541 | 43.999 | 18.761 | 0 | 0 | 53.986 | 31.423 | [5 empty] | 15.996 | 22.494 | 12 | 4.4794 | 4.1827 | 2.8512 | 2.6087 | 1.574 | 35.1381
2006-03-12 | 15:13 | 0 | 15.991 | 1 | 3 | 0 | 52.627 | 52.445 | 29.611 | 29.707 | 27.996 | 25.105 | 7.313 | 2 | 0 | 56.316 | 52.469 | 43.97 | 18.806 | 0 | 0 | 54.005 | 31.419 | [5 empty] | 0 | 22.92 | 13 | 4.4669 | 4.1708 | 2.8507 | 2.6087 | 1.5621 | 34.9702
2006-03-12 | 15:14 | 0 | 15.966 | 0 | 2 | 0 | 52.627 | 52.721 | 29.467 | 29.658 | 27.853 | 24.938 | 7.44 | 2 | 0 | 56.316 | 52.492 | 44.09 | 18.708 | 0 | 0 | 53.799 | 31.419 | [5 empty] | 0 | 22.969 | 14 | 4.4299 | 4.1356 | 2.8492 | 2.6087 | 1.5269 | 34.4685
2006-03-12 | 15:15 | 0 | 15.933 | 0 | 3 | 0 | 52.002 | 52.735 | 29.604 | 29.58 | 28.542 | 24.906 | 7.558 | 1 | 0 | 56.243 | 52.438 | 43.963 | 18.698 | 0 | 0 | 53.813 | 31.409 | [5 empty] | 0 | 22.422 | 15 | 4.3955 | 4.1029 | 2.8478 | 2.6087 | 1.4942 | 33.9949
2006-03-12 | 15:16 | 1 | 15.933 | 0 | 2 | 0 | 51.955 | 52.368 | 29.604 | 29.604 | 28.086 | 24.931 | 7.635 | 2 | 0 | 56.243 | 52.415 | 43.963 | 18.698 | 0 | 0 | 53.883 | 31.362 | [5 empty] | 15.933 | 22.351 | 16 | 4.3731 | 4.0816 | 2.8469 | 2.6087 | 1.4729 | 33.6818
2006-03-12 | 15:17 | 0 | 15.94 | 0 | 3 | 0 | 51.848 | 52.261 | 29.781 | 29.683 | 28.648 | 25.058 | 7.617 | 1 | 0 | 56.316 | 52.469 | 44.066 | 18.708 | 0 | 0 | 53.89 | 31.419 | [5 empty] | 0 | 22.165 | 17 | 4.3783 | 4.0866 | 2.8471 | 2.6087 | 1.4779 | 33.7553
2006-03-12 | 15:18 | 0 | 15.94 | 0 | 2 | 0 | 51.734 | 52.123 | 29.876 | 29.781 | 29.177 | 25.105 | 7.617 | 2 | 0 | 56.339 | 52.492 | 43.97 | 18.731 | 0 | 0 | 53.844 | 31.419 | [5 empty] | 0 | 21.953 | 18 | 4.3783 | 4.0866 | 2.8471 | 2.6087 | 1.4779 | 33.7553
2006-03-12 | 15:19 | 0 | 15.953 | 0 | 3 | 0 | 51.587 | 52.07 | 30.058 | 29.864 | 30.273 | 25.119 | 7.326 | 1 | 0 | 56.353 | 52.459 | 43.984 | 18.746 | 0 | 0 | 53.811 | 31.455 | [5 empty] | 0 | 21.723 | 19 | 4.4631 | 4.1672 | 2.8505 | 2.6087 | 1.5585 | 34.9192
2006-03-12 | 15:20 | 1 | 15.92 | 0 | 3 | 0 | 51.717 | 51.946 | 30.22 | 30.17 | 29.687 | 25.134 | 7.319 | 2 | 0 | 56.323 | 52.473 | 44.001 | 18.713 | 0 | 0 | 53.713 | 31.399 | [5 empty] | 15.92 | 21.547 | 20 | 4.4651 | 4.1691 | 2.8506 | 2.6087 | 1.5604 | 34.9466
2006-03-12 | 15:21 | 0 | 15.978 | 0 | 2 | 0 | 51.909 | 52.046 | 30.757 | 30.323 | 30.107 | 25.24 | 7.453 | 1 | 0 | 56.375 | 52.48 | 44.102 | 18.721 | 0 | 0 | 53.673 | 31.551 | [5 empty] | 0 | 21.586 | 21 | 4.4261 | 4.132 | 2.8491 | 2.6087 | 1.5233 | 34.4167
2006-03-12 | 15:22 | 0 | 15.978 | 1 | 3 | 1 | 51.587 | 52.207 | 31.431 | 30.757 | 30.587 | 25.24 | 7.53 | 2 | 0 | 56.419 | 52.459 | 44.149 | 18.721 | 0 | 0 | 53.629 | 31.406 | [5 empty] | 0 | 20.83 | 22 | 4.4037 | 4.1107 | 2.8481 | 2.6087 | 1.502 | 34.108
2006-03-12 | 15:23 | 0 | 15.945 | 0 | 3 | 0 | 51.556 | 52.016 | 32.314 | 31.374 | 30.266 | 25.254 | 7.293 | 1 | 0 | 56.412 | 52.429 | 43.977 | 18.688 | 0 | 0 | 53.552 | 31.423 | [5 empty] | 0 | 20.182 | 0 | 4.4727 | 4.1763 | 2.8509 | 2.6087 | 1.5676 | 35.0484
2006-03-12 | 15:24 | 1 | 15.92 | 0 | 3 | 0 | 51.878 | 52.039 | 33.118 | 32.434 | 30.242 | 25.279 | 7.241 | 2 | 0 | 56.369 | 52.473 | 44.023 | 18.761 | 0 | 0 | 53.484 | 31.399 | [5 empty] | 15.92 | 19.444 | 1 | 4.4878 | 4.1907 | 4.5286 | 4.2857 | -0.095023 | -2.1174
2006-03-12 | 15:25 | 0 | 15.895 | 0 | 2 | 0 | 51.741 | 52.107 | 33.871 | 33.237 | 30.531 | 25.279 | 7.419 | 2 | 0 | 56.389 | 52.473 | 44.094 | 18.761 | 0 | 0 | 53.484 | 31.399 | [5 empty] | 0 | 18.504 | 2 | 4.436 | 4.1414 | 4.5265 | 4.2857 | -0.14429 | -3.2528
2006-03-12 | 15:26 | 0 | 15.895 | 0 | 3 | 0 | 51.993 | 52.084 | 34.34 | 33.964 | 30.362 | 25.279 | 7.471 | 1 | 0 | 56.369 | 52.429 | 44.047 | 18.713 | 0 | 0 | 53.461 | 31.448 | [5 empty] | 0 | 18.029 | 3 | 4.4208 | 4.127 | 4.5259 | 4.2857 | -0.15869 | -3.5895
2006-03-12 | 15:27 | 0 | 15.928 | 0 | 3 | 0 | 52.161 | 52.345 | 34.818 | 34.467 | 30.107 | 25.431 | 7.504 | 1 | 0 | 56.442 | 52.48 | 44.078 | 18.746 | 0 | 0 | 53.491 | 31.502 | [5 empty] | 0 | 17.694 | 4 | 4.4112 | 4.1179 | 4.5255 | 4.2857 | -0.16782 | -3.8044
2006-03-12 | 15:28 | 0 | 15.895 | 0 | 3 | 0 | 51.993 | 52.473 | 34.952 | 34.835 | 29.881 | 25.328 | 7.496 | 2 | 0 | 56.458 | 52.473 | 44.07 | 18.786 | 0 | 0 | 53.484 | 31.47 | [5 empty] | 0 | 17.158 | 5 | 4.4136 | 4.1201 | 4.5256 | 4.2857 | -0.16561 | -3.7522
2006-03-12 | 15:29 | 1 | 15.92 | 0 | 3 | 0 | 51.694 | 52.45 | 35.397 | 35.093 | 30.34 | 25.377 | 7.319 | 1 | 0 | 56.435 | 52.473 | 44.118 | 18.786 | 0 | 0 | 53.484 | 31.495 | [5 empty] | 15.92 | 16.601 | 6 | 4.4651 | 4.1691 | 4.5277 | 4.2857 | -0.11661 | -2.6117
2006-03-12 | 15:30 | 0 | 15.92 | 0 | 3 | 0 | 51.65 | 52.084 | 35.069 | 35.61 | 30.7 | 25.472 | 7.319 | 1 | 0 | 56.458 | 52.473 | 44.142 | 18.811 | 0 | 0 | 53.391 | 31.495 | [5 empty] | 0 | 16.04 | 7 | 4.4651 | 4.1691 | 4.5277 | 4.2857 | -0.11661 | -2.6117
2006-03-12 | 15:31 | 0 | 15.915 | 0 | 3 | 0 | 52.011 | 52.032 | 34.689 | 35.158 | 31.08 | 25.419 | 7.11 | 2 | 0 | 56.407 | 52.445 | 44.231 | 18.731 | 0 | 0 | 53.339 | 31.465 | [5 empty] | 0 | 16.853 | 8 | 4.526 | 4.227 | 4.5301 | 4.2857 | -0.058762 | -1.2983
2006-03-12 | 15:32 | 0 | 15.92 | 1 | 3 | 0 | 52.221 | 52.406 | 34.598 | 35.022 | 31.857 | 25.521 | 7.089 | 1 | 0 | 56.435 | 52.473 | 44.212 | 18.786 | 0 | 0 | 53.346 | 31.495 | [5 empty] | 0 | 17.199 | 9 | 4.5321 | 4.2328 | 4.5304 | 4.2857 | -0.052949 | -1.1683
2006-03-12 | 15:33 | 1 | 15.895 | 0 | 3 | 0 | 52.429 | 52.588 | 34.598 | 34.856 | 32.193 | 25.568 | 7.115 | 1 | 0 | 56.458 | 52.52 | 44.305 | 18.786 | 0 | 0 | 53.346 | 31.519 | [5 empty] | 15.895 | 17.573 | 10 | 4.5245 | 4.2256 | 4.5301 | 4.2857 | -0.060146 | -1.3293
2006-03-12 | 15:34 | 0 | 15.89 | 0 | 3 | 0 | 52.378 | 52.698 | 34.641 | 34.9 | 31.948 | 25.539 | 7.313 | 2 | 0 | 56.43 | 52.445 | 44.3 | 18.781 | 0 | 0 | 53.295 | 31.49 | [5 empty] | 0 | 17.478 | 11 | 4.4669 | 4.1708 | 4.5277 | 4.2857 | -0.11495 | -2.5735
2006-03-12 | 15:35 | 0 | 15.89 | 0 | 3 | 0 | 52.492 | 52.653 | 34.665 | 34.923 | 32.117 | 25.492 | 7.362 | 1 | 0 | 56.407 | 52.401 | 44.255 | 18.756 | 0 | 0 | 53.363 | 31.49 | [5 empty] | 0 | 17.569 | 12 | 4.4526 | 4.1572 | 4.5271 | 4.2857 | -0.12852 | -2.8863
2006-03-12 | 15:36 | 0 | 15.89 | 0 | 3 | 1 | 52.515 | 52.768 | 34.852 | 34.9 | 31.924 | 25.708 | 7.339 | 1 | 0 | 56.476 | 52.445 | 44.231 | 18.731 | 0 | 0 | 53.339 | 31.514 | [5 empty] | 0 | 17.615 | 13 | 4.4593 | 4.1636 | 4.5274 | 4.2857 | -0.12215 | -2.7392
2006-03-12 | 15:37 | 1 | 15.89 | 0 | 3 | 0 | 52.606 | 52.905 | 34.852 | 35.017 | 31.73 | 25.563 | 7.465 | 2 | 0 | 56.407 | 52.401 | 44.255 | 18.781 | 0 | 0 | 53.339 | 31.514 | [5 empty] | 15.89 | 17.589 | 0 | 4.4226 | 4.1287 | 4.5259 | 4.2857 | -0.15703 | -3.5505
2006-03-12 | 15:38 | 0 | 15.883 | 0 | 3 | 0 | 52.623 | 52.898 | 34.916 | 35.127 | 31.338 | 25.58 | 7.432 | 1 | 0 | 56.378 | 52.371 | 44.224 | 18.774 | 0 | 0 | 53.241 | 31.507 | [5 empty] | 0 | 17.496 | 1 | 4.4322 | 4.1378 | 3.9906 | 3.75 | 0.38782 | 8.7501
2006-03-12 | 15:39 | 0 | 15.908 | 0 | 2 | 0 | 52.693 | 53.038 | 35.105 | 35.222 | 31.291 | 25.654 | 7.406 | 1 | 0 | 56.471 | 52.487 | 44.271 | 18.849 | 0 | 0 | 53.314 | 31.605 | [5 empty] | 0 | 17.471 | 2 | 4.4398 | 4.145 | 3.9909 | 3.75 | 0.39502 | 8.8973
2006-03-12 | 15:40 | 0 | 15.9 | 0 | 3 | 0 | 52.756 | 52.938 | 35.122 | 35.285 | 30.73 | 25.718 | 7.576 | 2 | 0 | 56.442 | 52.41 | 44.405 | 18.816 | 0 | 0 | 53.283 | 31.573 | [5 empty] | 0 | 17.471 | 3 | 4.3903 | 4.098 | 3.9889 | 3.75 | 0.34796 | 7.9258
2006-03-12 | 15:41 | 0 | 15.925 | 1 | 3 | 0 | 52.756 | 53.031 | 35.239 | 35.263 | 30.32 | 25.813 | 7.651 | 1 | 0 | 56.442 | 52.434 | 44.216 | 18.816 | 0 | 0 | 53.307 | 31.524 | [5 empty] | 0 | 17.493 | 4 | 4.3684 | 4.0772 | 3.988 | 3.75 | 0.3272 | 7.4902
2006-03-12 | 15:42 | 1 | 15.951 | 0 | 3 | 0 | 52.641 | 53.008 | 35.239 | 35.426 | 30.031 | 25.813 | 7.677 | 1 | 0 | 56.442 | 52.41 | 44.405 | 18.839 | 0 | 0 | 53.283 | 31.549 | [5 empty] | 15.951 | 17.215 | 5 | 4.3609 | 4.07 | 3.9877 | 3.75 | 0.32001 | 7.3382
2006-03-12 | 15:43 | 0 | 15.925 | 0 | 2 | 0 | 52.663 | 52.847 | 35.38 | 35.38 | 30.031 | 26.007 | 7.702 | 1 | 0 | 56.442 | 52.387 | 44.24 | 18.791 | 0 | 0 | 53.213 | 31.499 | [5 empty] | 0 | 17.283 | 6 | 4.3536 | 4.0631 | 3.9874 | 3.75 | 0.31309 | 7.1915
2006-03-12 | 15:44 | 0 | 15.777 | 0 | 3 | 0 | 53.19 | 52.894 | 35.239 | 35.404 | 30.465 | 25.887 | 7.576 | 2 | 0 | 56.419 | 52.41 | 44.312 | 18.839 | 0 | 0 | 53.19 | 31.524 | [5 empty] | 0 | 17.786 | 7 | 4.3903 | 4.098 | 3.9889 | 3.75 | 0.34796 | 7.9258
2006-03-12 | 15:45 | 0 | 15.704 | 0 | 2 | 0 | 53.559 | 53.328 | 35.309 | 35.38 | 30.44 | 26.032 | 7.825 | 1 | 0 | 56.419 | 52.41 | 44.24 | 18.839 | 0 | 0 | 53.169 | 31.499 | [5 empty] | 0 | 18.179 | 8 | 4.3178 | 4.029 | 3.986 | 3.75 | 0.27904 | 6.4626
2006-03-12 | 15:46 | 0 | 15.752 | 0 | 3 | 0 | 53.855 | 53.741 | 35.38 | 35.404 | 30.345 | 25.958 | 7.775 | 1 | 0 | 56.396 | 52.366 | 44.288 | 18.864 | 0 | 0 | 53.146 | 31.499 | [5 empty] | 0 | 18.451 | 9 | 4.3323 | 4.0429 | 3.9866 | 3.75 | 0.29288 | 6.7604
2006-03-12 | 15:47 | 1 | 15.752 | 0 | 2 | 0 | 54.429 | 53.925 | 35.285 | 35.38 | 30.511 | 26.056 | 7.8 | 1 | 0 | 56.419 | 52.41 | 44.24 | 18.816 | 0 | 0 | 53.19 | 31.524 | [5 empty] | 15.752 | 19.049 | 10 | 4.325 | 4.036 | 3.9863 | 3.75 | 0.28596 | 6.6117
2006-03-12 | 15:48 | 0 | 15.769 | 0 | 3 | 0 | 54.651 | 54.422 | 35.349 | 35.349 | 30.504 | 26.12 | 7.966 | 2 | 0 | 56.412 | 52.336 | 44.257 | 18.759 | 0 | 0 | 53.139 | 31.541 | [5 empty] | 0 | 19.302 | 11 | 4.2767 | 3.99 | 3.9843 | 3.75 | 0.24001 | 5.6121
2006-03-12 | 15:49 | 0 | 15.802 | 0 | 2 | 0 | 54.866 | 54.796 | 35.285 | 35.38 | 30.536 | 26.078 | 7.775 | 1 | 0 | 56.396 | 52.319 | 44.336 | 18.839 | 0 | 0 | 53.122 | 31.598 | [5 empty] | 0 | 19.486 | 12 | 4.3323 | 4.0429 | 3.9866 | 3.75 | 0.29288 | 6.7604
2006-03-12 | 15:50 | 0 | 15.817 | 1 | 2 | 0 | 55.293 | 54.903 | 35.301 | 35.349 | 30.649 | 26.024 | 7.818 | 1 | 0 | 56.366 | 52.289 | 44.281 | 18.806 | 0 | 0 | 53.183 | 31.541 | [5 empty] | 0 | 19.944 | 13 | 4.3198 | 4.031 | 3.986 | 3.75 | 0.28098 | 6.5044
2006-03-12 | 15:51 | 0 | 15.842 | 0 | 3 | 0 | 55.683 | 55.407 | 35.325 | 35.349 | 30.553 | 26.144 | 7.391 | 1 | 0 | 56.389 | 52.312 | 44.257 | 18.832 | 0 | 0 | 53.183 | 31.517 | [5 empty] | 0 | 20.334 | 14 | 4.4441 | 4.1492 | 3.9911 | 3.75 | 0.39917 | 8.982
2006-03-12 | 15:52 | 1 | 15.875 | 0 | 6 | 1 | 46.93 | 55.713 | 35.191 | 37.966 | 34.416 | 26.152 | 7.347 | 1 | 1 | 52.504 | 52.387 | 47.777 | 18.864 | 0 | 0 | 53.099 | 31.549 | [5 empty] | 15.875 | 8.964 | 15 | 4.457 | 4.1614 | 3.9916 | 3.75 | 0.41135 | 9.2294
2006-03-12 | 15:53 | 0 | 15.893 | 0 | 15 | 0 | 58.922 | 55.477 | 37.536 | 48.895 | 51.829 | 26.191 | 7.465 | 2 | 0 | 58.137 | 52.198 | 50.455 | 18.784 | 0 | 0 | 53.069 | 31.178 | [5 empty] | 0 | 10.027 | 0 | 4.4226 | 4.1287 | 3.9902 | 3.75 | 0.37869 | 8.5626
2006-03-12 | 15:54 | 1 | 15.918 | 0 | 14 | 0 | 66.658 | 55.225 | 40.966 | 56.702 | 57.128 | 26.12 | 7.767 | 1 | 0 | 64.73 | 52.014 | 57.039 | 18.832 | 0 | 0 | 53.092 | 32.622 | [5 empty] | 15.918 | 9.956 | 1 | 4.3346 | 4.0451 | 8.8081 | 8.5714 | -4.5263 | -104.4221
2006-03-12 | 15:55 | 1 | 15.943 | 0 | 15 | 0 | 69.927 | 54.812 | 44.14 | 60.942 | 59.146 | 26.088 | 7.785 | 0 | 0 | 68.318 | 52.168 | 60.755 | 18.799 | 0 | 0 | 53.062 | 36.351 | [5 empty] | 15.943 | 8.985 | 2 | 4.3294 | 4.0401 | 8.8079 | 8.5714 | -4.5313 | -104.6637
2006-03-12 | 15:56 | 1 | 15.966 | 0 | 15 | 0 | 70.873 | 54.513 | 46.396 | 62.847 | 60.312 | 26.144 | 7.491 | 1 | 0 | 69.708 | 52.726 | 62.713 | 18.832 | 0 | 0 | 53.069 | 39.275 | [5 empty] | 15.966 | 8.026 | 3 | 4.415 | 4.1215 | 8.8113 | 8.5714 | -4.4499 | -100.7909
2006-03-12 | 15:57 | 0 | 15.958 | 1 | 15 | 0 | 71.13 | 54.231 | 48.062 | 63.849 | 60.462 | 26.159 | 7.535 | 0 | 0 | 70.12 | 53.36 | 63.603 | 18.824 | 0 | 0 | 53.29 | 41.289 | [5 empty] | 0 | 7.281 | 4 | 4.4022 | 4.1093 | 8.8108 | 8.5714 | -4.4621 | -101.3609
2006-03-12 | 15:58 | 1 | 15.966 | 0 | 15 | 0 | 71.202 | 54.033 | 49.446 | 64.552 | 60.581 | 26.215 | 7.187 | 0 | 0 | 70.346 | 54.1 | 64.26 | 18.832 | 0 | 0 | 53.549 | 42.8 | [5 empty] | 15.966 | 6.65 | 5 | 4.5035 | 4.2056 | 8.8149 | 8.5714 | -4.3658 | -96.9412
2006-03-12 | 15:59 | 0 | 16.018 | 0 | 15 | 1 | 71.113 | 53.825 | 50.385 | 64.931 | 60.515 | 26 | 7.494 | 0 | 1 | 70.366 | 54.604 | 64.73 | 18.784 | 0 | 0 | 53.778 | 43.858 | [5 empty] | 0 | 6.182 | 6 | 4.4141 | 4.1207 | 8.8113 | 8.5714 | -4.4508 | -100.8296
2006-03-12 | 16:00 | 1 | 15.943 | 0 | 15 | 0 | 71.092 | 53.619 | 51.12 | 65.401 | 59.258 | 25.929 | 7.62 | 1 | 0 | 70.388 | 55.155 | 65.223 | 18.734 | 0 | 0 | 54.054 | 44.813 | [5 empty] | 15.943 | 5.691 | 0 | 4.3775 | 4.0858 | 8.8098 | 8.5714 | -4.4856 | -102.4715
2006-03-12 | 16:01 | 0 | 15.895 | 0 | 1 | 0 | 68.982 | 67.443 | 39.602 | 65.177 | 41.296 | 26.144 | 7.72 | 0 | 0 | 69.599 | 55.683 | 64.684 | 18.784 | 0 | 0 | 54.329 | 44.951 | [5 empty] | 0 | 3.805 | 1 | 4.3483 | 4.0581 | 1.9515 | 1.7143 | 2.3438 | 53.9015
2006-03-12 | 16:02 | 0 | 15.943 | 0 | 2 | 0 | 67.263 | 69.927 | 35.938 | 60.805 | 32.716 | 26.169 | 7.843 | 0 | 0 | 67.951 | 56.026 | 62.083 | 18.784 | 0 | 0 | 54.651 | 44.606 | [5 empty] | 0 | 6.458 | 2 | 4.3125 | 4.0241 | 1.95 | 1.7143 | 2.3098 | 53.5597
2006-03-12 | 16:03 | 0 | 15.895 | 0 | 0 | 0 | 65.873 | 69.158 | 34.62 | 49.743 | 27.976 | 26.296 | 7.628 | 0 | 0 | 66.619 | 56.35 | 59.041 | 18.816 | 0 | 0 | 54.933 | 44.099 | [5 empty] | 0 | 16.13 | 3 | 4.3751 | 4.0836 | 1.9526 | 1.7143 | 2.3693 | 54.1535
2006-03-12 | 16:04 | 0 | 15.918 | 0 | 0 | 0 | 65.177 | 68.653 | 34.01 | 47.908 | 23.928 | 26.218 | 7.342 | 0 | 0 | 65.535 | 56.455 | 56.791 | 18.759 | 0 | 0 | 55.064 | 43.551 | [5 empty] | 0 | 17.269 | 4 | 4.4584 | 4.1627 | 1.956 | 1.7143 | 2.4484 | 54.9175
2006-03-12 | 16:05 | 0 | 15.976 | 0 | 0 | 0 | 64.534 | 68.353 | 33.782 | 47.388 | 20.515 | 26.176 | 7.476 | 0 | 0 | 64.782 | 56.688 | 54.98 | 18.842 | 0 | 0 | 55.3 | 43.114 | [5 empty] | 0 | 17.146 | 5 | 4.4194 | 4.1256 | 1.9544 | 1.7143 | 2.4114 | 54.5631
2006-03-12 | 16:06 | 0 | 15.943 | 0 | 0 | 0 | 63.899 | 67.993 | 33.586 | 46.991 | 18.563 | 26.049 | 7.494 | 0 | 0 | 64.168 | 56.679 | 53.734 | 18.784 | 0 | 0 | 55.384 | 42.635 | [5 empty] | 0 | 16.908 | 6 | 4.4141 | 4.1207 | 1.9542 | 1.7143 | 2.4064 | 54.5151
2006-03-12 | 16:07 | 0 | 15.943 | 0 | 0 | 0 | 63.205 | 67.642 | 33.493 | 46.83 | 18.118 | 26.024 | 7.594 | 0 | 0 | 63.742 | 56.814 | 52.541 | 18.834 | 0 | 0 | 55.407 | 42.188 | [5 empty] | 0 | 16.375 | 7 | 4.385 | 4.093 | 1.953 | 1.7143 | 2.3787 | 54.2458
2006-03-12 | 16:08 | 0 | 15.976 | 0 | 0 | 0 | 62.585 | 67.247 | 33.407 | 46.333 | 16.815 | 26.105 | 7.02 | 0 | 0 | 63.413 | 56.912 | 51.722 | 18.842 | 0 | 0 | 55.552 | 41.75 | [5 empty] | 0 | 16.252 | 8 | 4.5522 | 4.2519 | 1.9597 | 1.7143 | 2.5376 | 55.7443
2006-03-12 | 16:09 | 0 | 16.001 | 0 | 0 | 0 | 61.957 | 66.822 | 33.359 | 46.013 | 15.852 | 26.056 | 7.476 | 0 | 0 | 63.1 | 56.935 | 51.057 | 18.816 | 0 | 0 | 55.645 | 41.42 | [5 empty] | 0 | 15.944 | 9 | 4.4194 | 4.1256 | 1.9544 | 1.7143 | 2.4114 | 54.5631
2006-03-12 | 16:10 | 0 | 15.928 | 0 | 0 | 0 | 61.307 | 66.419 | 33.287 | 45.647 | 15.506 | 25.84 | 7.527 | 1 | 0 | 62.808 | 56.978 | 50.667 | 18.816 | 0 | 0 | 55.666 | 41.092 | [5 empty] | 0 | 15.66 | 10 | 4.4045 | 4.1115 | 1.9538 | 1.7143 | 2.3972 | 54.4266
2006-03-12 | 16:11 | 0 | 15.769 | 0 | 0 | 0 | 60.647 | 65.916 | 33.256 | 45.341 | 15.795 | 25.664 | 7.494 | 0 | 0 | 62.605 | 56.978 | 50.256 | 18.816 | 0 | 0 | 55.736 | 40.81 | [5 empty] | 0 | 15.306 | 11 | 4.4141 | 4.1207 | 1.9542 | 1.7143 | 2.4064 | 54.5151
2006-03-12 | 16:12 | 0 | 15.697 | 0 | 0 | 0 | 60.02 | 65.446 | 33.118 | 44.972 | 15.302 | 25.735 | 7.393 | 0 | 0 | 62.329 | 57.039 | 50.065 | 18.784 | 0 | 0 | 55.729 | 40.425 | [5 empty] | 0 | 15.048 | 12 | 4.4436 | 4.1486 | 1.9553 | 1.7143 | 2.4343 | 54.7834
2006-03-12 | 16:13 | 0 | 15.722 | 0 | 0 | 0 | 59.415 | 64.953 | 33.046 | 44.676 | 14.389 | 25.615 | 7.519 | 0 | 0 | 62.151 | 57.039 | 49.834 | 18.784 | 0 | 0 | 55.774 | 40.143 | [5 empty] | 0 | 14.739 | 13 | 4.4069 | 4.1137 | 1.9539 | 1.7143 | 2.3995 | 54.4481
2006-03-12 | 16:14 | 0 | 15.78 | 0 | 0 | 0 | 58.772 | 64.579 | 33.077 | 44.24 | 13.781 | 25.573 | 7.45 | 0 | 0 | 62.023 | 57.069 | 49.729 | 18.816 | 0 | 0 | 55.804 | 39.87 | [5 empty] | 0 | 14.532 | 14 | 4.427 | 4.1328 | 1.9547 | 1.7143 | 2.4186 | 54.6324
2006-03-12 | 16:15 | 0 | 15.802 | 0 | 0 | 0 | 58.167 | 64.109 | 33.029 | 44.03 | 13.484 | 25.551 | 7.45 | 0 | 0 | 61.866 | 57.069 | 49.705 | 18.816 | 0 | 0 | 55.781 | 39.633 | [5 empty] | 0 | 14.137 | 15 | 4.427 | 4.1328 | 1.9547 | 1.7143 | 2.4186 | 54.6324
2006-03-12 | 16:16 | 0 | 15.802 | 0 | 0 | 0 | 57.516 | 63.682 | 32.819 | 43.7 | 14.646 | 25.431 | 7.45 | 0 | 0 | 61.777 | 57.113 | 49.544 | 18.867 | 0 | 0 | 55.804 | 39.375 | [5 empty] | 0 | 13.816 | 16 | 4.427 | 4.1328 | 1.9547 | 1.7143 | 2.4186 | 54.6324
2006-03-12 | 16:17 | 0 | 15.747 | 0 | 0 | 0 | 56.948 | 63.16 | 32.694 | 43.293 | 14.389 | 25.301 | 7.416 | 0 | 0 | 61.658 | 57.039 | 49.491 | 18.809 | 0 | 0 | 55.867 | 39.133 | [5 empty] | 0 | 13.655 | 17 | 4.4369 | 4.1423 | 1.9551 | 1.7143 | 2.428 | 54.7226
2006-03-12 | 16:18 | 0 | 15.78 | 0 | 2 | 0 | 60.791 | 60.768 | 32.63 | 39.141 | 13.952 | 25.431 | 7.197 | 0 | 0 | 61.597 | 57.069 | 49.453 | 18.816 | 0 | 0 | 55.897 | 38.976 | [5 empty] | 0 | 21.65 | 18 | 4.5006 | 4.2029 | 1.9577 | 1.7143 | 2.4886 | 55.2941
2006-03-12 | 16:19 | 0 | 15.764 | 0 | 0 | 0 | 60.529 | 59.406 | 33.72 | 35.246 | 13.716 | 25.269 | 7.234 | 0 | 0 | 61.514 | 57.142 | 49.414 | 18.877 | 0 | 0 | 55.575 | 38.741 | [5 empty] | 0 | 25.283 | 19 | 4.4899 | 4.1926 | 1.9572 | 1.7143 | 2.4783 | 55.1987
2006-03-12 | 16:20 | 0 | 15.754 | 0 | 0 | 0 | 59.915 | 58.817 | 34.065 | 34.416 | 12.496 | 25.311 | 6.948 | 0 | 0 | 61.439 | 57.046 | 49.292 | 18.769 | 0 | 0 | 55.713 | 38.555 | [5 empty] | 0 | 25.499 | 20 | 4.5731 | 4.2718 | 1.9606 | 1.7143 | 2.5575 | 55.9245
2006-03-12 | 16:21 | 0 | 15.812 | 0 | 0 | 0 | 59.363 | 58.532 | 33.955 | 34.33 | 11.493 | 25.247 | 7.056 | 0 | 0 | 61.403 | 57.076 | 49.346 | 18.827 | 0 | 0 | 55.904 | 38.421 | [5 empty] | 0 | 25.033 | 21 | 4.5417 | 4.2419 | 1.9593 | 1.7143 | 2.5276 | 55.6536
2006-03-12 | 16:22 | 0 | 15.78 | 0 | 0 | 0 | 58.66 | 58.19 | 33.782 | 34.041 | 10.374 | 25.215 | 6.87 | 0 | 0 | 61.327 | 57.09 | 49.316 | 18.794 | 0 | 0 | 55.965 | 38.177 | [5 empty] | 0 | 24.619 | 22 | 4.5959 | 4.2934 | 1.9615 | 1.7143 | 2.5791 | 56.1179
2006-03-12 | 16:23 | 0 | 15.805 | 0 | 0 | 0 | 58.055 | 57.852 | 33.617 | 34.017 | 10.892 | 25.117 | 7.2 | 0 | 0 | 61.261 | 57.09 | 49.407 | 18.819 | 0 | 0 | 56.012 | 38.014 | [5 empty] | 0 | 24.038 | 23 | 4.4998 | 4.202 | 1.9576 | 1.7143 | 2.4878 | 55.2864
2006-03-12 | 16:24 | 0 | 15.805 | 1 | 2 | 0 | 54.336 | 56.531 | 33.689 | 33.29 | 18.769 | 25.021 | 7.074 | 0 | 0 | 61.216 | 57.067 | 49.222 | 18.819 | 0 | 0 | 55.988 | 37.918 | [5 empty] | 0 | 21.046 | 24 | 4.5365 | 4.2369 | 1.9591 | 1.7143 | 2.5226 | 55.608
2006-03-12 | 16:25 | 0 | 15.78 | 0 | 2 | 0 | 54.91 | 56.709 | 33.266 | 33.173 | 22.66 | 25.046 | 6.948 | 0 | 0 | 61.149 | 57.113 | 49.155 | 18.844 | 0 | 0 | 55.965 | 37.708 | [5 empty] | 0 | 21.737 | 25 | 4.5731 | 4.2718 | 1.9606 | 1.7143 | 2.5575 | 55.9245
2006-03-12 | 16:26 | 0 | 15.78 | 0 | 2 | 0 | 54.084 | 55.69 | 31.693 | 33.5 | 24.322 | 25.021 | 6.87 | 0 | 0 | 61.035 | 57.067 | 49.131 | 18.844 | 0 | 0 | 55.918 | 37.591 | [5 empty] | 0 | 20.584 | 26 | 4.5959 | 4.2934 | 1.9615 | 1.7143 | 2.5791 | 56.1179
2006-03-12 | 16:27 | 0 | 15.754 | 0 | 2 | 0 | 53.741 | 54.726 | 30.658 | 32.032 | 25.84 | 24.901 | 6.971 | 0 | 0 | 60.923 | 57.067 | 49.108 | 18.819 | 0 | 0 | 55.895 | 37.473 | [5 empty] | 0 | 21.709 | 27 | 4.5664 | 4.2654 | 1.9603 | 1.7143 | 2.5511 | 55.8671
2006-03-12 | 16:28 | 1 | 15.805 | 0 | 3 | 0 | 53.19 | 54.268 | 29.911 | 30.707 | 26.875 | 24.926 | 6.896 | 0 | 0 | 60.901 | 57.09 | 48.993 | 18.867 | 0 | 0 | 55.918 | 37.332 | [5 empty] | 15.805 | 22.483 | 28 | 4.5883 | 4.2862 | 1.9612 | 1.7143 | 2.5719 | 56.0537
2006-03-12 | 16:29 | 0 | 15.754 | 0 | 2 | 0 | 52.639 | 53.764 | 29.624 | 29.911 | 28.057 | 24.828 | 6.922 | 0 | 0 | 60.789 | 57.09 | 48.993 | 18.819 | 0 | 0 | 55.874 | 37.215 | [5 empty] | 0 | 22.728 | 29 | 4.5807 | 4.279 | 1.9609 | 1.7143 | 2.5647 | 55.9892
2006-03-12 | 16:30 | 0 | 15.805 | 0 | 3 | 0 | 52.205 | 53.19 | 29.695 | 29.575 | 28.731 | 24.877 | 6.718 | 1 | 0 | 60.723 | 57.09 | 48.947 | 18.794 | 0 | 0 | 55.874 | 37.095 | [5 empty] | 0 | 22.63 | 30 | 4.6401 | 4.3355 | 1.9633 | 1.7143 | 2.6212 | 56.4893
2006-03-12 | 16:31 | 0 | 15.83 | 0 | 2 | 0 | 52.182 | 52.8 | 29.766 | 29.575 | 29.092 | 24.901 | 6.566 | 2 | 0 | 60.654 | 57.067 | 48.947 | 18.819 | 0 | 0 | 55.804 | 37.002 | [5 empty] | 0 | 22.607 | 31 | 4.6844 | 4.3775 | 1.9651 | 1.7143 | 2.6632 | 56.8537
2006-03-12 | 16:32 | 1 | 15.855 | 0 | 3 | 0 | 51.769 | 52.663 | 30.178 | 29.695 | 29.575 | 24.877 | 6.466 | 1 | 0 | 60.565 | 57.067 | 48.902 | 18.844 | 0 | 0 | 55.757 | 36.909 | [5 empty] | 15.855 | 22.074 | 32 | 4.7135 | 4.4052 | 1.9663 | 1.7143 | 2.6909 | 57.0897
2006-03-12 | 16:33 | 0 | 15.855 | 1 | 3 | 0 | 51.86 | 52.296 | 30.683 | 30.104 | 29.744 | 24.756 | 6.213 | 2 | 0 | 60.431 | 57.067 | 48.902 | 18.867 | 0 | 0 | 55.713 | 36.792 | [5 empty] | 0 | 21.756 | 33 | 4.7872 | 4.4752 | 1.9693 | 1.7143 | 2.761 | 57.674
2006-03-12 | 16:34 | 0 | 15.855 | 0 | 3 | 1 | 52.088 | 52.296 | 31.671 | 30.707 | 29.864 | 24.806 | 6.11 | 1 | 0 | 60.385 | 57.067 | 48.947 | 18.819 | 0 | 0 | 55.713 | 36.696 | [5 empty] | 0 | 21.381 | 34 | 4.8172 | 4.5038 | 1.9705 | 1.7143 | 2.7895 | 57.9068
2006-03-12 | 16:35 | 0 | 15.825 | 0 | 3 | 0 | 51.855 | 52.634 | 32.649 | 31.642 | 30.389 | 24.823 | 6.383 | 2 | 0 | 60.291 | 57.019 | 48.737 | 18.819 | 0 | 0 | 55.69 | 36.627 | [5 empty] | 0 | 20.213 | 0 | 4.7377 | 4.4282 | 1.9673 | 1.7143 | 2.7139 | 57.2834
2006-03-12 | 16:36 | 1 | 15.85 | 0 | 3 | 0 | 52.198 | 52.382 | 33.285 | 32.744 | 29.859 | 24.776 | 6.383 | 2 | 0 | 60.269 | 57.174 | 48.874 | 18.789 | 0 | 0 | 55.662 | 36.481 | [5 empty] | 15.85 | 19.454 | 1 | 4.7377 | 4.4282 | 4.8684 | 4.6154 | -0.1872 | -3.9513
2006-03-12 | 16:37 | 0 | 15.855 | 0 | 3 | 0 | 52.478 | 52.616 | 33.713 | 33.383 | 30.972 | 24.901 | 6.466 | 1 | 0 | 60.23 | 57.046 | 48.832 | 18.794 | 0 | 0 | 55.643 | 36.416 | [5 empty] | 0 | 19.095 | 2 | 4.7135 | 4.4052 | 4.8674 | 4.6154 | -0.21017 | -4.459
2006-03-12 | 16:38 | 0 | 15.85 | 0 | 3 | 0 | 52.772 | 52.842 | 33.847 | 33.637 | 31.063 | 24.918 | 6.335 | 2 | 0 | 60.157 | 56.996 | 48.781 | 18.739 | 0 | 0 | 55.594 | 36.316 | [5 empty] | 0 | 19.135 | 3 | 4.7516 | 4.4415 | 4.8689 | 4.6154 | -0.17391 | -3.66
2006-03-12 | 16:39 | 0 | 15.827 | 0 | 3 | 0 | 52.66 | 53.141 | 33.828 | 33.804 | 32.029 | 24.923 | 6.386 | 1 | 0 | 60.07 | 56.976 | 48.9 | 18.766 | 0 | 0 | 55.55 | 36.27 | [5 empty] | 0 | 18.856 | 4 | 4.7368 | 4.4274 | 4.8683 | 4.6154 | -0.18803 | -3.9695
2006-03-12 | 16:40 | 1 | 15.802 | 0 | 3 | 0 | 52.775 | 53.188 | 33.711 | 33.897 | 31.86 | 24.945 | 6.134 | 2 | 0 | 60.047 | 57.021 | 48.853 | 18.766 | 0 | 0 | 55.526 | 36.153 | [5 empty] | 15.802 | 18.878 | 5 | 4.8102 | 4.4971 | 4.8713 | 4.6154 | -0.11828 | -2.4589
2006-03-12 | 16:41 | 0 | 15.852 | 0 | 3 | 0 | 52.613 | 53.234 | 33.711 | 33.78 | 31.789 | 25.09 | 5.855 | 1 | 0 | 60.024 | 56.976 | 48.762 | 18.766 | 0 | 0 | 55.55 | 36.036 | [5 empty] | 0 | 18.833 | 6 | 4.8914 | 4.5743 | 4.8746 | 4.6154 | -0.041049 | -0.8392
2006-03-12 | 16:42 | 0 | 15.852 | 1 | 3 | 0 | 52.707 | 53.12 | 33.732 | 33.732 | 32.51 | 25.09 | 6.085 | 2 | 0 | 59.958 | 56.998 | 48.877 | 18.766 | 0 | 0 | 55.573 | 35.966 | [5 empty] | 0 | 18.975 | 7 | 4.8244 | 4.5107 | 4.8719 | 4.6154 | -0.10471 | -2.1705
2006-03-12 | 16:43 | 0 | 15.852 | 0 | 3 | 0 | 52.684 | 53.164 | 33.732 | 33.687 | 32.582 | 25.09 | 5.83 | 1 | 0 | 59.958 | 56.976 | 48.786 | 18.766 | 0 | 0 | 55.596 | 35.895 | [5 empty] | 0 | 18.997 | 8 | 4.8987 | 4.5813 | 4.8749 | 4.6154 | -0.034129 | -0.69669
2006-03-12 | 16:44 | 1 | 15.852 | 0 | 3 | 0 | 52.751 | 53.188 | 33.756 | 33.828 | 32.223 | 25.114 | 5.629 | 2 | 0 | 59.913 | 56.953 | 48.807 | 18.791 | 0 | 0 | 55.55 | 35.801 | [5 empty] | 15.852 | 18.923 | 9 | 4.9572 | 4.6369 | 4.8773 | 4.6154 | 0.021508 | 0.43387
2006-03-12 | 16:45 | 0 | 15.875 | 0 | 4 | 0 | 52.798 | 53.234 | 33.849 | 33.897 | 32.078 | 25.139 | 5.804 | 1 | 0 | 59.867 | 56.907 | 48.877 | 18.791 | 0 | 0 | 55.526 | 35.753 | [5 empty] | 0 | 18.901 | 10 | 4.9063 | 4.5885 | 4.8752 | 4.6154 | -0.026932 | -0.54893
2006-03-12 | 16:46 | 0 | 15.852 | 0 | 3 | 0 | 52.684 | 53.255 | 34.038 | 33.969 | 32.029 | 25.188 | 5.933 | 2 | 0 | 59.846 | 56.93 | 48.786 | 18.816 | 0 | 0 | 55.503 | 35.684 | [5 empty] | 0 | 18.715 | 11 | 4.8687 | 4.5527 | 4.8737 | 4.6154 | -0.062639 | -1.2866
2006-03-12 | 16:47 | 1 | 15.9 | 0 | 3 | 1 | 52.592 | 53.188 | 34.251 | 34.086 | 32.39 | 25.235 | 6.059 | 1 | 0 | 59.867 | 56.93 | 48.923 | 18.791 | 0 | 0 | 55.55 | 35.612 | [5 empty] | 15.9 | 18.506 | 12 | 4.832 | 4.5179 | 4.8722 | 4.6154 | -0.097516 | -2.0181
2006-03-12 | 16:48 | 0 | 15.875 | 0 | 3 | 0 | 52.775 | 53.12 | 34.579 | 34.345 | 32.414 | 25.355 | 5.933 | 2 | 0 | 59.867 | 56.93 | 48.853 | 18.766 | 0 | 0 | 55.459 | 35.543 | [5 empty] | 0 | 18.43 | 0 | 4.8687 | 4.5527 | 4.8737 | 4.6154 | -0.062639 | -1.2866
2006-03-12 | 16:49 | 0 | 15.845 | 0 | 3 | 0 | 52.793 | 53.251 | 34.691 | 34.668 | 32.718 | 25.35 | 5.369 | 1 | 0 | 59.75 | 56.925 | 48.849 | 18.761 | 0 | 0 | 55.384 | 35.443 | [5 empty] | 0 | 18.125 | 1 | 5.0329 | 4.7089 | 4.2649 | 4 | 0.70886 | 14.0844
2006-03-12 | 16:50 | 0 | 15.822 | 0 | 3 | 0 | 52.908 | 53.251 | 35.043 | 35.043 | 32.193 | 25.448 | 5.394 | 1 | 0 | 59.728 | 56.88 | 48.802 | 18.711 | 0 | 0 | 55.431 | 35.443 | [5 empty] | 0 | 17.865 | 2 | 5.0257 | 4.7019 | 4.2647 | 4 | 0.70194 | 13.9671
2006-03-12 | 16:51 | 1 | 15.87 | 0 | 3 | 0 | 52.793 | 53.365 | 35.256 | 35.301 | 32.095 | 25.448 | 5.472 | 2 | 0 | 59.705 | 56.88 | 48.825 | 18.761 | 0 | 0 | 55.452 | 35.373 | [5 empty] | 15.87 | 17.492 | 3 | 5.003 | 4.6804 | 4.2637 | 4 | 0.68035 | 13.599
2006-03-12 | 16:52 | 0 | 15.925 | 1 | 3 | 0 | 52.866 | 53.325 | 35.591 | 35.426 | 31.259 | 25.598 | 5.247 | 1 | 0 | 59.755 | 56.887 | 48.83 | 18.741 | 0 | 0 | 55.48 | 35.378 | [5 empty] | 0 | 17.44 | 4 | 5.0685 | 4.7426 | 4.2664 | 4 | 0.74263 | 14.652
2006-03-12 | 16:53 | 0 | 15.9 | 0 | 3 | 0 | 53.05 | 53.325 | 35.849 | 35.825 | 31.379 | 25.598 | 5.325 | 2 | 0 | 59.755 | 56.864 | 48.853 | 18.766 | 0 | 0 | 55.412 | 35.33 | [5 empty] | 0 | 17.225 | 5 | 5.0458 | 4.721 | 4.2655 | 4 | 0.72104 | 14.29
2006-03-12 | 16:54 | 0 | 15.895 | 0 | 3 | 0 | 53.412 | 53.412 | 36.055 | 35.962 | 30.747 | 25.713 | 5.294 | 1 | 0 | 59.705 | 56.88 | 48.895 | 18.711 | 0 | 0 | 55.361 | 35.256 | [5 empty] | 0 | 17.45 | 6 | 5.0548 | 4.7296 | 4.2658 | 4 | 0.72962 | 14.4343
2006-03-12 | 16:55 | 0 | 15.951 | 0 | 4 | 0 | 53.416 | 53.806 | 36.27 | 36.177 | 30.342 | 25.693 | 5.526 | 1 | 0 | 59.732 | 56.907 | 48.923 | 18.791 | 0 | 0 | 55.365 | 35.213 | [5 empty] | 0 | 17.239 | 7 | 4.9872 | 4.6654 | 4.2631 | 4 | 0.6654 | 13.3421
2006-03-12 | 16:56 | 1 | 15.9 | 0 | 3 | 0 | 53.554 | 53.806 | 36.411 | 36.318 | 30.56 | 25.789 | 5.551 | 2 | 0 | 59.732 | 56.864 | 48.923 | 18.741 | 0 | 0 | 55.365 | 35.144 | [5 empty] | 15.9 | 17.236 | 8 | 4.9799 | 4.6585 | 4.2628 | 4 | 0.65848 | 13.2227
2006-03-12 | 16:57 | 0 | 15.925 | 0 | 2 | 0 | 53.554 | 53.921 | 36.552 | 36.459 | 30.487 | 25.764 | 5.526 | 1 | 0 | 59.666 | 56.864 | 48.9 | 18.791 | 0 | 0 | 55.365 | 35.12 | [5 empty] | 0 | 17.095 | 9 | 4.9872 | 4.6654 | 4.2631 | 4 | 0.6654 | 13.3421
2006-03-12 | 16:58 | 0 | 15.9 | 0 | 3 | 0 | 53.463 | 53.921 | 36.648 | 36.694 | 30.028 | 25.789 | 5.222 | 1 | 0 | 59.689 | 56.887 | 48.923 | 18.766 | 0 | 0 | 55.344 | 35.05 | [5 empty] | 0 | 16.769 | 10 | 5.0758 | 4.7496 | 4.2667 | 4 | 0.74955 | 14.7673
2006-03-12 | 16:59 | 0 | 15.845 | 0 | 3 | 0 | 53.617 | 53.801 | 36.713 | 36.689 | 29.952 | 25.784 | 5.369 | 1 | 0 | 59.661 | 56.814 | 48.895 | 18.766 | 0 | 0 | 55.365 | 34.978 | [5 empty] | 0 | 16.928 | 11 | 5.0329 | 4.7089 | 4.2649 | 4 | 0.70886 | 14.0844
2006-03-12 | 17:00 | 1 | 15.87 | 0 | 3 | 0 | 53.503 | 54.009 | 36.923 | 36.782 | 29.952 | 25.759 | 5.369 | 2 | 0 | 59.639 | 56.836 | 48.895 | 18.711 | 0 | 0 | 55.337 | 34.926 | [5 empty] | 15.87 | 16.721 | 12 | 5.0329 | 4.7089 | 4.2649 | 4 | 0.70886 | 14.0844
2006-03-12 | 17:01 | 0 | 15.925 | 1 | 3 | 0 | 53.531 | 53.967 | 37.048 | 37 | 29.812 | 25.838 | 5.021 | 1 | 0 | 59.666 | 56.864 | 48.991 | 18.766 | 0 | 0 | 55.344 | 34.909 | [5 empty] | 0 | 16.531 | 13 | 5.1343 | 4.8052 | 4.2691 | 4 | 0.80519 | 15.6826
2006-03-12 | 17:02 | 0 | 15.925 | 0 | 3 | 1 | 53.715 | 53.921 | 37.141 | 37.117 | 29.692 | 25.909 | 5.173 | 1 | 0 | 59.666 | 56.864 | 48.9 | 18.766 | 0 | 0 | 55.298 | 34.861 | [5 empty] | 0 | 16.598 | 14 | 5.09 | 4.7631 | 4.2673 | 4 | 0.76311 | 14.9923
2006-03-12 | 17:03 | 0 | 15.895 | 0 | 3 | 0 | 53.939 | 54.03 | 37.277 | 37.301 | 29.589 | 25.784 | 5.142 | 1 | 0 | 59.639 | 56.791 | 49.01 | 18.736 | 0 | 0 | 55.316 | 34.88 | [5 empty] | 0 | 16.638 | 0 | 5.099 | 4.7717 | 4.2676 | 4 | 0.77169 | 15.1341
2006-03-12 | 17:04 | 0 | 15.925 | 0 | 2 | 0 | 54.128 | 54.289 | 37.471 | 37.351 | 29.908 | 25.982 | 5.199 | 1 | 0 | 59.666 | 56.864 | 48.968 | 18.741 | 0 | 0 | 55.298 | 34.79 | [5 empty] | 0 | 16.777 | 1 | 5.0825 | 4.7559 | 3.7964 | 3.5294 | 1.2265 | 24.1322
2006-03-12 | 17:05 | 1 | 15.925 | 0 | 3 | 0 | 54.152 | 54.518 | 37.634 | 37.423 | 29.812 | 25.789 | 5.374 | 2 | 0 | 59.643 | 56.818 | 48.923 | 18.741 | 0 | 0 | 55.298 | 34.768 | [5 empty] | 15.925 | 16.729 | 2 | 5.0315 | 4.7075 | 3.7943 | 3.5294 | 1.1781 | 23.4138
2006-03-12 | 17:06 | 0 | 15.895 | 0 | 3 | 0 | 54.329 | 54.534 | 37.653 | 37.677 | 30.023 | 25.808 | 5.168 | 1 | 0 | 59.616 | 56.836 | 49.031 | 18.736 | 0 | 0 | 55.27 | 34.715 | [5 empty] | 0 | 16.652 | 3 | 5.0915 | 4.7645 | 3.7967 | 3.5294 | 1.2351 | 24.2579
2006-03-12 | 17:07 | 0 | 15.87 | 0 | 3 | 0 | 54.42 | 54.581 | 37.842 | 37.887 | 29.928 | 25.784 | 5.217 | 1 | 0 | 59.57 | 56.768 | 48.963 | 18.711 | 0 | 0 | 55.27 | 34.691 | [5 empty] | 0 | 16.533 | 4 | 5.0772 | 4.7509 | 3.7962 | 3.5294 | 1.2215 | 24.0589
2006-03-12 | 17:08 | 0 | 15.87 | 0 | 2 | 0 | 54.513 | 54.789 | 38.004 | 37.983 | 29.903 | 25.879 | 5.217 | 1 | 0 | 59.616 | 56.768 | 48.963 | 18.711 | 0 | 0 | 55.246 | 34.668 | [5 empty] | 0 | 16.53 | 5 | 5.0772 | 4.7509 | 3.7962 | 3.5294 | 1.2215 | 24.0589
2006-03-12 | 17:09 | 1 | 15.845 | 0 | 3 | 0 | 55.085 | 54.765 | 38.193 | 38.145 | 30.362 | 25.904 | 5.242 | 1 | 0 | 59.57 | 56.768 | 48.986 | 18.711 | 0 | 0 | 55.179 | 34.644 | [5 empty] | 15.845 | 16.94 | 6 | 5.0699 | 4.744 | 3.7959 | 3.5294 | 1.2146 | 23.957
2006-03-12 | 17:10 | 0 | 15.87 | 1 | 3 | 0 | 55.589 | 55.337 | 38.169 | 38.287 | 30.771 | 25.879 | 5.142 | 2 | 0 | 59.616 | 56.791 | 49.01 | 18.711 | 0 | 0 | 55.223 | 34.668 | [5 empty] | 0 | 17.302 | 7 | 5.099 | 4.7717 | 3.797 | 3.5294 | 1.2423 | 24.363
2006-03-12 | 17:11 | 0 | 15.895 | 0 | 2 | 0 | 55.774 | 55.727 | 38.217 | 38.476 | 31.061 | 25.904 | 5.065 | 1 | 0 | 59.57 | 56.859 | 49.148 | 18.711 | 0 | 0 | 55.223 | 34.598 | [5 empty] | 0 | 17.298 | 8 | 5.1215 | 4.793 | 3.7979 | 3.5294 | 1.2636 | 24.6725
2006-03-12 | 17:12 | 0 | 15.87 | 0 | 3 | 0 | 56.096 | 56.002 | 38.358 | 38.662 | 31.541 | 25.879 | 5.041 | 1 | 0 | 59.55 | 56.791 | 49.01 | 18.736 | 0 | 0 | 55.155 | 34.526 | [5 empty] | 0 | 17.434 | 9 | 5.1285 | 4.7997 | 3.7982 | 3.5294 | 1.2702 | 24.7684
2006-03-12 | 17:13 | 0 | 15.87 | 0 | 2 | 0 | 56.252 | 56.343 | 38.428 | 38.782 | 31.541 | 25.857 | 5.09 | 1 | 0 | 59.57 | 56.747 | 49.054 | 18.711 | 0 | 0 | 55.179 | 34.502 | [5 empty] | 0 | 17.47 | 10 | 5.1142 | 4.7861 | 3.7976 | 3.5294 | 1.2567 | 24.5723
2006-03-12 | 17:14 | 1 | 15.87 | 0 | 3 | 0 | 56.186 | 56.521 | 38.569 | 38.782 | 31.374 | 25.808 | 5.065 | 1 | 0 | 59.57 | 56.768 | 48.986 | 18.711 | 0 | 0 | 55.155 | 34.481 | [5 empty] | 15.87 | 17.404 | 11 | 5.1215 | 4.793 | 3.7979 | 3.5294 | 1.2636 | 24.6725
2006-03-12 | 17:15 | 0 | 15.895 | 0 | 3 | 0 | 56.298 | 56.544 | 38.569 | 38.851 | 31.396 | 25.904 | 5.217 | 1 | 0 | 59.639 | 56.836 | 49.077 | 18.736 | 0 | 0 | 55.2 | 34.481 | [5 empty] | 0 | 17.447 | 12 | 5.0772 | 4.7509 | 3.7962 | 3.5294 | 1.2215 | 24.0589
2006-03-12 | 17:16 | 0 | 15.87 | 0 | 2 | 0 | 56.521 | 56.613 | 38.734 | 39.086 | 31.517 | 25.929 | 5.217 | 1 | 0 | 59.593 | 56.791 | 49.148 | 18.786 | 0 | 0 | 55.109 | 34.481 | [5 empty] | 0 | 17.435 | 13 | 5.0772 | 4.7509 | 3.7962 | 3.5294 | 1.2215 | 24.0589
2006-03-12 | 17:17 | 0 | 15.863 | 0 | 3 | 0 | 56.672 | 56.718 | 38.703 | 38.985 | 31.485 | 25.992 | 4.982 | 2 | 0 | 59.563 | 56.761 | 49.024 | 18.728 | 0 | 0 | 55.102 | 34.402 | [5 empty] | 0 | 17.687 | 14 | 5.1456 | 4.816 | 3.7989 | 3.5294 | 1.2866 | 25.0031
2006-03-12 | 17:18 | 0 | 15.895 | 0 | 2 | 0 | 56.994 | 56.925 | 38.734 | 39.086 | 31.615 | 25.953 | 5.016 | 1 | 0 | 59.57 | 56.768 | 49.077 | 18.786 | 0 | 0 | 55.109 | 34.409 | [5 empty] | 0 | 17.908 | 15 | 5.1357 | 4.8066 | 3.7985 | 3.5294 | 1.2772 | 24.8681
2006-03-12 | 17:19 | 1 | 15.888 | 0 | 3 | 1 | 57.039 | 57.243 | 38.808 | 39.042 | 31.691 | 25.933 | 5.121 | 1 | 0 | 59.618 | 56.793 | 49.056 | 18.764 | 0 | 0 | 55.043 | 34.39 | [5 empty] | 15.888 | 17.997 | 16 | 5.1052 | 4.7775 | 3.7973 | 3.5294 | 1.2481 | 24.4477
2006-03-12 | 17:20 | 0 | 15.87 | 1 | 2 | 0 | 56.989 | 57.281 | 38.873 | 39.155 | 31.708 | 26.12 | 4.99 | 1 | 0 | 59.591 | 56.788 | 49.028 | 18.734 | 0 | 0 | 55.015 | 34.337 | [5 empty] | 0 | 17.834 | 0 | 5.1433 | 4.8138 | 3.7988 | 3.5294 | 1.2844 | 24.9714
2006-03-12 | 17:21 | 0 | 15.87 | 0 | 3 | 0 | 57.012 | 57.281 | 38.92 | 39.203 | 31.541 | 25.926 | 5.116 | 1 | 0 | 59.522 | 56.72 | 49.075 | 18.711 | 0 | 0 | 54.968 | 34.361 | [5 empty] | 0 | 17.809 | 1 | 5.1066 | 4.7789 | 3.7973 | 3.5294 | 1.2495 | 24.4678
2006-03-12 | 17:22 | 0 | 15.845 | 0 | 3 | 0 | 57.081 | 57.37 | 39.107 | 39.272 | 31.517 | 26 | 5.09 | 1 | 0 | 59.545 | 56.72 | 49.098 | 18.711 | 0 | 0 | 54.968 | 34.314 | [5 empty] | 0 | 17.809 | 2 | 5.1142 | 4.7861 | 3.7976 | 3.5294 | 1.2567 | 24.5723
2006-03-12 | 17:23 | 0 | 15.878 | 0 | 2 | 0 | 57.131 | 57.379 | 39.162 | 39.514 | 31.693 | 26.032 | 5.072 | 2 | 0 | 59.552 | 56.706 | 49.129 | 18.718 | 0 | 0 | 54.952 | 34.321 | [5 empty] | 0 | 17.617 | 3 | 5.1194 | 4.7911 | 3.7979 | 3.5294 | 1.2617 | 24.6445
2006-03-12 | 17:24 | 1 | 15.845 | 0 | 3 | 0 | 57.124 | 57.439 | 39.083 | 39.578 | 31.853 | 26.071 | 4.964 | 1 | 0 | 59.522 | 56.72 | 49.052 | 18.711 | 0 | 0 | 54.922 | 34.314 | [5 empty] | 15.845 | 17.546 | 4 | 5.1509 | 4.821 | 3.7991 | 3.5294 | 1.2916 | 25.0744
2006-03-12 | 17:25 | 0 | 15.903 | 0 | 2 | 0 | 57.154 | 57.423 | 39.186 | 39.609 | 31.74 | 26.056 | 4.998 | 1 | 0 | 59.575 | 56.729 | 49.129 | 18.766 | 0 | 0 | 54.999 | 34.345 | [5 empty] | 0 | 17.545 | 5 | 5.141 | 4.8116 | 3.7987 | 3.5294 | 1.2821 | 24.9396
2006-03-12 | 17:26 | 0 | 15.87 | 0 | 3 | 0 | 57.058 | 57.393 | 39.179 | 39.507 | 31.683 | 26.169 | 4.964 | 1 | 0 | 59.614 | 56.743 | 49.052 | 18.734 | 0 | 0 | 55.06 | 34.29 | [5 empty] | 0 | 17.551 | 6 | 5.1509 | 4.821 | 3.7991 | 3.5294 | 1.2916 | 25.0744
2006-03-12 | 17:27 | 0 | 15.87 | 0 | 2 | 0 | 57.081 | 57.439 | 39.248 | 39.483 | 31.853 | 26.071 | 4.913 | 1 | 0 | 59.545 | 56.699 | 49.098 | 18.711 | 0 | 0 | 55.036 | 34.266 | [5 empty] | 0 | 17.598 | 7 | 5.1657 | 4.8351 | 3.7997 | 3.5294 | 1.3057 | 25.2756
2006-03-12 | 17:28 | 0 | 15.87 | 0 | 3 | 0 | 56.946 | 57.393 | 39.272 | 39.672 | 31.902 | 26.12 | 4.887 | 1 | 0 | 59.522 | 56.677 | 49.122 | 18.686 | 0 | 0 | 54.992 | 34.244 | [5 empty] | 0 | 17.274 | 8 | 5.1733 | 4.8423 | 3.8 | 3.5294 | 1.3129 | 25.3777
2006-03-12 | 17:29 | 1 | 15.87 | 1 | 3 | 0 | 56.989 | 57.281 | 39.389 | 39.602 | 32.142 | 26.191 | 4.712 | 1 | 0 | 59.568 | 56.677 | 49.075 | 18.635 | 0 | 0 | 54.922 | 34.196 | [5 empty] | 15.87 | 17.387 | 9 | 5.2243 | 4.8907 | 3.8021 | 3.5294 | 1.3613 | 26.0574
2006-03-12 | 17:30 | 0 | 15.87 | 0 | 2 | 0 | 56.946 | 57.281 | 39.224 | 39.672 | 31.951 | 26.215 | 4.786 | 1 | 0 | 59.522 | 56.677 | 48.984 | 18.711 | 0 | 0 | 54.877 | 34.125 | [5 empty] | 0 | 17.274 | 10 | 5.2027 | 4.8702 | 3.8012 | 3.5294 | 1.3408 | 25.7716
2006-03-12 | 17:31 | 0 | 15.845 | 0 | 3 | 0 | 56.946 | 57.304 | 39.155 | 39.53 | 31.683 | 26.12 | 4.534 | 2 | 0 | 59.522 | 56.677 | 49.007 | 18.711 | 0 | 0 | 54.877 | 34.125 | [5 empty] | 0 | 17.416 | 11 | 5.2761 | 4.94 | 3.8042 | 3.5294 | 1.4106 | 26.7352
2006-03-12 | 17:32 | 0 | 15.815 | 0 | 3 | 0 | 56.827 | 57.277 | 39.126 | 39.432 | 32.088 | 26.066 | 4.325 | 1 | 0 | 59.495 | 56.626 | 49.024 | 18.656 | 0 | 0 | 54.849 | 34.12 | [5 empty] | 0 | 17.395 | 12 | 5.337 | 4.9978 | 3.8067 | 3.5294 | 1.4684 | 27.5143
2006-03-12 | 17:33 | 1 | 15.87 | 0 | 2 | 0 | 56.677 | 57.281 | 39.107 | 39.507 | 32.311 | 26.12 | 4.686 | 1 | 0 | 59.545 | 56.699 | 49.052 | 18.686 | 0 | 0 | 54.877 | 34.125 | [5 empty] | 15.87 | 17.17 | 13 | 5.2318 | 4.8979 | 3.8024 | 3.5294 | 1.3685 | 26.1572
2006-03-12 | 17:34 | 0 | 15.87 | 0 | 3 | 0 | 56.496 | 57.058 | 39.107 | 39.461 | 32.093 | 26.191 | 4.761 | 1 | 0 | 59.522 | 56.631 | 49.075 | 18.661 | 0 | 0 | 54.854 | 34.125 | [5 empty] | 0 | 17.035 | 14 | 5.21 | 4.8772 | 3.8015 | 3.5294 | 1.3477 | 25.8684
2006-03-12 | 17:35 | 0 | 15.87 | 0 | 3 | 0 | 56.43 | 56.9 | 38.966 | 39.413 | 32.022 | 26.095 | 4.686 | 1 | 0 | 59.502 | 56.631 | 49.075 | 18.711 | 0 | 0 | 54.784 | 34.148 | [5 empty] | 0 | 17.017 | 15 | 5.2318 | 4.8979 | 3.8024 | 3.5294 | 1.3685 | 26.1572
2006-03-12 | 17:36 | 0 | 15.815 | 0 | 3 | 1 | 56.334 | 56.693 | 38.844 | 39.385 | 32.162 | 26.139 | 4.755 | 1 | 0 | 59.474 | 56.649 | 49.047 | 18.681 | 0 | 0 | 54.779 | 34.12 | [5 empty] | 0 | 16.949 | 16 | 5.2117 | 4.8788 | 3.8016 | 3.5294 | 1.3494 | 25.8916
2006-03-12 | 17:37 | 0 | 15.845 | 0 | 2 | 0 | 56.184 | 56.699 | 38.873 | 39.272 | 32.166 | 26.169 | 4.812 | 1 | 0 | 59.456 | 56.631 | 49.075 | 18.686 | 0 | 0 | 54.761 | 34.103 | [5 empty] | 0 | 16.912 | 0 | 5.1951 | 4.863 | 3.8009 | 3.5294 | 1.3336 | 25.6706
2006-03-12 | 17:38 | 1 | 15.895 | 1 | 3 | 0 | 56.161 | 56.585 | 38.779 | 39.155 | 32.166 | 26.36 | 4.812 | 2 | 0 | 59.479 | 56.699 | 49.236 | 18.784 | 0 | 0 | 54.74 | 34.079 | [5 empty] | 15.895 | 17.006 | 1 | 5.1951 | 4.863 | 3.8009 | 3.5294 | 1.3336 | 25.6706
2006-03-12 | 17:39 | 0 | 15.87 | 0 | 3 | 0 | 55.953 | 56.496 | 38.71 | 39.157 | 32.071 | 26.193 | 4.609 | 1 | 0 | 59.504 | 56.636 | 49.171 | 18.661 | 0 | 0 | 54.765 | 34.127 | [5 empty] | 0 | 16.796 | 2 | 5.2543 | 4.9192 | 3.8033 | 3.5294 | 1.3898 | 26.4512
2006-03-12 | 17:40 | 0 | 15.908 | 0 | 3 | 0 | 55.879 | 56.401 | 38.77 | 39.076 | 32.061 | 26.23 | 4.521 | 1 | 0 | 59.515 | 56.601 | 49.068 | 18.648 | 0 | 0 | 54.754 | 34.163 | [5 empty] | 0 | 16.803 | 3 | 5.2799 | 4.9436 | 3.8044 | 3.5294 | 1.4142 | 26.7842
2006-03-12 | 17:41 | 0 | 15.857 | 0 | 2 | 0 | 55.718 | 56.266 | 38.581 | 39.098 | 31.963 | 26.132 | 4.647 | 1 | 0 | 59.495 | 56.624 | 49.068 | 18.698 | 0 | 0 | 54.709 | 34.093 | [5 empty] | 0 | 16.62 | 4 | 5.2432 | 4.9087 | 3.8029 | 3.5294 | 1.3793 | 26.3065
2006-03-12 | 17:42 | 0 | 15.913 | 0 | 3 | 0 | 55.699 | 56.293 | 38.633 | 38.964 | 31.897 | 26.211 | 4.475 | 1 | 0 | 59.477 | 56.629 | 49.117 | 18.728 | 0 | 0 | 54.737 | 34.098 | [5 empty] | 0 | 16.735 | 5 | 5.2933 | 4.9563 | 3.8049 | 3.5294 | 1.4269 | 26.957
2006-03-12 | 17:43 | 1 | 15.913 | 0 | 3 | 0 | 55.907 | 56.112 | 38.564 | 38.916 | 31.946 | 26.26 | 4.5 | 1 | 0 | 59.543 | 56.629 | 49.302 | 18.728 | 0 | 0 | 54.737 | 34.074 | [5 empty] | 15.913 | 16.991 | 6 | 5.286 | 4.9494 | 3.8046 | 3.5294 | 1.42 | 26.8632
2006-03-12 | 17:44 | 0 | 15.883 | 0 | 3 | 0 | 55.466 | 56.266 | 38.44 | 38.863 | 31.674 | 26.11 | 4.318 | 2 | 0 | 59.472 | 56.624 | 49.159 | 18.698 | 0 | 0 | 54.709 | 34.046 | [5 empty] | 0 | 16.603 | 7 | 5.339 | 4.9998 | 3.8068 | 3.5294 | 1.4704 | 27.5401
2006-03-12 | 17:45 | 0 | 15.888 | 0 | 3 | 0 | 55.242 | 55.907 | 38.492 | 38.822 | 31.414 | 26.139 | 4.374 | 1 | 0 | 59.477 | 56.606 | 49.164 | 18.678 | 0 | 0 | 54.644 | 34.074 | [5 empty] | 0 | 16.42 | 8 | 5.3227 | 4.9843 | 3.8061 | 3.5294 | 1.4549 | 27.3333
2006-03-12 | 17:46 | 0 | 15.938 | 0 | 3 | 0 | 55.172 | 55.655 | 38.564 | 38.892 | 31.487 | 26.211 | 4.652 | 1 | 0 | 59.477 | 56.674 | 49.14 | 18.827 | 0 | 0 | 54.644 | 34.098 | [5 empty] | 0 | 16.28 | 9 | 5.2417 | 4.9073 | 3.8028 | 3.5294 | 1.3779 | 26.2874
2006-03-12 | 17:47 | 0 | 15.913 | 0 | 2 | 0 | 55.057 | 55.585 | 38.564 | 38.822 | 31.198 | 26.139 | 4.449 | 1 | 0 | 59.454 | 56.606 | 49.096 | 18.703 | 0 | 0 | 54.623 | 34.074 | [5 empty] | 0 | 16.235 | 10 | 5.3009 | 4.9635 | 3.8052 | 3.5294 | 1.4341 | 27.0542
2006-03-12 | 17:48 | 1 | 15.883 | 1 | 3 | 0 | 55.006 | 55.466 | 38.464 | 38.887 | 31.024 | 26.061 | 4.24 | 1 | 0 | 59.426 | 56.558 | 49.136 | 18.698 | 0 | 0 | 54.572 | 34.046 | [5 empty] | 15.883 | 16.119 | 11 | 5.3617 | 5.0214 | 3.8077 | 3.5294 | 1.492 | 27.8261
2006-03-12 | 17:49 | 0 | 15.908 | 0 | 3 | 0 | 54.985 | 55.375 | 38.464 | 38.794 | 30.904 | 26.11 | 4.444 | 1 | 0 | 59.426 | 56.558 | 49.045 | 18.623 | 0 | 0 | 54.639 | 34.022 | [5 empty] | 0 | 16.191 | 12 | 5.3023 | 4.9649 | 3.8053 | 3.5294 | 1.4355 | 27.0729
2006-03-12 | 17:50 | 0 | 15.908 | 0 | 3 | 0 | 55.006 | 55.419 | 38.488 | 38.839 | 30.975 | 26.085 | 4.596 | 2 | 0 | 59.404 | 56.558 | 49.021 | 18.648 | 0 | 0 | 54.663 | 34.022 | [5 empty] | 0 | 16.167 | 13 | 5.258 | 4.9228 | 3.8035 | 3.5294 | 1.3934 | 26.5006
2006-03-12 | 17:51 | 0 | 15.883 | 0 | 3 | 0 | 55.053 | 55.396 | 38.535 | 38.98 | 31.747 | 25.941 | 4.544 | 1 | 0 | 59.404 | 56.535 | 49.112 | 18.648 | 0 | 0 | 54.572 | 33.998 | [5 empty] | 0 | 16.073 | 14 | 5.2732 | 4.9372 | 3.8041 | 3.5294 | 1.4078 | 26.6975
2006-03-12 | 17:52 | 1 | 15.857 | 0 | 3 | 0 | 54.961 | 55.466 | 38.557 | 38.911 | 31.794 | 26.085 | 4.495 | 1 | 0 | 59.404 | 56.535 | 49.089 | 18.673 | 0 | 0 | 54.572 | 33.974 | [5 empty] | 15.857 | 16.05 | 15 | 5.2875 | 4.9508 | 3.8047 | 3.5294 | 1.4214 | 26.882
2006-03-12 | 17:53 | 0 | 15.913 | 0 | 3 | 1 | 55.148 | 55.403 | 38.586 | 39.057 | 32.017 | 26.066 | 4.678 | 1 | 0 | 59.431 | 56.54 | 49.073 | 18.653 | 0 | 0 | 54.623 | 34.003 | [5 empty] | 0 | 16.091 | 16 | 5.2342 | 4.9001 | 3.8025 | 3.5294 | 1.3707 | 26.1879
2006-03-12 | 17:54 | 0 | 15.857 | 0 | 3 | 0 | 55.076 | 55.512 | 38.557 | 38.935 | 32.061 | 26.157 | 4.57 | 1 | 0 | 59.383 | 56.535 | 49.068 | 18.673 | 0 | 0 | 54.595 | 33.974 | [5 empty] | 0 | 16.141 | 0 | 5.2656 | 4.93 | 3.8038 | 3.5294 | 1.4006 | 26.5992
2006-03-12 | 17:55 | 0 | 15.883 | 0 | 3 | 0 | 55.053 | 55.466 | 38.557 | 39.028 | 32.061 | 26.061 | 4.621 | 2 | 0 | 59.383 | 56.49 | 49.136 | 18.673 | 0 | 0 | 54.525 | 33.952 | [5 empty] | 0 | 16.025 | 1 | 5.2508 | 4.9159 | 3.8032 | 3.5294 | 1.3865 | 26.4056
2006-03-12 | 17:56 | 0 | 15.883 | 0 | 3 | 0 | 54.847 | 55.489 | 38.653 | 38.863 | 32.083 | 26.085 | 4.444 | 1 | 0 | 59.404 | 56.512 | 48.975 | 18.623 | 0 | 0 | 54.525 | 33.904 | [5 empty] | 0 | 15.984 | 2 | 5.3023 | 4.9649 | 3.8053 | 3.5294 | 1.4355 | 27.0729
2006-03-12 | 17:57 | 1 | 15.883 | 1 | 3 | 0 | 54.709 | 55.258 | 38.605 | 38.98 | 32.083 | 26.11 | 4.392 | 1 | 0 | 59.404 | 56.535 | 49.136 | 18.673 | 0 | 0 | 54.525 | 33.904 | [5 empty] | 15.883 | 15.729 | 3 | 5.3174 | 4.9793 | 3.8059 | 3.5294 | 1.4499 | 27.2665
2006-03-12 | 17:58 | 0 | 15.908 | 0 | 3 | 0 | 54.616 | 55.099 | 38.653 | 38.887 | 31.674 | 26.23 | 4.47 | 1 | 0 | 59.404 | 56.512 | 48.951 | 18.698 | 0 | 0 | 54.525 | 33.904 | [5 empty] | 0 | 15.729 | 4 | 5.2947 | 4.9577 | 3.805 | 3.5294 | 1.4283 | 26.9757
2006-03-12 | 17:59 | 0 | 15.883 | 0 | 3 | 0 | 54.709 | 54.997 | 38.688 | 38.923 | 31.446 | 26.073 | 4.506 | 1 | 0 | 59.328 | 56.503 | 49.08 | 18.635 | 0 | 0 | 54.516 | 33.916 | [5 empty] | 0 | 15.786 | 5 | 5.2843 | 4.9477 | 3.8045 | 3.5294 | 1.4183 | 26.8406
2006-03-12 | 18:00 | 0 | 15.817 | 0 | 3 | 0 | 54.651 | 55.088 | 38.827 | 39.038 | 31.347 | 26.166 | 4.58 | 2 | 0 | 59.303 | 56.478 | 49.01 | 18.633 | 0 | 0 | 54.56 | 33.869 | [5 empty] | 0 | 15.613 | 6 | 5.2627 | 4.9273 | 3.8037 | 3.5294 | 1.3978 | 26.5613
2006-03-12 | 18:01 | 0 | 15.842 | 0 | 2 | 0 | 54.719 | 55.088 | 38.851 | 38.968 | 31.563 | 26.24 | 4.48 | 1 | 0 | 59.372 | 56.478 | 48.94 | 18.658 | 0 | 0 | 54.581 | 33.821 | [5 empty] | 0 | 15.751 | 7 | 5.2918 | 4.9549 | 3.8048 | 3.5294 | 1.4255 | 26.9382
2006-03-12 | 18:02 | 1 | 15.842 | 0 | 3 | 0 | 54.833 | 55.179 | 39.062 | 38.992 | 31.419 | 26.191 | 4.454 | 1 | 0 | 59.372 | 56.524 | 48.986 | 18.633 | 0 | 0 | 54.537 | 33.821 | [5 empty] | 15.842 | 15.841 | 8 | 5.2994 | 4.9621 | 3.8052 | 3.5294 | 1.4327 | 27.0356
2006-03-12 | 18:03 | 0 | 15.817 | 0 | 3 | 0 | 55.109 | 55.202 | 39.062 | 39.133 | 31.637 | 26.166 | 4.202 | 1 | 0 | 59.326 | 56.432 | 49.077 | 18.61 | 0 | 0 | 54.537 | 33.821 | [5 empty] | 0 | 15.976 | 9 | 5.3728 | 5.0319 | 3.8081 | 3.5294 | 1.5025 | 27.9646
2006-03-12 | 18:04 | 0 | 15.842 | 0 | 3 | 0 | 55.155 | 55.477 | 39.227 | 39.203 | 31.757 | 26.191 | 4.428 | 1 | 0 | 59.28 | 56.41 | 48.963 | 18.633 | 0 | 0 | 54.49 | 33.821 | [5 empty] | 0 | 15.952 | 10 | 5.307 | 4.9693 | 3.8055 | 3.5294 | 1.4399 | 27.1326
2006-03-12 | 18:05 | 0 | 15.842 | 0 | 3 | 0 | 55.132 | 55.568 | 39.296 | 39.296 | 31.588 | 26.191 | 4.377 | 2 | 0 | 59.326 | 56.432 | 48.986 | 18.61 | 0 | 0 | 54.443 | 33.869 | [5 empty] | 0 | 15.836 | 11 | 5.3218 | 4.9834 | 3.8061 | 3.5294 | 1.454 | 27.3221
2006-03-12 | 18:06 | 0 | 15.817 | 0 | 3 | 0 | 55.202 | 55.498 | 39.413 | 39.437 | 31.637 | 26.24 | 4.328 | 1 | 0 | 59.303 | 56.478 | 48.963 | 18.633 | 0 | 0 | 54.376 | 33.869 | [5 empty] | 0 | 15.765 | 12 | 5.3361 | 4.997 | 3.8066 | 3.5294 | 1.4676 | 27.5033
2006-03-12 | 18:07 | 1 | 15.835 | 1 | 3 | 0 | 55.377 | 55.561 | 39.454 | 39.454 | 31.941 | 26.088 | 4.421 | 1 | 0 | 59.274 | 56.426 | 48.956 | 18.625 | 0 | 0 | 54.392 | 33.907 | [5 empty] | 15.835 | 15.923 | 13 | 5.309 | 4.9713 | 3.8055 | 3.5294 | 1.4419 | 27.1587
2006-03-12 | 18:08 | 0 | 15.868 | 0 | 3 | 0 | 55.431 | 55.774 | 39.461 | 39.578 | 32.24 | 26.022 | 4.454 | 1 | 0 | 59.28 | 56.389 | 48.986 | 18.658 | 0 | 0 | 54.422 | 33.914 | [5 empty] | 0 | 15.853 | 14 | 5.2994 | 4.9621 | 3.8052 | 3.5294 | 1.4327 | 27.0356
2006-03-12 | 18:09 | 0 | 15.842 | 0 | 3 | 0 | 55.34 | 55.797 | 39.65 | 39.65 | 32.142 | 26.144 | 4.454 | 1 | 0 | 59.28 | 56.389 | 49.031 | 18.658 | 0 | 0 | 54.467 | 33.914 | [5 empty] | 0 | 15.69 | 15 | 5.2994 | 4.9621 | 3.8052 | 3.5294 | 1.4327 | 27.0356
2006-03-12 | 18:10 | 0 | 15.842 | 0 | 3 | 1 | 55.34 | 55.729 | 39.767 | 39.696 | 31.757 | 26.046 | 4.428 | 1 | 0 | 59.237 | 56.432 | 49.01 | 18.708 | 0 | 0 | 54.49 | 33.869 | [5 empty] | 0 | 15.644 | 16 | 5.307 | 4.9693 | 3.8055 | 3.5294 | 1.4399 | 27.1326
2006-03-12 | 18:11 | 1 | 15.842 | 0 | 3 | 0 | 55.293 | 55.729 | 39.861 | 39.743 | 31.708 | 26.12 | 4.454 | 2 | 0 | 59.258 | 56.455 | 48.963 | 18.633 | 0 | 0 | 54.513 | 33.821 | [5 empty] | 15.842 | 15.55 | 0 | 5.2994 | 4.9621 | 3.8052 | 3.5294 | 1.4327 | 27.0356
2006-03-12 | 18:12 | 0 | 15.842 | 0 | 2 | 0 | 55.361 | 55.706 | 39.908 | 39.932 | 31.806 | 26.071 | 4.403 | 1 | 0 | 59.258 | 56.366 | 49.01 | 18.633 | 0 | 0 | 54.49 | 33.821 | [5 empty] | 0 | 15.429 | 1 | 5.3142 | 4.9762 | 4.0263 | 3.75 | 1.2262 | 23.0748
2006-03-12 | 18:13 | 0 | 15.81 | 0 | 3 | 0 | 55.561 | 55.699 | 40.042 | 39.947 | 31.725 | 26.088 | 4.421 | 1 | 0 | 59.207 | 56.359 | 48.979 | 18.625 | 0 | 0 | 54.436 | 33.814 | [5 empty] | 0 | 15.614 | 2 | 5.309 | 4.9713 | 4.0261 | 3.75 | 1.2213 | 23.0037
2006-03-12 | 18:14 | 0 | 15.835 | 0 | 3 | 0 | 55.652 | 55.974 | 40.064 | 40.16 | 31.725 | 26.159 | 4.269 | 1 | 0 | 59.228 | 56.359 | 48.956 | 18.6 | 0 | 0 | 54.436 | 33.766 | [5 empty] | 0 | 15.492 | 3 | 5.3533 | 5.0133 | 4.0279 | 3.75 | 1.2633 | 23.5994
2006-03-12 | 18:15 | 0 | 15.81 | 0 | 3 | 0 | 55.767 | 55.995 | 40.16 | 40.064 | 31.774 | 26.159 | 4.318 | 1 | 0 | 59.207 | 56.359 | 49.07 | 18.578 | 0 | 0 | 54.369 | 33.766 | [5 empty] | 0 | 15.703 | 4 | 5.339 | 4.9998 | 4.0273 | 3.75 | 1.2498 | 23.4085
2006-03-12 | 18:16 | 1 | 15.81 | 1 | 3 | 0 | 55.743 | 56.156 | 40.229 | 40.301 | 31.75 | 26.112 | 4.343 | 2 | 0 | 59.228 | 56.337 | 48.956 | 18.6 | 0 | 0 | 54.369 | 33.742 | [5 empty] | 15.81 | 15.442 | 5 | 5.3317 | 4.9929 | 4.0271 | 3.75 | 1.2429 | 23.3106
2006-03-12 | 18:17 | 0 | 15.842 | 0 | 3 | 0 | 55.636 | 56.232 | 40.26 | 40.215 | 31.997 | 26.12 | 3.998 | 1 | 0 | 59.258 | 56.389 | 48.986 | 18.658 | 0 | 0 | 54.49 | 33.845 | [5 empty] | 0 | 15.421 | 6 | 5.4322 | 5.0884 | 4.0311 | 3.75 | 1.3384 | 24.6375
2006-03-12 | 18:18 | 0 | 15.842 | 0 | 3 | 0 | 55.659 | 56.072 | 40.236 | 40.401 | 32.336 | 26.046 | 4.251 | 1 | 0 | 59.237 | 56.389 | 49.077 | 18.734 | 0 | 0 | 54.352 | 33.914 | [5 empty] | 0 | 15.258 | 7 | 5.3585 | 5.0183 | 4.0281 | 3.75 | 1.2683 | 23.6693
2006-03-12 | 18:19 | 0 | 15.817 | 0 | 3 | 0 | 55.636 | 56.026 | 40.332 | 40.413 | 32.274 | 26.034 | 4.315 | 1 | 0 | 59.246 | 56.442 | 49.019 | 18.646 | 0 | 0 | 54.385 | 33.785 | [5 empty] | 0 | 15.223 | 8 | 5.3399 | 5.0006 | 4.0274 | 3.75 | 1.2506 | 23.4202
2006-03-12 | 18:20 | 0 | 15.8 | 0 | 4 | 0 | 55.687 | 56.009 | 40.36 | 40.337 | 32.341 | 26.029 | 4.207 | 1 | 0 | 59.219 | 56.348 | 48.968 | 18.666 | 0 | 0 | 54.334 | 33.732 | [5 empty] | 0 | 15.35 | 9 | 5.3713 | 5.0305 | 4.0287 | 3.75 | 1.2805 | 23.8396
2006-03-12 | 18:21 | 1 | 15.85 | 0 | 3 | 0 | 55.825 | 56.077 | 40.502 | 40.454 | 32.792 | 26.054 | 4.41 | 1 | 0 | 59.219 | 56.325 | 49.082 | 18.59 | 0 | 0 | 54.289 | 33.732 | [5 empty] | 15.85 | 15.371 | 10 | 5.3122 | 4.9743 | 4.0263 | 3.75 | 1.2243 | 23.0471
2006-03-12 | 18:22 | 0 | 15.825 | 0 | 3 | 0 | 55.755 | 56.168 | 40.712 | 40.547 | 33.003 | 26.174 | 4.384 | 1 | 0 | 59.196 | 56.325 | 48.968 | 18.615 | 0 | 0 | 54.289 | 33.732 | [5 empty] | 0 | 15.208 | 11 | 5.3198 | 4.9815 | 4.0266 | 3.75 | 1.2315 | 23.1496
2006-03-12 | 18:23 | 0 | 15.857 | 0 | 3 | 0 | 56.061 | 56.22 | 40.815 | 40.767 | 33.082 | 26.326 | 4.318 | 2 | 0 | 59.248 | 56.378 | 48.998 | 18.623 | 0 | 0 | 54.341 | 33.763 | [5 empty] | 0 | 15.294 | 12 | 5.339 | 4.9998 | 4.0273 | 3.75 | 1.2498 | 23.4085
2006-03-12 | 18:24 | 0 | 15.85 | 0 | 3 | 0 | 56.03 | 56.371 | 40.877 | 40.877 | 32.862 | 26.488 | 4.359 | 1 | 0 | 59.196 | 56.348 | 49.059 | 18.59 | 0 | 0 | 54.357 | 33.802 | [5 empty] | 0 | 15.153 | 13 | 5.3271 | 4.9884 | 4.0269 | 3.75 | 1.2384 | 23.2479
2006-03-12 | 18:25 | 0 | 15.825 | 0 | 3 | 0 | 55.963 | 56.414 | 40.784 | 41.042 | 32.885 | 26.463 | 4.284 | 1 | 0 | 59.196 | 56.348 | 49.059 | 18.615 | 0 | 0 | 54.31 | 33.802 | [5 empty] | 0 | 14.921 | 14 | 5.3489 | 5.0092 | 4.0277 | 3.75 | 1.2592 | 23.5411
2006-03-12 | 18:26 | 1 | 15.85 | 1 | 3 | 1 | 55.872 | 56.302 | 40.853 | 40.901 | 32.72 | 26.679 | 4.233 | 1 | 0 | 59.219 | 56.348 | 49.082 | 18.64 | 0 | 0 | 54.38 | 33.897 | [5 empty] | 15.85 | 14.971 | 15 | 5.3638 | 5.0233 | 4.0284 | 3.75 | 1.2733 | 23.7391
2006-03-12 | 18:27 | 0 | 15.875 | 0 | 3 | 0 | 56.1 | 56.213 | 40.947 | 40.994 | 32.933 | 26.777 | 4.258 | 1 | 0 | 59.196 | 56.28 | 49.038 | 18.59 | 0 | 0 | 54.266 | 33.78 | [5 empty] | 0 | 15.106 | 0 | 5.3565 | 5.0164 | 4.0281 | 3.75 | 1.2664 | 23.6422
2006-03-12 | 18:28 | 0 | 15.875 | 0 | 3 | 0 | 56.054 | 56.46 | 41.018 | 41.018 | 32.909 | 26.799 | 4.31 | 1 | 0 | 59.219 | 56.302 | 48.991 | 18.615 | 0 | 0 | 54.266 | 33.756 | [5 empty] | 0 | 15.036 | 1 | 5.3413 | 5.002 | 4.0274 | 3.75 | 1.252 | 23.4397
2006-03-12 | 18:29 | 0 | 15.845 | 0 | 3 | 0 | 56.163 | 56.41 | 40.99 | 41.059 | 32.929 | 26.603 | 4.227 | 1 | 0 | 59.146 | 56.252 | 49.01 | 18.585 | 0 | 0 | 54.238 | 33.727 | [5 empty] | 0 | 15.104 | 2 | 5.3655 | 5.025 | 4.0284 | 3.75 | 1.275 | 23.7623
2006-03-12 | 18:30 | 1 | 15.85 | 0 | 3 | 0 | 55.734 | 56.594 | 41.324 | 41.183 | 33.381 | 26.679 | 4.132 | 2 | 0 | 59.196 | 56.302 | 48.991 | 18.615 | 0 | 0 | 54.266 | 33.732 | [5 empty] | 15.85 | 14.551 | 3 | 5.3932 | 5.0513 | 4.0295 | 3.75 | 1.3013 | 24.128
2006-03-12 | 18:31 | 0 | 15.898 | 0 | 3 | 0 | 55.596 | 56.236 | 40.664 | 41.346 | 33.402 | 26.632 | 4.032 | 1 | 0 | 59.173 | 56.28 | 48.991 | 18.615 | 0 | 0 | 54.266 | 33.756 | [5 empty] | 0 | 14.25 | 4 | 5.4223 | 5.0789 | 4.0307 | 3.75 | 1.3289 | 24.5089
2006-03-12 | 18:32 | 0 | 15.875 | 0 | 4 | 0 | 55.482 | 56.009 | 40.384 | 40.784 | 33.381 | 26.799 | 4.158 | 1 | 0 | 59.173 | 56.28 | 48.991 | 18.615 | 0 | 0 | 54.289 | 33.78 | [5 empty] | 0 | 14.698 | 5 | 5.3856 | 5.0441 | 4.0292 | 3.75 | 1.2941 | 24.0283
2006-03-12 | 18:33 | 0 | 15.875 | 0 | 3 | 0 | 55.207 | 55.893 | 40.243 | 40.526 | 33.708 | 26.679 | 4.184 | 1 | 0 | 59.128 | 56.236 | 49.038 | 18.59 | 0 | 0 | 54.31 | 33.78 | [5 empty] | 0 | 14.681 | 6 | 5.378 | 5.0369 | 4.0289 | 3.75 | 1.2869 | 23.9283
2006-03-12 | 18:34 | 0 | 15.795 | 0 | 3 | 0 | 55.062 | 55.613 | 40.119 | 40.449 | 33.586 | 26.77 | 4.153 | 1 | 0 | 59.1 | 56.252 | 48.986 | 18.56 | 0 | 0 | 54.215 | 33.821 | [5 empty] | 0 | 14.613 | 7 | 5.387 | 5.0454 | 4.0293 | 3.75 | 1.2954 | 24.0475
2006-03-12 | 18:35 | 1 | 15.82 | 1 | 4 | 0 | 54.971 | 55.498 | 40.215 | 40.401 | 33.61 | 26.649 | 4.227 | 1 | 0 | 59.146 | 56.209 | 48.963 | 18.56 | 0 | 0 | 54.191 | 33.704 | [5 empty] | 15.82 | 14.57 | 8 | 5.3655 | 5.025 | 4.0284 | 3.75 | 1.275 | 23.7623
2006-03-12 | 18:36 | 0 | 15.85 | 0 | 3 | 0 | 55.022 | 55.503 | 40.289 | 40.526 | 33.543 | 26.654 | 4.132 | 1 | 0 | 59.173 | 56.302 | 49.014 | 18.59 | 0 | 0 | 54.196 | 33.732 | [5 empty] | 0 | 14.496 | 9 | 5.3932 | 5.0513 | 4.0295 | 3.75 | 1.3013 | 24.128
2006-03-12 | 18:37 | 0 | 15.769 | 0 | 3 | 0 | 54.903 | 55.431 | 40.26 | 40.497 | 33.493 | 26.578 | 4.279 | 2 | 0 | 59.1 | 56.209 | 48.986 | 18.537 | 0 | 0 | 54.077 | 33.727 | [5 empty] | 0 | 14.406 | 10 | 5.3504 | 5.0106 | 4.0278 | 3.75 | 1.2606 | 23.5605
2006-03-12 | 18:38 | 0 | 15.795 | 0 | 4 | 0 | 54.833 | 55.384 | 40.119 | 40.473 | 33.328 | 26.36 | 4.328 | 1 | 0 | 59.123 | 56.209 | 49.01 | 18.56 | 0 | 0 | 54.054 | 33.704 | [5 empty] | 0 | 14.36 | 11 | 5.3361 | 4.997 | 4.0272 | 3.75 | 1.247 | 23.3694
2006-03-12 | 18:39 | 0 | 15.769 | 0 | 3 | 0 | 54.789 | 55.27 | 40.143 | 40.473 | 33.187 | 26.24 | 4.202 | 1 | 0 | 59.1 | 56.163 | 49.054 | 18.56 | 0 | 0 | 54.054 | 33.68 | [5 empty] | 0 | 14.316 | 12 | 5.3728 | 5.0319 | 4.0287 | 3.75 | 1.2819 | 23.8589
2006-03-12 | 18:40 | 1 | 15.777 | 0 | 4 | 0 | 54.702 | 55.183 | 40.126 | 40.456 | 33.639 | 26.176 | 4.109 | 1 | 0 | 59.061 | 56.17 | 49.014 | 18.542 | 0 | 0 | 54.037 | 33.663 | [5 empty] | 15.777 | 14.246 | 13 | 5.3999 | 5.0576 | 4.0298 | 3.75 | 1.3076 | 24.216
2006-03-12 | 18:41 | 0 | 15.777 | 0 | 3 | 0 | 54.635 | 55.162 | 39.892 | 40.456 | 33.897 | 26.392 | 4.083 | 1 | 0 | 59.107 | 56.17 | 48.856 | 18.593 | 0 | 0 | 54.037 | 33.663 | [5 empty] | 0 | 14.179 | 14 | 5.4074 | 5.0648 | 4.0301 | 3.75 | 1.3148 | 24.3152
2006-03-12 | 18:42 | 0 | 15.777 | 0 | 3 | 1 | 54.565 | 55.139 | 39.703 | 40.102 | 33.969 | 26.367 | 4.109 | 1 | 0 | 59.061 | 56.17 | 48.877 | 18.568 | 0 | 0 | 54.061 | 33.615 | [5 empty] | 0 | 14.463 | 15 | 5.3999 | 5.0576 | 4.0298 | 3.75 | 1.3076 | 24.216
2006-03-12 | 18:43 | 0 | 15.785 | 0 | 4 | 0 | 54.686 | 55.032 | 39.758 | 40.112 | 34.141 | 26.23 | 4.117 | 2 | 0 | 59.091 | 56.177 | 48.93 | 18.575 | 0 | 0 | 54.023 | 33.646 | [5 empty] | 0 | 14.574 | 0 | 5.3975 | 5.0554 | 4.0297 | 3.75 | 1.3054 | 24.1854
2006-03-12 | 18:44 | 1 | 15.777 | 0 | 3 | 0 | 54.679 | 55.139 | 39.774 | 40.033 | 34.275 | 26.152 | 4.057 | 1 | 0 | 59.061 | 56.193 | 48.877 | 18.568 | 0 | 0 | 54.198 | 33.57 | [5 empty] | 15.777 | 14.646 | 1 | 5.415 | 5.072 | 4.0304 | 3.75 | 1.322 | 24.4141
2006-03-12 | 18:45 | 0 | 15.752 | 1 | 4 | 0 | 54.749 | 55.162 | 39.82 | 40.15 | 34.11 | 26.176 | 4.184 | 1 | 0 | 59.061 | 56.147 | 48.97 | 18.542 | 0 | 0 | 54.175 | 33.546 | [5 empty] | 0 | 14.599 | 2 | 5.378 | 5.0369 | 4.0289 | 3.75 | 1.2869 | 23.9283
2006-03-12 | 18:46 | 0 | 15.802 | 0 | 3 | 0 | 54.679 | 55.183 | 39.939 | 40.219 | 33.594 | 26.343 | 4.184 | 1 | 0 | 59.084 | 56.17 | 48.856 | 18.568 | 0 | 0 | 54.128 | 33.546 | [5 empty] | 0 | 14.46 | 3 | 5.378 | 5.0369 | 4.0289 | 3.75 | 1.2869 | 23.9283
2006-03-12 | 18:47 | 0 | 15.802 | 0 | 4 | 0 | 54.611 | 55.116 | 40.102 | 40.315 | 33.239 | 26.416 | 4.135 | 1 | 0 | 59.061 | 56.124 | 48.877 | 18.542 | 0 | 0 | 54.152 | 33.594 | [5 empty] | 0 | 14.296 | 4 | 5.3923 | 5.0504 | 4.0295 | 3.75 | 1.3004 | 24.1165
2006-03-12 | 18:48 | 1 | 15.777 | 0 | 3 | 0 | 54.635 | 55.092 | 40.081 | 40.384 | 33.053 | 26.343 | 4.235 | 2 | 0 | 59.041 | 56.1 | 48.993 | 18.542 | 0 | 0 | 54.061 | 33.57 | [5 empty] | 15.777 | 14.251 | 5 | 5.3632 | 5.0228 | 4.0283 | 3.75 | 1.2728 | 23.7313
2006-03-12 | 18:49 | 0 | 15.777 | 0 | 4 | 0 | 54.611 | 55.001 | 40.267 | 40.456 | 32.795 | 26.416 | 4.083 | 1 | 0 | 59.041 | 56.259 | 48.97 | 18.568 | 0 | 0 | 54.084 | 33.546 | [5 empty] | 0 | 14.155 | 6 | 5.4074 | 5.0648 | 4.0301 | 3.75 | 1.3148 | 24.3152
2006-03-12 | 18:50 | 0 | 15.802 | 0 | 3 | 0 | 54.679 | 55.046 | 40.36 | 40.597 | 32.582 | 26.463 | 4.109 | 1 | 0 | 59.041 | 56.079 | 48.877 | 18.542 | 0 | 0 | 54.084 | 33.498 | [5 empty] | 0 | 14.082 | 7 | 5.3999 | 5.0576 | 4.0298 | 3.75 | 1.3076 | 24.216
2006-03-12 | 18:51 | 0 | 15.802 | 0 | 3 | 0 | 54.702 | 55.069 | 40.502 | 40.691 | 32.414 | 26.463 | 4.032 | 1 | 0 | 59.061 | 56.1 | 48.877 | 18.568 | 0 | 0 | 54.107 | 33.498 | [5 empty] | 0 | 14.011 | 8 | 5.4223 | 5.0789 | 4.0307 | 3.75 | 1.3289 | 24.5089
2006-03-12 | 18:52 | 0 | 15.772 | 0 | 4 | 0 | 54.812 | 55.134 | 40.573 | 40.832 | 32.269 | 26.367 | 4.032 | 1 | 0 | 59.041 | 56.1 | 48.9 | 18.568 | 0 | 0 | 54.084 | 33.498 | [5 empty] | 0 | 13.98 | 9 | 5.4223 | 5.0789 | 4.0307 | 3.75 | 1.3289 | 24.5089
2006-03-12 | 18:53 | 1 | 15.802 | 0 | 3 | 0 | 54.772 | 55.23 | 40.714 | 40.856 | 32.078 | 26.488 | 4.083 | 1 | 0 | 59.041 | 56.056 | 48.856 | 18.568 | 0 | 0 | 54.037 | 33.498 | [5 empty] | 15.802 | 13.916 | 10 | 5.4074 | 5.0648 | 4.0301 | 3.75 | 1.3148 | 24.3152
2006-03-12 | 18:54 | 0 | 15.802 | 1 | 3 | 0 | 54.817 | 55.207 | 40.691 | 41.09 | 32.174 | 26.488 | 4.006 | 2 | 0 | 58.995 | 56.1 | 48.877 | 18.618 | 0 | 0 | 54.037 | 33.452 | [5 empty] | 0 | 13.727 | 11 | 5.4299 | 5.0861 | 4.031 | 3.75 | 1.3361 | 24.6073
2006-03-12 | 18:55 | 0 | 15.797 | 0 | 4 | 0 | 54.765 | 55.202 | 40.803 | 40.968 | 32.169 | 26.412 | 4.104 | 1 | 0 | 59.013 | 56.051 | 48.804 | 18.537 | 0 | 0 | 53.986 | 33.448 | [5 empty] | 0 | 13.797 | 12 | 5.4013 | 5.059 | 4.0299 | 3.75 | 1.309 | 24.2351
2006-03-12 | 18:56 | 0 | 15.802 | 0 | 3 | 0 | 55.069 | 55.183 | 40.88 | 41.066 | 32.439 | 26.561 | 4.109 | 1 | 0 | 59.13 | 56.079 | 48.856 | 18.618 | 0 | 0 | 54.014 | 33.498 | [5 empty] | 0 | 14.003 | 13 | 5.3999 | 5.0576 | 4.0298 | 3.75 | 1.3076 | 24.216
2006-03-12 | 18:57 | 0 | 15.802 | 0 | 3 | 0 | 55.277 | 55.414 | 40.925 | 41.159 | 32.912 | 26.463 | 4.006 | 1 | 0 | 59.018 | 56.1 | 49.014 | 18.568 | 0 | 0 | 53.97 | 33.498 | [5 empty] | 0 | 14.118 | 14 | 5.4299 | 5.0861 | 4.031 | 3.75 | 1.3361 | 24.6073
2006-03-12 | 18:58 | 1 | 15.777 | 0 | 3 | 1 | 55.277 | 55.643 | 41.066 | 41.301 | 33.311 | 26.441 | 3.931 | 1 | 0 | 58.995 | 55.986 | 48.97 | 18.568 | 0 | 0 | 53.97 | 33.452 | [5 empty] | 15.777 | 13.976 | 15 | 5.4517 | 5.1069 | 4.0319 | 3.75 | 1.3569 | 24.8895
2006-03-12 | 18:59 | 0 | 15.747 | 0 | 4 | 0 | 55.454 | 55.662 | 41.155 | 41.413 | 33.586 | 26.532 | 4.026 | 1 | 0 | 59.013 | 56.028 | 48.849 | 18.49 | 0 | 0 | 53.918 | 33.424 | [5 empty] | 0 | 14.041 | 0 | 5.424 | 5.0806 | 4.0308 | 3.75 | 1.3306 | 24.5316
2006-03-12 | 19:00 | 0 | 15.777 | 0 | 3 | 0 | 55.459 | 55.918 | 41.396 | 41.42 | 33.682 | 26.483 | 4.052 | 2 | 0 | 58.945 | 55.981 | 48.986 | 18.537 | 0 | 0 | 53.872 | 33.328 | [5 empty] | 0 | 14.039 | 1 | 5.4165 | 5.0734 | 3.8099 | 3.5294 | 1.544 | 28.5056
2006-03-12 | 19:01 | 0 | 15.777 | 0 | 3 | 0 | 55.529 | 55.918 | 41.42 | 41.513 | 33.546 | 26.512 | 4.109 | 1 | 0 | 58.95 | 56.009 | 48.9 | 18.593 | 0 | 0 | 53.9 | 33.287 | [5 empty] | 0 | 14.016 | 2 | 5.3999 | 5.0576 | 3.8092 | 3.5294 | 1.5282 | 28.3011
2006-03-12 | 19:02 | 0 | 15.797 | 0 | 3 | 0 | 55.683 | 55.937 | 41.554 | 41.602 | 33.775 | 26.507 | 3.926 | 1 | 0 | 58.945 | 55.958 | 48.872 | 18.563 | 0 | 0 | 53.872 | 33.376 | [5 empty] | 0 | 14.081 | 3 | 5.4531 | 5.1083 | 3.8114 | 3.5294 | 1.5789 | 28.9534
2006-03-12 | 19:03 | 1 | 15.772 | 0 | 4 | 0 | 56.096 | 56.028 | 41.602 | 41.671 | 34.598 | 26.483 | 4.127 | 1 | 0 | 58.945 | 55.981 | 48.872 | 18.588 | 0 | 0 | 53.872 | 33.376 | [5 empty] | 15.772 | 14.425 | 4 | 5.3946 | 5.0526 | 3.809 | 3.5294 | 1.5232 | 28.2362
2006-03-12 | 19:04 | 0 | 15.802 | 1 | 3 | 0 | 56.371 | 56.505 | 41.7 | 41.82 | 35.12 | 26.632 | 4.057 | 1 | 0 | 58.972 | 56.009 | 48.877 | 18.618 | 0 | 0 | 53.9 | 33.405 | [5 empty] | 0 | 14.551 | 5 | 5.415 | 5.072 | 3.8098 | 3.5294 | 1.5426 | 28.4877
2006-03-12 | 19:05 | 0 | 15.747 | 0 | 3 | 0 | 56.209 | 56.59 | 41.86 | 41.884 | 34.974 | 26.556 | 4.001 | 1 | 0 | 58.968 | 55.958 | 48.872 | 18.588 | 0 | 0 | 53.848 | 33.376 | [5 empty] | 0 | 14.325 | 6 | 5.4313 | 5.0875 | 3.8105 | 3.5294 | 1.5581 | 28.6876
2006-03-12 | 19:06 | 0 | 15.747 | 0 | 3 | 0 | 56.165 | 56.547 | 41.954 | 41.977 | 34.598 | 26.676 | 3.975 | 1 | 0 | 58.991 | 55.958 | 48.849 | 18.537 | 0 | 0 | 53.827 | 33.4 | [5 empty] | 0 | 14.188 | 7 | 5.4389 | 5.0947 | 3.8108 | 3.5294 | 1.5653 | 28.78
2006-03-12 | 19:07 | 1 | 15.772 | 0 | 4 | 0 | 56.165 | 56.501 | 41.954 | 42.049 | 34.268 | 26.556 | 4.001 | 2 | 0 | 58.945 | 55.958 | 48.872 | 18.537 | 0 | 0 | 53.78 | 33.376 | [5 empty] | 15.772 | 14.116 | 8 | 5.4313 | 5.0875 | 3.8105 | 3.5294 | 1.5581 | 28.6876
2006-03-12 | 19:08 | 0 | 15.747 | 0 | 3 | 0 | 56.277 | 56.569 | 42.049 | 42.236 | 34.34 | 26.532 | 4.026 | 1 | 0 | 58.922 | 55.914 | 48.919 | 18.563 | 3 | 0 | 58.922 | 21.206 | [5 empty] | 0 | 14.041 | 9 | 5.424 | 5.0806 | 3.8102 | 3.5294 | 1.5512 | 28.5985
2006-03-12 | 19:09 | 0 | 15.797 | 0 | 3 | 0 | 56.343 | 56.658 | 42.308 | 42.166 | 34.268 | 26.676 | 3.849 | 1 | 0 | 58.899 | 55.82 | 48.576 | 18.512 | 0 | 0 | 60.314 | 14.613 | [5 empty] | 0 | 14.177 | 10 | 5.4756 | 5.1296 | 3.8123 | 3.5294 | 1.6002 | 29.2241
2006-03-12 | 19:10 | 0 | 15.772 | 0 | 3 | 0 | 56.458 | 56.704 | 42.449 | 42.26 | 34.223 | 26.578 | 3.926 | 1 | 0 | 58.899 | 55.776 | 47.931 | 18.563 | 0 | 0 | 60.469 | 13.972 | [5 empty] | 0 | 14.198 | 11 | 5.4531 | 5.1083 | 3.8114 | 3.5294 | 1.5789 | 28.9534
2006-03-12 | 19:11 | 0 | 15.772 | 0 | 4 | 0 | 56.478 | 56.839 | 42.425 | 42.518 | 34.081 | 26.532 | 3.8 | 1 | 0 | 58.879 | 55.706 | 47.152 | 18.563 | 0 | 0 | 60.38 | 14.342 | [5 empty] | 0 | 13.96 | 12 | 5.4898 | 5.1432 | 3.8129 | 3.5294 | 1.6137 | 29.3952
2006-03-12 | 19:12 | 1 | 15.772 | 0 | 3 | 0 | 56.412 | 56.793 | 42.518 | 42.494 | 34.034 | 26.556 | 3.774 | 1 | 0 | 58.856 | 55.729 | 46.328 | 18.537 | 0 | 0 | 60.2 | 15.081 | [5 empty] | 15.772 | 13.918 | 13 | 5.4974 | 5.1504 | 3.8132 | 3.5294 | 1.6209 | 29.4856
2006-03-12 | 19:13 | 0 | 15.797 | 1 | 3 | 0 | 56.547 | 56.793 | 42.566 | 42.566 | 34.247 | 26.412 | 3.722 | 1 | 0 | 58.856 | 55.683 | 45.777 | 18.537 | 0 | 0 | 60.045 | 15.895 | [5 empty] | 0 | 13.981 | 14 | 5.5126 | 5.1648 | 3.8138 | 3.5294 | 1.6353 | 29.6657
2006-03-12 | 19:14 | 0 | 15.797 | 0 | 3 | 0 | 56.681 | 56.95 | 42.635 | 42.542 | 34.199 | 26.507 | 3.748 | 1 | 0 | 58.856 | 55.683 | 45.317 | 18.563 | 0 | 0 | 59.931 | 16.536 | [5 empty] | 0 | 14.139 | 15 | 5.505 | 5.1576 | 3.8135 | 3.5294 | 1.6281 | 29.5758
2006-03-12 | 19:15 | 0 | 15.772 | 0 | 4 | 1 | 56.613 | 57.062 | 42.635 | 42.635 | 33.847 | 26.532 | 3.522 | 1 | 0 | 58.856 | 55.662 | 44.904 | 18.563 | 0 | 0 | 59.798 | 17.032 | [5 empty] | 0 | 13.978 | 16 | 5.5708 | 5.2201 | 3.8162 | 3.5294 | 1.6907 | 30.3493
2006-03-12 | 19:16 | 0 | 15.739 | 0 | 3 | 0 | 56.606 | 56.964 | 42.7 | 42.58 | 33.603 | 26.426 | 3.663 | 1 | 0 | 58.803 | 55.608 | 44.554 | 18.48 | 0 | 0 | 59.655 | 17.567 | [5 empty] | 0 | 14.026 | 0 | 5.5297 | 5.1811 | 3.8145 | 3.5294 | 1.6517 | 29.8689
2006-03-12 | 19:17 | 1 | 15.772 | 0 | 3 | 0 | 56.636 | 57.062 | 42.731 | 42.59 | 33.61 | 26.483 | 3.47 | 2 | 0 | 58.81 | 55.662 | 44.374 | 18.537 | 0 | 0 | 59.595 | 18.07 | [5 empty] | 15.772 | 14.046 | 1 | 5.5859 | 5.2345 | 3.8168 | 3.5294 | 1.7051 | 30.5247
2006-03-12 | 19:18 | 0 | 15.797 | 0 | 3 | 0 | 56.747 | 57.039 | 42.683 | 42.707 | 33.61 | 26.556 | 3.522 | 1 | 0 | 58.833 | 55.638 | 44.188 | 18.563 | 0 | 0 | 59.484 | 18.49 | [5 empty] | 0 | 14.04 | 2 | 5.5708 | 5.2201 | 3.8162 | 3.5294 | 1.6907 | 30.3493
2006-03-12 | 19:19 | 0 | 15.82 | 0 | 4 | 0 | 56.928 | 57.197 | 42.752 | 42.671 | 34.046 | 26.397 | 3.686 | 1 | 0 | 58.819 | 55.601 | 44.197 | 18.55 | 0 | 0 | 59.335 | 18.872 | [5 empty] | 0 | 14.257 | 3 | 5.523 | 5.1747 | 3.8142 | 3.5294 | 1.6453 | 29.7898
2006-03-12 | 19:20 | 0 | 15.885 | 0 | 3 | 0 | 56.939 | 57.32 | 42.647 | 42.695 | 34.4 | 26.473 | 3.534 | 1 | 0 | 58.733 | 55.533 | 43.87 | 18.527 | 0 | 0 | 59.203 | 19.168 | [5 empty] | 0 | 14.244 | 4 | 5.5673 | 5.2168 | 3.816 | 3.5294 | 1.6874 | 30.3087
2006-03-12 | 19:21 | 1 | 15.797 | 0 | 3 | 0 | 56.857 | 57.284 | 42.705 | 42.752 | 34.409 | 26.289 | 3.674 | 1 | 0 | 58.854 | 55.683 | 43.834 | 18.537 | 0 | 0 | 59.146 | 19.551 | [5 empty] | 15.797 | 14.105 | 5 | 5.5265 | 5.178 | 3.8144 | 3.5294 | 1.6486 | 29.8311
2006-03-12 | 19:22 | 0 | 15.737 | 0 | 4 | 0 | 56.848 | 57.206 | 42.719 | 42.788 | 34.4 | 26.279 | 3.586 | 1 | 0 | 58.753 | 55.557 | 43.8 | 18.527 | 0 | 0 | 59.023 | 19.787 | [5 empty] | 0 | 14.06 | 6 | 5.5522 | 5.2024 | 3.8154 | 3.5294 | 1.673 | 30.1321
2006-03-12 | 19:23 | 0 | 15.797 | 1 | 3 | 0 | 56.814 | 57.238 | 42.776 | 42.705 | 34.361 | 26.313 | 3.648 | 1 | 0 | 58.785 | 55.545 | 43.669 | 18.563 | 0 | 0 | 58.943 | 20.144 | [5 empty] | 0 | 14.109 | 7 | 5.5341 | 5.1852 | 3.8147 | 3.5294 | 1.6558 | 29.9203
2006-03-12 | 19:24 | 0 | 15.737 | 0 | 3 | 0 | 56.782 | 57.186 | 42.695 | 42.719 | 34.187 | 26.279 | 3.511 | 1 | 0 | 58.753 | 55.512 | 43.659 | 18.502 | 0 | 0 | 58.799 | 20.353 | [5 empty] | 0 | 14.063 | 8 | 5.574 | 5.2232 | 3.8163 | 3.5294 | 1.6937 | 30.3865
2006-03-12 | 19:25 | 0 | 15.737 | 0 | 3 | 0 | 56.782 | 57.163 | 42.695 | 42.836 | 34.4 | 26.23 | 3.534 | 2 | 0 | 58.733 | 55.466 | 43.659 | 18.477 | 0 | 0 | 58.664 | 20.617 | [5 empty] | 0 | 13.946 | 9 | 5.5673 | 5.2168 | 3.816 | 3.5294 | 1.6874 | 30.3087
2006-03-12 | 19:26 | 1 | 15.772 | 0 | 4 | 0 | 56.745 | 57.172 | 42.752 | 42.846 | 34.574 | 26.218 | 3.547 | 1 | 0 | 58.765 | 55.545 | 43.599 | 18.537 | 0 | 0 | 58.63 | 20.941 | [5 empty] | 15.772 | 13.899 | 10 | 5.5635 | 5.2132 | 3.8159 | 3.5294 | 1.6838 | 30.2647
2006-03-12 | 19:27 | 0 | 15.762 | 0 | 3 | 0 | 56.736 | 57.14 | 42.836 | 42.719 | 34.634 | 26.159 | 3.46 | 1 | 0 | 58.753 | 55.466 | 43.401 | 18.477 | 0 | 0 | 58.53 | 21.147 | [5 empty] | 0 | 14.017 | 11 | 5.5888 | 5.2373 | 3.8169 | 3.5294 | 1.7079 | 30.5584
2006-03-12 | 19:28 | 0 | 15.762 | 0 | 3 | 0 | 56.782 | 57.186 | 42.743 | 42.906 | 34.493 | 26.279 | 3.534 | 1 | 0 | 58.71 | 55.419 | 43.446 | 18.477 | 0 | 0 | 58.484 | 21.412 | [5 empty] | 0 | 13.876 | 12 | 5.5673 | 5.2168 | 3.816 | 3.5294 | 1.6874 | 30.3087
2006-03-12 | 19:29 | 0 | 15.772 | 0 | 3 | 0 | 56.814 | 57.172 | 42.846 | 42.846 | 34.337 | 26.313 | 3.674 | 1 | 0 | 58.765 | 55.498 | 43.41 | 18.537 | 0 | 0 | 58.45 | 21.711 | [5 empty] | 0 | 13.968 | 13 | 5.5265 | 5.178 | 3.8144 | 3.5294 | 1.6486 | 29.8311
2006-03-12 | 19:30 | 0 | 15.737 | 0 | 4 | 0 | 56.804 | 57.14 | 42.836 | 42.764 | 34.541 | 26.23 | 3.56 | 1 | 0 | 58.71 | 55.466 | 43.353 | 18.502 | 0 | 0 | 58.329 | 21.92 | [5 empty] | 0 | 14.04 | 14 | 5.5597 | 5.2096 | 3.8157 | 3.5294 | 1.6802 | 30.2205
2006-03-12 | 19:31 | 1 | 15.687 | 0 | 3 | 0 | 56.69 | 57.163 | 42.743 | 42.788 | 34.352 | 26.375 | 3.534 | 1 | 0 | 58.71 | 55.466 | 43.305 | 18.502 | 0 | 0 | 58.26 | 22.135 | [5 empty] | 15.687 | 13.902 | 15 | 5.5673 | 5.2168 | 3.816 | 3.5294 | 1.6874 | 30.3087
2006-03-12 | 19:32 | 0 | 15.712 | 1 | 3 | 1 | 56.69 | 57.094 | 42.671 | 42.812 | 34.258 | 26.184 | 3.612 | 1 | 0 | 58.71 | 55.442 | 43.401 | 18.452 | 0 | 0 | 58.149 | 22.376 | [5 empty] | 0 | 13.878 | 16 | 5.5446 | 5.1952 | 3.8151 | 3.5294 | 1.6658 | 30.0435
2006-03-12 | 19:33 | 0 | 15.712 | 0 | 4 | 0 | 56.579 | 57.051 | 42.578 | 42.788 | 33.694 | 26.184 | 3.586 | 1 | 0 | 58.687 | 55.466 | 43.284 | 18.502 | 0 | 0 | 58.082 | 22.618 | [5 empty] | 0 | 13.791 | 0 | 5.5522 | 5.2024 | 3.8154 | 3.5294 | 1.673 | 30.1321
2006-03-12 | 19:34 | 0 | 15.712 | 0 | 3 | 0 | 56.647 | 57.074 | 42.554 | 42.812 | 34.141 | 26.159 | 3.586 | 1 | 0 | 58.687 | 55.396 | 43.284 | 18.502 | 0 | 0 | 58.037 | 22.883 | [5 empty] | 0 | 13.835 | 1 | 5.5522 | 5.2024 | 4.036 | 3.75 | 1.4524 | 26.1591
2006-03-12 | 19:35 | 0 | 15.737 | 0 | 3 | 0 | 56.67 | 57.094 | 42.602 | 42.671 | 34.541 | 26.279 | 3.637 | 1 | 0 | 58.753 | 55.396 | 43.26 | 18.477 | 0 | 0 | 58.037 | 23.219 | [5 empty] | 0 | 13.999 | 2 | 5.5373 | 5.1883 | 4.0354 | 3.75 | 1.4383 | 25.9743
2006-03-12 | 19:36 | 1 | 15.707 | 0 | 4 | 0 | 56.663 | 57.09 | 42.408 | 42.573 | 35.053 | 26.105 | 3.632 | 1 | 0 | 58.683 | 55.347 | 43.183 | 18.447 | 0 | 0 | 57.964 | 23.454 | [5 empty] | 15.707 | 14.09 | 3 | 5.5388 | 5.1897 | 4.0354 | 3.75 | 1.4397 | 25.9925
2006-03-12 | 19:37 | 0 | 15.737 | 0 | 3 | 0 | 56.423 | 57.094 | 42.365 | 42.437 | 34.892 | 26.159 | 3.56 | 1 | 0 | 58.71 | 55.375 | 43.284 | 18.477 | 0 | 0 | 57.902 | 23.727 | [5 empty] | 0 | 13.986 | 4 | 5.5597 | 5.2096 | 4.0363 | 3.75 | 1.4596 | 26.2529
2006-03-12 | 19:38 | 0 | 15.712 | 0 | 3 | 0 | 56.175 | 56.871 | 42.343 | 42.461 | 34.493 | 26.184 | 3.586 | 2 | 0 | 58.687 | 55.375 | 43.236 | 18.477 | 0 | 0 | 57.902 | 23.893 | [5 empty] | 0 | 13.714 | 5 | 5.5522 | 5.2024 | 4.036 | 3.75 | 1.4524 | 26.1591
2006-03-12 | 19:39 | 0 | 15.687 | 0 | 4 | 0 | 56.04 | 56.624 | 42.178 | 42.365 | 34.4 | 26.147 | 3.473 | 1 | 0 | 58.701 | 55.386 | 43.295 | 18.49 | 0 | 0 | 57.827 | 24.075 | [5 empty] | 0 | 13.675 | 6 | 5.5851 | 5.2337 | 4.0373 | 3.75 | 1.4837 | 26.565
2006-03-12 | 19:40 | 1 | 15.757 | 0 | 3 | 0 | 55.853 | 56.533 | 42.08 | 42.221 | 34.349 | 26.252 | 3.429 | 1 | 0 | 58.708 | 55.372 | 43.303 | 18.497 | 0 | 0 | 57.811 | 24.347 | [5 empty] | 15.757 | 13.632 | 7 | 5.5979 | 5.2459 | 4.0378 | 3.75 | 1.4959 | 26.7218
2006-03-12 | 19:41 | 0 | 15.722 | 1 | 4 | 0 | 55.774 | 56.277 | 41.977 | 42.305 | 33.893 | 26.169 | 3.622 | 1 | 0 | 58.721 | 55.363 | 43.317 | 18.512 | 0 | 0 | 57.845 | 24.602 | [5 empty] | 0 | 13.469 | 8 | 5.5417 | 5.1924 | 4.0356 | 3.75 | 1.4424 | 26.0288
2006-03-12 | 19:42 | 0 | 15.722 | 0 | 3 | 0 | 55.774 | 56.163 | 41.836 | 42.119 | 33.986 | 26.264 | 3.596 | 1 | 0 | 58.698 | 55.363 | 43.224 | 18.462 | 0 | 0 | 57.802 | 24.7 | [5 empty] | 0 | 13.655 | 9 | 5.5492 | 5.1996 | 4.0359 | 3.75 | 1.4496 | 26.123
2006-03-12 | 19:43 | 0 | 15.757 | 0 | 4 | 0 | 55.806 | 56.241 | 41.918 | 42.176 | 33.974 | 26.274 | 3.581 | 1 | 0 | 58.708 | 55.417 | 43.233 | 18.522 | 0 | 0 | 57.765 | 24.855 | [5 empty] | 0 | 13.63 | 10 | 5.5536 | 5.2038 | 4.036 | 3.75 | 1.4538 | 26.1772
2006-03-12 | 19:44 | 0 | 15.757 | 0 | 3 | 0 | 55.762 | 56.195 | 41.846 | 42.035 | 33.995 | 26.228 | 3.607 | 1 | 0 | 58.774 | 55.396 | 43.209 | 18.598 | 0 | 0 | 57.742 | 25.046 | [5 empty] | 0 | 13.727 | 11 | 5.546 | 5.1966 | 4.0357 | 3.75 | 1.4466 | 26.0832
2006-03-12 | 19:45 | 1 | 15.747 | 0 | 4 | 0 | 55.659 | 56.119 | 41.743 | 41.954 | 33.893 | 26.12 | 3.645 | 1 | 0 | 58.653 | 55.316 | 43.152 | 18.487 | 0 | 0 | 57.69 | 25.205 | [5 empty] | 15.747 | 13.705 | 12 | 5.535 | 5.1861 | 4.0353 | 3.75 | 1.4361 | 25.9453
2006-03-12 | 19:46 | 0 | 15.747 | 0 | 3 | 0 | 55.568 | 56.072 | 41.695 | 41.86 | 33.893 | 26.264 | 3.519 | 1 | 0 | 58.721 | 55.34 | 43.128 | 18.439 | 0 | 0 | 57.667 | 25.325 | [5 empty] | 0 | 13.708 | 13 | 5.5717 | 5.2209 | 4.0368 | 3.75 | 1.4709 | 26.4004
2006-03-12 | 19:47 | 0 | 15.747 | 0 | 4 | 0 | 55.316 | 56.005 | 41.647 | 41.836 | 33.821 | 26.144 | 3.596 | 1 | 0 | 58.676 | 55.293 | 43.176 | 18.512 | 0 | 0 | 57.621 | 25.495 | [5 empty] | 0 | 13.48 | 14 | 5.5492 | 5.1996 | 4.0359 | 3.75 | 1.4496 | 26.123
2006-03-12 | 19:48 | 0 | 15.782 | 0 | 3 | 1 | 55.211 | 55.739 | 41.657 | 41.705 | 34.254 | 26.154 | 3.707 | 2 | 0 | 58.685 | 55.326 | 43.257 | 18.522 | 0 | 0 | 57.653 | 25.649 | [5 empty] | 0 | 13.506 | 15 | 5.5169 | 5.1689 | 4.0346 | 3.75 | 1.4189 | 25.7191
2006-03-12 | 19:49 | 1 | 15.747 | 0 | 4 | 0 | 55.246 | 55.636 | 41.554 | 41.671 | 34.034 | 26.049 | 3.57 | 1 | 0 | 58.653 | 55.316 | 43.152 | 18.487 | 0 | 0 | 57.621 | 25.735 | [5 empty] | 15.747 | 13.575 | 0 | 5.5568 | 5.2068 | 4.0362 | 3.75 | 1.4568 | 26.2169
2006-03-12 | 19:50 | 0 | 15.769 | 0 | 3 | 0 | 55.202 | 55.683 | 41.554 | 41.623 | 34.22 | 26.073 | 3.545 | 1 | 0 | 58.653 | 55.316 | 43.152 | 18.462 | 0 | 0 | 57.667 | 25.83 | [5 empty] | 0 | 13.579 | 1 | 5.5641 | 5.2137 | 4.0365 | 3.75 | 1.4637 | 26.307
2006-03-12 | 19:51 | 0 | 15.769 | 1 | 4 | 0 | 55.407 | 55.706 | 41.461 | 41.647 | 33.986 | 26.12 | 3.622 | 1 | 0 | 58.63 | 55.316 | 43.083 | 18.512 | 0 | 0 | 57.599 | 25.953 | [5 empty] | 0 | 13.76 | 2 | 5.5417 | 5.1924 | 4.0356 | 3.75 | 1.4424 | 26.0288
2006-03-12 | 19:52 | 0 | 15.795 | 0 | 3 | 0 | 55.407 | 55.729 | 41.695 | 41.623 | 34.01 | 26.12 | 3.671 | 1 | 0 | 58.63 | 55.363 | 43.152 | 18.588 | 0 | 0 | 57.555 | 26.098 | [5 empty] | 0 | 13.784 | 3 | 5.5274 | 5.1789 | 4.035 | 3.75 | 1.4289 | 25.8506
2006-03-12 | 19:53 | 0 | 15.805 | 0 | 4 | 0 | 55.235 | 55.853 | 41.564 | 41.657 | 33.785 | 26.154 | 3.658 | 1 | 0 | 58.685 | 55.326 | 43.162 | 18.522 | 0 | 0 | 57.519 | 26.252 | [5 empty] | 0 | 13.578 | 4 | 5.5312 | 5.1825 | 4.0351 | 3.75 | 1.4325 | 25.898
2006-03-12 | 19:54 | 1 | 15.805 | 0 | 4 | 0 | 55.417 | 55.715 | 41.494 | 41.635 | 33.713 | 26.228 | 3.681 | 2 | 0 | 58.685 | 55.258 | 43.116 | 18.497 | 0 | 0 | 57.564 | 26.372 | [5 empty] | 15.805 | 13.782 | 5 | 5.5245 | 5.1761 | 4.0349 | 3.75 | 1.4261 | 25.8141
2006-03-12 | 19:55 | 0 | 15.769 | 0 | 3 | 0 | 55.431 | 55.867 | 41.485 | 41.602 | 33.916 | 26.12 | 3.671 | 1 | 0 | 58.607 | 55.246 | 43.176 | 18.512 | 0 | 0 | 57.375 | 26.458 | [5 empty] | 0 | 13.829 | 6 | 5.5274 | 5.1789 | 4.035 | 3.75 | 1.4289 | 25.8506
2006-03-12 | 19:56 | 0 | 15.747 | 0 | 4 | 0 | 55.431 | 55.82 | 41.506 | 41.719 | 33.799 | 26.12 | 3.697 | 1 | 0 | 58.587 | 55.225 | 43.104 | 18.512 | 0 | 0 | 57.375 | 26.627 | [5 empty] | 0 | 13.712 | 7 | 5.5198 | 5.1717 | 4.0347 | 3.75 | 1.4217 | 25.7557
2006-03-12 | 19:57 | 0 | 15.769 | 0 | 3 | 0 | 55.431 | 55.82 | 41.506 | 41.789 | 33.893 | 26.169 | 3.697 | 1 | 0 | 58.63 | 55.246 | 43.2 | 18.537 | 0 | 0 | 57.329 | 26.772 | [5 empty] | 0 | 13.642 | 8 | 5.5198 | 5.1717 | 4.0347 | 3.75 | 1.4217 | 25.7557
2006-03-12 | 19:58 | 0 | 15.769 | 0 | 4 | 0 | 55.316 | 55.774 | 41.602 | 41.836 | 33.962 | 26.12 | 3.671 | 1 | 0 | 58.607 | 55.225 | 43.083 | 18.512 | 0 | 0 | 57.329 | 26.868 | [5 empty] | 0 | 13.48 | 9 | 5.5274 | 5.1789 | 4.035 | 3.75 | 1.4289 | 25.8506
2006-03-12 | 19:59 | 1 | 15.769 | 0 | 3 | 0 | 55.179 | 55.683 | 41.623 | 41.884 | 33.821 | 26.313 | 3.496 | 1 | 0 | 58.651 | 55.267 | 43.08 | 18.487 | 0 | 0 | 57.35 | 26.939 | [5 empty] | 15.769 | 13.295 | 10 | 5.5784 | 5.2273 | 4.037 | 3.75 | 1.4773 | 26.4828
2006-03-12 | 20:00 | 0 | 15.757 | 1 | 4 | 0 | 55.188 | 55.44 | 41.8 | 41.846 | 33.409 | 26.277 | 3.684 | 1 | 0 | 58.616 | 55.279 | 43.116 | 18.5 | 0 | 0 | 57.272 | 27.071 | [5 empty] | 0 | 13.342 | 11 | 5.5236 | 5.1753 | 4.0348 | 3.75 | 1.4253 | 25.8032
2006-03-12 | 20:01 | 0 | 15.757 | 0 | 3 | 0 | 55.118 | 55.601 | 41.939 | 41.918 | 33.739 | 26.252 | 3.558 | 1 | 0 | 58.55 | 55.165 | 43.14 | 18.427 | 0 | 0 | 57.227 | 27.145 | [5 empty] | 0 | 13.2 | 12 | 5.5603 | 5.2101 | 4.0363 | 3.75 | 1.4601 | 26.2601
2006-03-12 | 20:02 | 0 | 15.757 | 0 | 4 | 0 | 55.074 | 55.554 | 41.777 | 41.963 | 33.95 | 26.181 | 3.558 | 2 | 0 | 58.55 | 55.165 | 43.162 | 18.449 | 0 | 0 | 57.227 | 27.24 | [5 empty] | 0 | 13.111 | 13 | 5.5603 | 5.2101 | 4.0363 | 3.75 | 1.4601 | 26.2601
2006-03-12 | 20:03 | 1 | 15.757 | 0 | 4 | 0 | 55.097 | 55.531 | 41.87 | 41.987 | 33.692 | 26.157 | 3.609 | 1 | 0 | 58.55 | 55.165 | 43.162 | 18.475 | 0 | 0 | 57.204 | 27.336 | [5 empty] | 15.757 | 13.11 | 14 | 5.5455 | 5.196 | 4.0357 | 3.75 | 1.446 | 26.0759
2006-03-12 | 20:04 | 0 | 15.734 | 0 | 3 | 1 | 55.05 | 55.44 | 41.87 | 41.987 | 33.385 | 26.301 | 3.609 | 1 | 0 | 58.527 | 55.211 | 43.14 | 18.475 | 0 | 0 | 57.16 | 27.434 | [5 empty] | 0 | 13.063 | 15 | 5.5455 | 5.196 | 4.0357 | 3.75 | 1.446 | 26.0759
2006-03-12 | 20:05 | 0 | 15.704 | 0 | 4 | 0 | 55.046 | 55.48 | 41.793 | 41.958 | 33.57 | 26.247 | 3.627 | 1 | 0 | 58.523 | 55.16 | 43.111 | 18.444 | 0 | 0 | 57.156 | 27.547 | [5 empty] | 0 | 13.088 | 0 | 5.5402 | 5.191 | 4.0355 | 3.75 | 1.441 | 26.0106
2006-03-12 | 20:06 | 0 | 15.734 | 0 | 3 | 0 | 55.097 | 55.508 | 41.846 | 42.176 | 33.433 | 26.252 | 3.609 | 1 | 0 | 58.55 | 55.141 | 43.233 | 18.449 | 0 | 0 | 57.204 | 27.674 | [5 empty] | 0 | 12.921 | 1 | 5.5455 | 5.196 | 3.8151 | 3.5294 | 1.6666 | 30.0537
2006-03-12 | 20:07 | 0 | 15.734 | 0 | 4 | 0 | 55.188 | 55.487 | 41.894 | 42.245 | 33.316 | 26.252 | 3.583 | 1 | 0 | 58.527 | 55.141 | 43.281 | 18.427 | 0 | 0 | 57.204 | 27.745 | [5 empty] | 0 | 12.943 | 2 | 5.553 | 5.2032 | 3.8154 | 3.5294 | 1.6738 | 30.1423
2006-03-12 | 20:08 | 1 | 15.734 | 0 | 4 | 0 | 55.211 | 55.624 | 42.08 | 42.152 | 33.503 | 26.277 | 3.609 | 1 | 0 | 58.527 | 55.188 | 43.14 | 18.449 | 0 | 0 | 57.227 | 27.915 | [5 empty] | 15.734 | 13.059 | 3 | 5.5455 | 5.196 | 3.8151 | 3.5294 | 1.6666 | 30.0537
2006-03-12 | 20:09 | 0 | 15.734 | 1 | 3 | 0 | 55.372 | 55.715 | 42.128 | 42.317 | 33.644 | 26.203 | 3.635 | 2 | 0 | 58.55 | 55.211 | 43.281 | 18.475 | 0 | 0 | 57.138 | 27.89 | [5 empty] | 0 | 13.055 | 4 | 5.5379 | 5.1888 | 3.8148 | 3.5294 | 1.6594 | 29.9649
2006-03-12 | 20:10 | 0 | 15.727 | 0 | 4 | 0 | 55.55 | 55.825 | 42.147 | 42.265 | 33.45 | 26.198 | 3.4 | 1 | 0 | 58.523 | 55.137 | 43.205 | 18.444 | 0 | 0 | 57.087 | 27.956 | [5 empty] | 0 | 13.285 | 5 | 5.6063 | 5.2539 | 3.8176 | 3.5294 | 1.7245 | 30.7594
2006-03-12 | 20:11 | 0 | 15.679 | 0 | 3 | 0 | 55.596 | 55.916 | 42.123 | 42.334 | 33.263 | 26.174 | 3.4 | 1 | 0 | 58.5 | 55.16 | 43.274 | 18.444 | 0 | 0 | 56.953 | 28.005 | [5 empty] | 0 | 13.262 | 6 | 5.6063 | 5.2539 | 3.8176 | 3.5294 | 1.7245 | 30.7594
2006-03-12 | 20:12 | 1 | 15.757 | 0 | 4 | 0 | 55.645 | 56.014 | 42.41 | 42.504 | 33.385 | 26.157 | 3.483 | 1 | 0 | 58.55 | 55.097 | 43.257 | 18.449 | 0 | 0 | 56.98 | 28.108 | [5 empty] | 15.757 | 13.141 | 7 | 5.5822 | 5.2309 | 3.8166 | 3.5294 | 1.7015 | 30.481
2006-03-12 | 20:13 | 0 | 15.734 | 0 | 3 | 0 | 55.692 | 56.058 | 42.528 | 42.48 | 33.479 | 26.058 | 3.406 | 1 | 0 | 58.527 | 55.118 | 43.303 | 18.475 | 0 | 0 | 56.914 | 28.179 | [5 empty] | 0 | 13.212 | 8 | 5.6046 | 5.2522 | 3.8175 | 3.5294 | 1.7228 | 30.7393
2006-03-12 | 20:14 | 0 | 15.704 | 0 | 4 | 0 | 55.734 | 56.124 | 42.475 | 42.571 | 33.357 | 26.103 | 3.478 | 1 | 0 | 58.454 | 55.069 | 43.181 | 18.397 | 0 | 0 | 56.93 | 28.15 | [5 empty] | 0 | 13.163 | 9 | 5.5836 | 5.2323 | 3.8167 | 3.5294 | 1.7029 | 30.4978
2006-03-12 | 20:15 | 0 | 15.734 | 0 | 3 | 0 | 55.83 | 56.172 | 42.552 | 42.621 | 33.503 | 26.108 | 3.431 | 1 | 0 | 58.505 | 55.097 | 43.257 | 18.427 | 0 | 0 | 56.957 | 28.3 | [5 empty] | 0 | 13.209 | 10 | 5.5973 | 5.2453 | 3.8172 | 3.5294 | 1.7159 | 30.6557
2006-03-12 | 20:16 | 0 | 15.734 | 0 | 4 | 0 | 56.082 | 56.307 | 42.621 | 42.762 | 33.574 | 26.132 | 3.583 | 1 | 0 | 58.482 | 55.074 | 43.303 | 18.449 | 0 | 0 | 56.868 | 28.469 | [5 empty] | 0 | 13.32 | 11 | 5.553 | 5.2032 | 3.8154 | 3.5294 | 1.6738 | 30.1423
2006-03-12 | 20:17 | 1 | 15.734 | 0 | 3 | 0 | 56.172 | 56.487 | 42.81 | 42.903 | 33.902 | 26.157 | 3.483 | 1 | 0 | 58.482 | 55.05 | 43.327 | 18.427 | 0 | 0 | 56.935 | 28.444 | [5 empty] | 15.734 | 13.269 | 12 | 5.5822 | 5.2309 | 3.8166 | 3.5294 | 1.7015 | 30.481
2006-03-12 | 20:18 | 0 | 15.709 | 1 | 4 | 0 | 56.152 | 56.599 | 42.858 | 42.975 | 33.95 | 26.108 | 3.457 | 2 | 0 | 58.482 | 55.074 | 43.398 | 18.449 | 0 | 0 | 56.868 | 28.54 | [5 empty] | 0 | 13.177 | 13 | 5.5897 | 5.2381 | 3.8169 | 3.5294 | 1.7087 | 30.5684
2006-03-12 | 20:19 | 0 | 15.709 | 0 | 3 | 0 | 56.2 | 56.581 | 42.977 | 43.118 | 33.763 | 26.061 | 3.406 | 1 | 0 | 58.486 | 55.055 | 43.377 | 18.452 | 0 | 0 | 56.916 | 28.591 | [5 empty] | 0 | 13.082 | 14 | 5.6046 | 5.2522 | 3.8175 | 3.5294 | 1.7228 | 30.7393
2006-03-12 | 20:20 | 0 | 15.694 | 0 | 3 | 0 | 56.321 | 56.501 | 42.87 | 43.176 | 33.467 | 26.095 | 3.416 | 1 | 0 | 58.518 | 55.202 | 43.456 | 18.485 | 0 | 0 | 56.925 | 28.672 | [5 empty] | 0 | 13.145 | 15 | 5.6017 | 5.2495 | 3.8174 | 3.5294 | 1.72 | 30.7059
2006-03-12 | 20:21 | 0 | 15.714 | 0 | 4 | 1 | 56.248 | 56.608 | 43.099 | 43.051 | 33.204 | 26.186 | 3.434 | 1 | 0 | 58.468 | 55.013 | 43.31 | 18.382 | 0 | 0 | 56.944 | 28.716 | [5 empty] | 0 | 13.197 | 16 | 5.5964 | 5.2445 | 3.8172 | 3.5294 | 1.7151 | 30.6456
2006-03-12 | 20:22 | 1 | 15.714 | 0 | 3 | 0 | 56.382 | 56.674 | 43.075 | 43.147 | 33.555 | 26.09 | 3.537 | 1 | 0 | 58.468 | 55.013 | 43.382 | 18.407 | 0 | 0 | 56.944 | 28.763 | [5 empty] | 15.714 | 13.235 | 0 | 5.5664 | 5.216 | 3.816 | 3.5294 | 1.6865 | 30.2986
2006-03-12 | 20:23 | 0 | 15.714 | 0 | 4 | 0 | 56.585 | 56.898 | 43.264 | 43.264 | 33.696 | 25.992 | 3.485 | 1 | 0 | 58.445 | 54.99 | 43.475 | 18.432 | 0 | 0 | 56.877 | 28.788 | [5 empty] | 0 | 13.321 | 1 | 5.5816 | 5.2304 | 3.8166 | 3.5294 | 1.7009 | 30.4742
2006-03-12 | 20:24 | 0 | 15.714 | 0 | 3 | 0 | 56.921 | 57.055 | 43.264 | 43.286 | 34.026 | 26.066 | 3.485 | 1 | 0 | 58.491 | 55.013 | 43.405 | 18.53 | 0 | 0 | 56.877 | 28.861 | [5 empty] | 0 | 13.635 | 2 | 5.5816 | 5.2304 | 3.8166 | 3.5294 | 1.7009 | 30.4742
2006-03-12 | 20:25 | 0 | 15.737 | 0 | 4 | 0 | 56.855 | 57.325 | 43.193 | 43.451 | 34.074 | 26.017 | 3.434 | 1 | 0 | 58.468 | 54.99 | 43.592 | 18.432 | 0 | 0 | 56.898 | 28.908 | [5 empty] | 0 | 13.404 | 3 | 5.5964 | 5.2445 | 3.8172 | 3.5294 | 1.7151 | 30.6456
2006-03-12 | 20:26 | 0 | 15.689 | 0 | 3 | 0 | 56.697 | 57.124 | 43.217 | 43.334 | 34.05 | 26.041 | 3.537 | 1 | 0 | 58.445 | 54.99 | 43.523 | 18.382 | 0 | 0 | 56.944 | 28.957 | [5 empty] | 0 | 13.363 | 4 | 5.5664 | 5.216 | 3.816 | 3.5294 | 1.6865 | 30.2986
2006-03-12 | 20:27 | 1 | 15.714 | 0 | 4 | 0 | 56.809 | 57.055 | 43.264 | 43.382 | 34.12 | 26.017 | 3.46 | 1 | 0 | 58.445 | 55.036 | 43.547 | 18.454 | 0 | 0 | 56.898 | 29.028 | [5 empty] | 15.714 | 13.427 | 5 | 5.5888 | 5.2373 | 3.8169 | 3.5294 | 1.7079 | 30.5584
2006-03-12 | 20:28 | 0 | 15.689 | 1 | 3 | 0 | 56.674 | 57.078 | 43.405 | 43.286 | 33.957 | 26.066 | 3.434 | 1 | 0 | 58.425 | 55.013 | 43.451 | 18.454 | 0 | 0 | 56.855 | 29.052 | [5 empty] | 0 | 13.388 | 6 | 5.5964 | 5.2445 | 3.8172 | 3.5294 | 1.7151 | 30.6456
2006-03-12 | 20:29 | 0 | 15.714 | 0 | 4 | 0 | 56.697 | 57.101 | 43.358 | 43.382 | 34.357 | 26.017 | 3.411 | 1 | 0 | 58.468 | 55.036 | 43.499 | 18.48 | 0 | 0 | 56.832 | 29.101 | [5 empty] | 0 | 13.315 | 7 | 5.6031 | 5.2508 | 3.8175 | 3.5294 | 1.7214 | 30.7226
2006-03-12 | 20:30 | 0 | 15.714 | 0 | 3 | 0 | 56.697 | 57.078 | 43.616 | 43.547 | 34.756 | 26.112 | 3.511 | 1 | 0 | 58.445 | 54.99 | 43.592 | 18.432 | 0 | 0 | 56.786 | 29.173 | [5 empty] | 0 | 13.15 | 8 | 5.574 | 5.2232 | 3.8163 | 3.5294 | 1.6937 | 30.3865
2006-03-12 | 20:31 | 1 | 15.737 | 0 | 4 | 0 | 56.763 | 57.124 | 43.592 | 43.733 | 34.684 | 25.946 | 3.485 | 1 | 0 | 58.445 | 54.966 | 43.709 | 18.432 | 0 | 0 | 56.786 | 29.197 | [5 empty] | 15.737 | 13.03 | 9 | 5.5816 | 5.2304 | 3.8166 | 3.5294 | 1.7009 | 30.4742
2006-03-12 | 20:32 | 0 | 15.737 | 0 | 3 | 0 | 56.921 | 57.19 | 43.592 | 43.592 | 35.366 | 25.946 | 3.586 | 1 | 0 | 58.445 | 54.943 | 43.547 | 18.432 | 0 | 0 | 56.786 | 29.222 | [5 empty] | 0 | 13.329 | 10 | 5.5522 | 5.2024 | 3.8154 | 3.5294 | 1.673 | 30.1321
2006-03-12 | 20:33 | 0 | 15.737 | 0 | 3 | 0 | 56.832 | 57.459 | 43.616 | 43.568 | 35.883 | 25.946 | 3.586 | 1 | 0 | 58.445 | 54.966 | 43.547 | 18.432 | 0 | 0 | 56.786 | 29.271 | [5 empty] | 0 | 13.264 | 11 | 5.5522 | 5.2024 | 3.8154 | 3.5294 | 1.673 | 30.1321
2006-03-12 | 20:34 | 0 | 15.714 | 0 | 4 | 0 | 56.855 | 57.259 | 43.64 | 43.523 | 36.141 | 25.946 | 3.511 | 1 | 0 | 58.445 | 54.99 | 43.616 | 18.432 | 0 | 0 | 56.763 | 29.317 | [5 empty] | 0 | 13.332 | 12 | 5.574 | 5.2232 | 3.8163 | 3.5294 | 1.6937 | 30.3865
2006-03-12 | 20:35 | 0 | 15.689 | 0 | 3 | 0 | 56.832 | 57.37 | 43.499 | 43.592 | 35.765 | 26.017 | 3.434 | 2 | 0 | 58.425 | 54.99 | 43.709 | 18.432 | 0 | 0 | 56.763 | 29.391 | [5 empty] | 0 | 13.24 | 13 | 5.5964 | 5.2445 | 3.8172 | 3.5294 | 1.7151 | 30.6456
2006-03-12 | 20:36 | 1 | 15.689 | 0 | 4 | 0 | 56.743 | 57.213 | 43.475 | 43.499 | 35.39 | 25.968 | 3.485 | 1 | 0 | 58.402 | 54.898 | 43.568 | 18.454 | 0 | 0 | 56.697 | 29.486 | [5 empty] | 15.689 | 13.244 | 14 | 5.5816 | 5.2304 | 3.8166 | 3.5294 | 1.7009 | 30.4742
2006-03-12 | 20:37 | 0 | 15.689 | 1 | 3 | 0 | 56.563 | 57.124 | 43.451 | 43.547 | 34.825 | 26.017 | 3.434 | 1 | 0 | 58.402 | 54.966 | 43.616 | 18.432 | 0 | 0 | 56.674 | 29.511 | [5 empty] | 0 | 13.016 | 15 | 5.5964 | 5.2445 | 3.8172 | 3.5294 | 1.7151 | 30.6456
2006-03-12 | 20:38 | 0 | 15.714 | 0 | 4 | 1 | 56.563 | 56.944 | 43.427 | 43.499 | 34.708 | 25.897 | 3.434 | 1 | 0 | 58.402 | 54.898 | 43.709 | 18.407 | 0 | 0 | 56.629 | 29.56 | [5 empty] | 0 | 13.064 | 16 | 5.5964 | 5.2445 | 3.8172 | 3.5294 | 1.7151 | 30.6456
2006-03-12 | 20:39 | 0 | 15.684 | 0 | 4 | 0 | 56.467 | 56.916 | 43.47 | 43.377 | 34.797 | 26.012 | 3.429 | 1 | 0 | 58.372 | 54.845 | 43.633 | 18.399 | 0 | 0 | 56.622 | 29.553 | [5 empty] | 0 | 13.09 | 0 | 5.5979 | 5.2459 | 3.8172 | 3.5294 | 1.7164 | 30.6624
2006-03-12 | 20:40 | 0 | 15.661 | 0 | 3 | 0 | 56.446 | 56.893 | 43.47 | 43.401 | 34.916 | 25.916 | 3.534 | 1 | 0 | 58.352 | 54.847 | 43.683 | 18.379 | 0 | 0 | 56.581 | 29.651 | [5 empty] | 0 | 13.045 | 1 | 5.5673 | 5.2168 | 4.0366 | 3.75 | 1.4668 | 26.3465
2006-03-12 | 20:41 | 1 | 15.717 | 0 | 4 | 0 | 56.563 | 56.877 | 43.477 | 43.499 | 34.732 | 26.09 | 3.565 | 1 | 0 | 58.468 | 54.898 | 43.664 | 18.432 | 0 | 0 | 56.674 | 29.705 | [5 empty] | 15.717 | 13.064 | 2 | 5.5583 | 5.2082 | 4.0362 | 3.75 | 1.4582 | 26.2349
2006-03-12 | 20:42 | 0 | 15.739 | 0 | 3 | 0 | 56.405 | 56.898 | 43.429 | 43.499 | 34.287 | 26.188 | 3.287 | 1 | 0 | 58.445 | 54.852 | 43.664 | 18.384 | 0 | 0 | 56.674 | 29.729 | [5 empty] | 0 | 12.906 | 3 | 5.6392 | 5.2852 | 4.0395 | 3.75 | 1.5352 | 27.2229
2006-03-12 | 20:43 | 0 | 15.692 | 0 | 4 | 0 | 56.405 | 56.898 | 43.358 | 43.477 | 34.098 | 26.26 | 3.462 | 1 | 0 | 58.425 | 54.852 | 43.664 | 18.384 | 0 | 0 | 56.674 | 29.754 | [5 empty] | 0 | 12.928 | 4 | 5.5883 | 5.2367 | 4.0374 | 3.75 | 1.4867 | 26.6043
2006-03-12 | 20:44 | 0 | 15.717 | 0 | 3 | 0 | 56.293 | 56.809 | 43.217 | 43.336 | 34.122 | 25.995 | 3.591 | 1 | 0 | 58.356 | 54.807 | 43.688 | 18.409 | 0 | 0 | 56.631 | 29.778 | [5 empty] | 0 | 12.957 | 5 | 5.5507 | 5.201 | 4.0359 | 3.75 | 1.451 | 26.141
2006-03-12 | 20:45 | 1 | 15.636 | 0 | 4 | 0 | 56.357 | 56.67 | 43.071 | 43.284 | 34.304 | 26.181 | 3.509 | 1 | 0 | 58.397 | 54.894 | 43.635 | 18.402 | 0 | 0 | 56.604 | 29.773 | [5 empty] | 15.636 | 13.073 | 6 | 5.5746 | 5.2237 | 4.0369 | 3.75 | 1.4737 | 26.4362
2006-03-12 | 20:46 | 0 | 15.692 | 1 | 3 | 0 | 56.339 | 56.809 | 43.123 | 43.171 | 34.498 | 26.044 | 3.462 | 1 | 0 | 58.379 | 54.852 | 43.805 | 18.432 | 0 | 0 | 56.585 | 29.849 | [5 empty] | 0 | 13.168 | 7 | 5.5883 | 5.2367 | 4.0374 | 3.75 | 1.4867 | 26.6043
2006-03-12 | 20:47 | 0 | 15.687 | 0 | 4 | 0 | 56.312 | 56.715 | 43.071 | 43.142 | 34.352 | 26.039 | 3.305 | 1 | 0 | 58.374 | 54.8 | 43.728 | 18.402 | 0 | 0 | 56.535 | 29.869 | [5 empty] | 0 | 13.17 | 8 | 5.634 | 5.2802 | 4.0393 | 3.75 | 1.5302 | 27.1598
2006-03-12 | 20:48 | 0 | 15.734 | 0 | 4 | 0 | 56.243 | 56.738 | 42.929 | 43.095 | 34.282 | 26.134 | 3.457 | 2 | 0 | 58.352 | 54.8 | 43.659 | 18.402 | 0 | 0 | 56.624 | 29.844 | [5 empty] | 0 | 13.148 | 9 | 5.5897 | 5.2381 | 4.0375 | 3.75 | 1.4881 | 26.6221
2006-03-12 | 20:49 | 0 | 15.734 | 0 | 3 | 0 | 55.949 | 56.647 | 42.929 | 43.001 | 33.835 | 26.134 | 3.382 | 1 | 0 | 58.352 | 54.779 | 43.659 | 18.427 | 0 | 0 | 56.535 | 29.893 | [5 empty] | 0 | 12.948 | 10 | 5.6116 | 5.2589 | 4.0384 | 3.75 | 1.5089 | 26.8885
2006-03-12 | 20:50 | 1 | 15.739 | 0 | 4 | 0 | 55.977 | 56.451 | 42.958 | 43.03 | 33.582 | 26.115 | 3.514 | 1 | 0 | 58.333 | 54.807 | 43.712 | 18.457 | 0 | 0 | 56.517 | 29.969 | [5 empty] | 15.739 | 12.947 | 11 | 5.5731 | 5.2223 | 4.0368 | 3.75 | 1.4723 | 26.4183
2006-03-12 | 20:51 | 0 | 15.739 | 0 | 3 | 0 | 55.816 | 56.362 | 42.796 | 42.913 | 33.84 | 26.164 | 3.614 | 1 | 0 | 58.356 | 54.807 | 43.688 | 18.432 | 0 | 0 | 56.563 | 29.994 | [5 empty] | 0 | 12.903 | 12 | 5.544 | 5.1946 | 4.0357 | 3.75 | 1.4446 | 26.0578
2006-03-12 | 20:52 | 0 | 15.739 | 0 | 4 | 0 | 55.769 | 56.25 | 42.654 | 42.913 | 33.771 | 26.115 | 3.388 | 1 | 0 | 58.333 | 54.807 | 43.805 | 18.457 | 0 | 0 | 56.563 | 30.018 | [5 empty] | 0 | 12.856 | 13 | 5.6098 | 5.2572 | 4.0383 | 3.75 | 1.5072 | 26.8672
2006-03-12 | 20:53 | 0 | 15.835 | 0 | 4 | 0 | 55.627 | 56.312 | 42.602 | 42.788 | 33.553 | 26.085 | 3.23 | 1 | 0 | 58.329 | 54.709 | 43.683 | 18.354 | 0 | 0 | 56.558 | 30.014 | [5 empty] | 0 | 12.839 | 14 | 5.6558 | 5.3009 | 4.0402 | 3.75 | 1.5509 | 27.4219
2006-03-12 | 20:54 | 0 | 15.692 | 0 | 3 | 1 | 55.608 | 56.068 | 42.63 | 42.748 | 33.605 | 26.115 | 3.362 | 1 | 0 | 58.29 | 54.761 | 43.781 | 18.432 | 0 | 0 | 56.54 | 30.043 | [5 empty] | 0 | 12.86 | 15 | 5.6174 | 5.2644 | 4.0386 | 3.75 | 1.5144 | 26.9591
2006-03-12 | 20:55 | 1 | 15.734 | 0 | 4 | 0 | 55.559 | 56.086 | 42.53 | 42.647 | 33.787 | 26.11 | 3.282 | 1 | 0 | 58.306 | 54.686 | 43.659 | 18.379 | 0 | 0 | 56.469 | 30.038 | [5 empty] | 15.734 | 12.912 | 0 | 5.6407 | 5.2865 | 4.0396 | 3.75 | 1.5365 | 27.2404
2006-03-12 | 20:56 | 0 | 15.739 | 1 | 4 | 0 | 55.839 | 56.181 | 42.396 | 42.607 | 34.098 | 26.164 | 3.313 | 1 | 0 | 58.313 | 54.737 | 43.64 | 18.432 | 0 | 0 | 56.517 | 30.114 | [5 empty] | 0 | 13.232 | 1 | 5.6317 | 5.278 | 4.0392 | 3.75 | 1.528 | 27.1317
2006-03-12 | 20:57 | 0 | 15.764 | 0 | 3 | 0 | 55.977 | 56.362 | 42.372 | 42.559 | 34.897 | 26.115 | 3.261 | 1 | 0 | 58.267 | 54.714 | 43.688 | 18.409 | 0 | 0 | 56.54 | 30.114 | [5 empty] | 0 | 13.418 | 2 | 5.6468 | 5.2924 | 4.0398 | 3.75 | 1.5424 | 27.3138
2006-03-12 | 20:58 | 0 | 15.739 | 0 | 4 | 0 | 56.021 | 56.496 | 42.255 | 42.607 | 35.203 | 26.068 | 3.313 | 1 | 0 | 58.29 | 54.714 | 43.664 | 18.432 | 0 | 0 | 56.496 | 30.163 | [5 empty] | 0 | 13.414 | 3 | 5.6317 | 5.278 | 4.0392 | 3.75 | 1.528 | 27.1317
2006-03-12 | 20:59 | 1 | 15.709 | 0 | 4 | 0 | 55.949 | 56.49 | 42.248 | 42.389 | 34.916 | 26.304 | 3.408 | 2 | 0 | 58.24 | 54.756 | 43.776 | 18.379 | 0 | 0 | 56.423 | 30.134 | [5 empty] | 15.709 | 13.56 | 4 | 5.604 | 5.2517 | 4.0381 | 3.75 | 1.5017 | 26.7964
2006-03-12 | 21:00 | 0 | 15.749 | 0 | 4 | 0 | 55.984 | 56.483 | 42.286 | 42.451 | 34.648 | 26.245 | 3.473 | 1 | 0 | 58.254 | 54.656 | 43.649 | 18.417 | 0 | 0 | 56.371 | 30.173 | [5 empty] | 0 | 13.533 | 5 | 5.5851 | 5.2337 | 4.0373 | 3.75 | 1.4837 | 26.565
2006-03-12 | 21:01 | 0 | 15.749 | 0 | 3 | 0 | 55.755 | 56.391 | 42.145 | 42.31 | 34.177 | 26.22 | 3.346 | 1 | 0 | 58.254 | 54.677 | 43.743 | 18.417 | 0 | 0 | 56.348 | 30.197 | [5 empty] | 0 | 13.445 | 6 | 5.622 | 5.2688 | 4.0388 | 3.75 | 1.5188 | 27.0156
2006-03-12 | 21:02 | 0 | 15.694 | 0 | 4 | 0 | 55.613 | 56.209 | 42.116 | 42.305 | 33.845 | 26.215 | 3.393 | 1 | 0 | 58.226 | 54.649 | 43.693 | 18.364 | 0 | 0 | 56.252 | 30.19 | [5 empty] | 0 | 13.308 | 7 | 5.6084 | 5.2558 | 4.0383 | 3.75 | 1.5058 | 26.8495
2006-03-12 | 21:03 | 0 | 15.724 | 0 | 4 | 0 | 55.456 | 56.077 | 42.31 | 42.499 | 33.66 | 26.196 | 3.346 | 1 | 0 | 58.208 | 54.632 | 43.649 | 18.417 | 0 | 0 | 56.325 | 30.244 | [5 empty] | 0 | 12.957 | 8 | 5.622 | 5.2688 | 4.0388 | 3.75 | 1.5188 | 27.0156
2006-03-12 | 21:04 | 1 | 15.724 | 0 | 3 | 0 | 55.55 | 56.007 | 42.334 | 42.403 | 34.108 | 26.196 | 3.473 | 1 | 0 | 58.208 | 54.632 | 43.649 | 18.394 | 0 | 0 | 56.348 | 30.269 | [5 empty] | 15.724 | 13.147 | 9 | 5.5851 | 5.2337 | 4.0373 | 3.75 | 1.4837 | 26.565
2006-03-12 | 21:05 | 0 | 15.694 | 1 | 4 | 0 | 55.522 | 56.002 | 42.257 | 42.54 | 33.938 | 26.12 | 3.341 | 1 | 0 | 58.18 | 54.604 | 43.621 | 18.364 | 0 | 0 | 56.321 | 30.31 | [5 empty] | 0 | 12.982 | 10 | 5.6235 | 5.2702 | 4.0389 | 3.75 | 1.5202 | 27.0332
2006-03-12 | 21:06 | 0 | 15.724 | 0 | 4 | 0 | 55.435 | 55.984 | 42.334 | 42.475 | 34.108 | 26.22 | 3.473 | 1 | 0 | 58.208 | 54.632 | 43.649 | 18.417 | 0 | 0 | 56.325 | 30.364 | [5 empty] | 0 | 12.96 | 11 | 5.5851 | 5.2337 | 4.0373 | 3.75 | 1.4837 | 26.565
2006-03-12 | 21:07 | 0 | 15.671 | 0 | 3 | 0 | 55.522 | 55.911 | 42.164 | 42.446 | 34.031 | 26.191 | 3.315 | 2 | 0 | 58.18 | 54.604 | 43.738 | 18.339 | 0 | 0 | 56.275 | 30.335 | [5 empty] | 0 | 13.076 | 12 | 5.6311 | 5.2774 | 4.0392 | 3.75 | 1.5274 | 27.1246
2006-03-12 | 21:08 | 1 | 15.671 | 0 | 4 | 0 | 55.498 | 55.956 | 42.281 | 42.564 | 33.986 | 26.191 | 3.393 | 1 | 0 | 58.158 | 54.581 | 43.714 | 18.339 | 0 | 0 | 56.252 | 30.359 | [5 empty] | 15.671 | 12.934 | 13 | 5.6084 | 5.2558 | 4.0383 | 3.75 | 1.5058 | 26.8495
2006-03-12 | 21:09 | 0 | 15.694 | 0 | 4 | 0 | 55.566 | 55.865 | 42.257 | 42.446 | 34.314 | 26.095 | 3.519 | 1 | 0 | 58.158 | 54.581 | 43.738 | 18.339 | 0 | 0 | 56.275 | 30.384 | [5 empty] | 0 | 13.12 | 14 | 5.5717 | 5.2209 | 4.0368 | 3.75 | 1.4709 | 26.4004
2006-03-12 | 21:10 | 0 | 15.671 | 0 | 3 | 1 | 55.522 | 55.979 | 42.257 | 42.47 | 34.244 | 26.264 | 3.341 | 1 | 0 | 58.203 | 54.581 | 43.762 | 18.339 | 0 | 0 | 56.252 | 30.359 | [5 empty] | 0 | 13.052 | 15 | 5.6235 | 5.2702 | 4.0389 | 3.75 | 1.5202 | 27.0332
2006-03-12 | 21:11 | 0 | 15.694 | 0 | 4 | 0 | 55.475 | 55.888 | 42.164 | 42.516 | 33.938 | 26.12 | 3.367 | 1 | 0 | 58.158 | 54.581 | 43.693 | 18.364 | 0 | 0 | 56.186 | 30.408 | [5 empty] | 0 | 12.959 | 0 | 5.6159 | 5.263 | 4.0386 | 3.75 | 1.513 | 26.9415
2006-03-12 | 21:12 | 0 | 15.724 | 0 | 4 | 0 | 55.594 | 55.939 | 42.286 | 42.475 | 33.684 | 26.196 | 3.321 | 1 | 0 | 58.165 | 54.539 | 43.791 | 18.369 | 0 | 0 | 56.191 | 30.484 | [5 empty] | 0 | 13.119 | 1 | 5.6293 | 5.2757 | 4.0391 | 3.75 | 1.5257 | 27.1036
2006-03-12 | 21:13 | 1 | 15.719 | 0 | 4 | 0 | 55.407 | 56.002 | 42.398 | 42.398 | 33.515 | 26.144 | 3.467 | 1 | 0 | 58.158 | 54.534 | 43.714 | 18.339 | 0 | 0 | 56.186 | 30.479 | [5 empty] | 15.719 | 13.009 | 2 | 5.5868 | 5.2353 | 4.0374 | 3.75 | 1.4853 | 26.5865
2006-03-12 | 21:14 | 0 | 15.694 | 1 | 3 | 0 | 55.246 | 55.865 | 42.281 | 42.516 | 33.727 | 26.12 | 3.493 | 1 | 0 | 58.114 | 54.558 | 43.714 | 18.339 | 0 | 0 | 56.117 | 30.479 | [5 empty] | 0 | 12.73 | 3 | 5.5792 | 5.2281 | 4.0371 | 3.75 | 1.4781 | 26.4935
2006-03-12 | 21:15 | 0 | 15.694 | 0 | 4 | 0 | 55.223 | 55.75 | 42.305 | 42.54 | 33.491 | 26.095 | 3.416 | 1 | 0 | 58.137 | 54.49 | 43.786 | 18.364 | 0 | 0 | 56.163 | 30.528 | [5 empty] | 0 | 12.683 | 4 | 5.6017 | 5.2495 | 4.038 | 3.75 | 1.4995 | 26.768
2006-03-12 | 21:16 | 0 | 15.702 | 0 | 4 | 0 | 55.389 | 55.687 | 42.382 | 42.544 | 33.637 | 26.196 | 3.473 | 1 | 0 | 58.185 | 54.562 | 43.721 | 18.417 | 0 | 0 | 56.257 | 30.533 | [5 empty] | 0 | 12.845 | 5 | 5.5851 | 5.2337 | 4.0373 | 3.75 | 1.4837 | 26.565
2006-03-12 | 21:17 | 1 | 15.694 | 0 | 4 | 0 | 55.155 | 55.75 | 42.329 | 42.564 | 33.562 | 26.071 | 3.315 | 2 | 0 | 58.091 | 54.49 | 43.786 | 18.339 | 0 | 0 | 56.163 | 30.553 | [5 empty] | 15.694 | 12.591 | 6 | 5.6311 | 5.2774 | 4.0392 | 3.75 | 1.5274 | 27.1246
2006-03-12 | 21:18 | 0 | 15.719 | 0 | 3 | 0 | 55.246 | 55.683 | 42.47 | 42.492 | 33.538 | 26.071 | 3.315 | 1 | 0 | 58.114 | 54.49 | 43.714 | 18.314 | 0 | 0 | 56.186 | 30.578 | [5 empty] | 0 | 12.754 | 7 | 5.6311 | 5.2774 | 4.0392 | 3.75 | 1.5274 | 27.1246
2006-03-12 | 21:19 | 0 | 15.694 | 0 | 4 | 0 | 55.27 | 55.82 | 42.422 | 42.564 | 33.938 | 26.071 | 3.493 | 1 | 0 | 58.114 | 54.49 | 43.81 | 18.364 | 0 | 0 | 56.209 | 30.624 | [5 empty] | 0 | 12.706 | 8 | 5.5792 | 5.2281 | 4.0371 | 3.75 | 1.4781 | 26.4935
2006-03-12 | 21:20 | 0 | 15.719 | 0 | 4 | 0 | 55.384 | 55.727 | 42.446 | 42.492 | 34.668 | 25.951 | 3.367 | 1 | 0 | 58.091 | 54.443 | 43.738 | 18.314 | 0 | 0 | 56.209 | 30.624 | [5 empty] | 0 | 12.892 | 9 | 5.6159 | 5.263 | 4.0386 | 3.75 | 1.513 | 26.9415
2006-03-12 | 21:21 | 0 | 15.671 | 0 | 4 | 0 | 55.27 | 55.797 | 42.329 | 42.492 | 35.043 | 25.902 | 3.519 | 1 | 0 | 58.069 | 54.42 | 43.738 | 18.314 | 0 | 0 | 56.186 | 30.624 | [5 empty] | 0 | 12.778 | 10 | 5.5717 | 5.2209 | 4.0368 | 3.75 | 1.4709 | 26.4004
2006-03-12 | 21:22 | 1 | 15.724 | 0 | 3 | 0 | 55.298 | 55.825 | 42.403 | 42.544 | 35.447 | 25.955 | 3.447 | 1 | 0 | 58.119 | 54.495 | 43.791 | 18.344 | 0 | 0 | 56.28 | 30.678 | [5 empty] | 15.724 | 12.754 | 11 | 5.5926 | 5.2409 | 4.0376 | 3.75 | 1.4909 | 26.6578
2006-03-12 | 21:23 | 0 | 15.694 | 1 | 4 | 0 | 55.246 | 55.75 | 42.375 | 42.729 | 35.254 | 26.046 | 3.493 | 1 | 0 | 58.069 | 54.49 | 43.855 | 18.339 | 0 | 0 | 56.252 | 30.624 | [5 empty] | 0 | 12.517 | 12 | 5.5792 | 5.2281 | 4.0371 | 3.75 | 1.4781 | 26.4935
2006-03-12 | 21:24 | 0 | 15.719 | 0 | 4 | 0 | 55.384 | 55.636 | 42.398 | 42.681 | 34.526 | 25.902 | 3.568 | 1 | 0 | 58.069 | 54.42 | 43.903 | 18.339 | 0 | 0 | 56.364 | 30.722 | [5 empty] | 0 | 12.703 | 13 | 5.5574 | 5.2074 | 4.0362 | 3.75 | 1.4574 | 26.2241
2006-03-12 | 21:25 | 0 | 15.694 | 0 | 4 | 0 | 55.246 | 55.82 | 42.47 | 42.564 | 34.22 | 26.046 | 3.594 | 1 | 0 | 58.069 | 54.443 | 43.762 | 18.364 | 0 | 0 | 56.252 | 30.673 | [5 empty] | 0 | 12.682 | 14 | 5.5498 | 5.2002 | 4.0359 | 3.75 | 1.4502 | 26.1302
2006-03-12 | 21:26 | 1 | 15.724 | 0 | 4 | 1 | 55.412 | 55.802 | 42.592 | 42.64 | 33.967 | 26.054 | 3.524 | 2 | 0 | 58.096 | 54.471 | 43.862 | 18.344 | 0 | 0 | 56.257 | 30.727 | [5 empty] | 15.724 | 12.772 | 15 | 5.5702 | 5.2196 | 4.0367 | 3.75 | 1.4696 | 26.3824
2006-03-12 | 21:27 | 0 | 15.694 | 0 | 3 | 0 | 55.704 | 55.888 | 42.705 | 42.681 | 33.914 | 26.095 | 3.594 | 1 | 0 | 58.023 | 54.42 | 43.762 | 18.339 | 0 | 0 | 56.186 | 30.698 | [5 empty] | 0 | 13.023 | 0 | 5.5498 | 5.2002 | 4.0359 | 3.75 | 1.4502 | 26.1302
2006-03-12 | 21:28 | 0 | 15.694 | 0 | 4 | 0 | 55.704 | 56.209 | 42.657 | 42.729 | 33.797 | 26.095 | 3.493 | 1 | 0 | 58.046 | 54.397 | 43.903 | 18.364 | 0 | 0 | 56.093 | 30.698 | [5 empty] | 0 | 12.975 | 1 | 5.5792 | 5.2281 | 4.0371 | 3.75 | 1.4781 | 26.4935
2006-03-12 | 21:29 | 0 | 15.719 | 0 | 4 | 0 | 55.774 | 56.186 | 42.657 | 42.939 | 33.68 | 26.046 | 3.619 | 1 | 0 | 58.069 | 54.376 | 43.975 | 18.314 | 0 | 0 | 56.186 | 30.744 | [5 empty] | 0 | 12.835 | 2 | 5.5425 | 5.1933 | 4.0356 | 3.75 | 1.4433 | 26.0397
2006-03-12 | 21:30 | 0 | 15.719 | 0 | 4 | 0 | 55.683 | 56.117 | 42.752 | 42.894 | 33.773 | 26 | 3.519 | 1 | 0 | 58.023 | 54.352 | 43.834 | 18.339 | 0 | 0 | 56.117 | 30.744 | [5 empty] | 0 | 12.789 | 3 | 5.5717 | 5.2209 | 4.0368 | 3.75 | 1.4709 | 26.4004
2006-03-12 | 21:31 | 1 | 15.719 | 0 | 3 | 0 | 55.613 | 56.072 | 42.87 | 42.915 | 33.656 | 26.095 | 3.493 | 1 | 0 | 58.023 | 54.352 | 43.855 | 18.314 | 0 | 0 | 56.14 | 30.818 | [5 empty] | 15.719 | 12.698 | 4 | 5.5792 | 5.2281 | 4.0371 | 3.75 | 1.4781 | 26.4935
2006-03-12 | 21:32 | 0 | 15.694 | 1 | 4 | 0 | 55.566 | 56.026 | 42.963 | 43.032 | 33.445 | 26.046 | 3.467 | 1 | 0 | 58.023 | 54.329 | 43.951 | 18.339 | 0 | 0 | 56.049 | 30.769 | [5 empty] | 0 | 12.534 | 5 | 5.5868 | 5.2353 | 4.0374 | 3.75 | 1.4853 | 26.5865
2006-03-12 | 21:33 | 0 | 15.719 | 0 | 4 | 0 | 55.613 | 56.117 | 43.032 | 43.104 | 33.232 | 26.024 | 3.568 | 1 | 0 | 58.023 | 54.329 | 43.975 | 18.339 | 0 | 0 | 55.979 | 30.793 | [5 empty] | 0 | 12.509 | 6 | 5.5574 | 5.2074 | 4.0362 | 3.75 | 1.4574 | 26.2241
2006-03-12 | 21:34 | 0 | 15.684 | 0 | 4 | 0 | 55.65 | 56.084 | 42.999 | 43.071 | 33.505 | 25.965 | 3.431 | 1 | 0 | 57.991 | 54.296 | 43.8 | 18.304 | 0 | 0 | 55.993 | 30.759 | [5 empty] | 0 | 12.579 | 7 | 5.5973 | 5.2453 | 4.0378 | 3.75 | 1.4953 | 26.7147
2006-03-12 | 21:35 | 1 | 15.719 | 0 | 3 | 0 | 55.704 | 56.14 | 43.011 | 43.128 | 34.455 | 25.975 | 3.594 | 1 | 0 | 58.002 | 54.306 | 43.855 | 18.339 | 0 | 0 | 56.002 | 30.818 | [5 empty] | 15.719 | 12.576 | 8 | 5.5498 | 5.2002 | 4.0359 | 3.75 | 1.4502 | 26.1302
2006-03-12 | 21:36 | 0 | 15.694 | 0 | 4 | 0 | 55.704 | 56.163 | 43.173 | 43.221 | 34.407 | 26 | 3.519 | 1 | 0 | 57.98 | 54.282 | 43.879 | 18.364 | 0 | 0 | 56.049 | 30.842 | [5 empty] | 0 | 12.483 | 9 | 5.5717 | 5.2209 | 4.0368 | 3.75 | 1.4709 | 26.4004
2006-03-12 | 21:37 | 0 | 15.694 | 0 | 4 | 0 | 55.979 | 56.209 | 43.08 | 43.269 | 34.785 | 25.951 | 3.619 | 2 | 0 | 57.957 | 54.259 | 43.951 | 18.339 | 0 | 0 | 56.026 | 30.818 | [5 empty] | 0 | 12.71 | 10 | 5.5425 | 5.1933 | 4.0356 | 3.75 | 1.4433 | 26.0397
2006-03-12 | 21:38 | 0 | 15.671 | 0 | 3 | 0 | 56.14 | 56.567 | 43.173 | 43.269 | 34.809 | 26.024 | 3.645 | 1 | 0 | 57.98 | 54.282 | 43.903 | 18.364 | 0 | 0 | 55.979 | 30.818 | [5 empty] | 0 | 12.871 | 11 | 5.535 | 5.1861 | 4.0353 | 3.75 | 1.4361 | 25.9453
2006-03-12 | 21:39 | 0 | 15.671 | 0 | 4 | 0 | 56.14 | 56.61 | 43.152 | 43.293 | 34.668 | 25.951 | 3.594 | 1 | 0 | 57.98 | 54.376 | 43.996 | 18.412 | 0 | 0 | 56.026 | 30.889 | [5 empty] | 0 | 12.847 | 12 | 5.5498 | 5.2002 | 4.0359 | 3.75 | 1.4502 | 26.1302
2006-03-12 | 21:40 | 1 | 15.646 | 0 | 4 | 0 | 55.911 | 56.633 | 43.104 | 43.41 | 34.29 | 25.975 | 3.594 | 1 | 0 | 57.957 | 54.238 | 43.927 | 18.339 | 0 | 0 | 56.002 | 30.938 | [5 empty] | 15.646 | 12.501 | 13 | 5.5498 | 5.2002 | 4.0359 | 3.75 | 1.4502 | 26.1302
2006-03-12 | 21:41 | 0 | 15.611 | 0 | 4 | 0 | 55.764 | 56.378 | 43.212 | 43.26 | 34.328 | 25.892 | 3.509 | 1 | 0 | 57.948 | 54.226 | 43.87 | 18.278 | 0 | 0 | 55.993 | 30.879 | [5 empty] | 0 | 12.504 | 14 | 5.5746 | 5.2237 | 4.0369 | 3.75 | 1.4737 | 26.4362
2006-03-12 | 21:42 | 0 | 15.694 | 1 | 3 | 1 | 55.841 | 56.343 | 43.245 | 43.339 | 34.29 | 26 | 3.519 | 1 | 0 | 58.002 | 54.282 | 43.903 | 18.339 | 0 | 0 | 55.979 | 30.962 | [5 empty] | 0 | 12.502 | 15 | 5.5717 | 5.2209 | 4.0368 | 3.75 | 1.4709 | 26.4004
2006-03-12 | 21:43 | 0 | 15.694 | 0 | 4 | 0 | 55.75 | 56.343 | 43.41 | 43.362 | 34.29 | 26.046 | 3.619 | 1 | 0 | 57.98 | 54.238 | 43.951 | 18.339 | 0 | 0 | 55.956 | 30.913 | [5 empty] | 0 | 12.388 | 0 | 5.5425 | 5.1933 | 4.0356 | 3.75 | 1.4433 | 26.0397
2006-03-12 | 21:44 | 0 | 15.719 | 0 | 4 | 0 | 55.797 | 56.229 | 43.527 | 43.434 | 34.455 | 25.975 | 3.416 | 1 | 0 | 57.98 | 54.238 | 43.951 | 18.314 | 0 | 0 | 55.911 | 30.938 | [5 empty] | 0 | 12.363 | 1 | 5.6017 | 5.2495 | 3.8174 | 3.5294 | 1.72 | 30.7059
2006-03-12 | 21:45 | 1 | 15.719 | 0 | 4 | 0 | 55.82 | 56.298 | 43.504 | 43.48 | 34.29 | 25.951 | 3.645 | 1 | 0 | 57.98 | 54.215 | 44.02 | 18.339 | 0 | 0 | 55.888 | 30.987 | [5 empty] | 15.719 | 12.34 | 2 | 5.535 | 5.1861 | 3.8147 | 3.5294 | 1.6567 | 29.9306
2006-03-12 | 21:46 | 0 | 15.719 | 0 | 3 | 0 | 55.841 | 56.275 | 43.621 | 43.504 | 34.668 | 26.071 | 3.645 | 1 | 0 | 58.002 | 54.215 | 44.044 | 18.314 | 0 | 0 | 55.935 | 30.962 | [5 empty] | 0 | 12.337 | 3 | 5.535 | 5.1861 | 3.8147 | 3.5294 | 1.6567 | 29.9306
2006-03-12 | 21:47 | 0 | 15.719 | 0 | 4 | 0 | 55.82 | 56.321 | 43.48 | 43.597 | 35.019 | 25.902 | 3.594 | 1 | 0 | 57.957 | 54.168 | 44.02 | 18.314 | 0 | 0 | 55.956 | 30.938 | [5 empty] | 0 | 12.223 | 4 | 5.5498 | 5.2002 | 3.8153 | 3.5294 | 1.6708 | 30.1049
2006-03-12 | 21:48 | 0 | 15.671 | 0 | 4 | 0 | 55.774 | 56.275 | 43.386 | 43.527 | 35.208 | 25.975 | 3.619 | 1 | 0 | 57.957 | 54.191 | 44.02 | 18.314 | 0 | 0 | 55.956 | 30.962 | [5 empty] | 0 | 12.247 | 5 | 5.5425 | 5.1933 | 3.815 | 3.5294 | 1.6638 | 30.0196
2006-03-12 | 21:49 | 1 | 15.671 | 0 | 4 | 0 | 55.797 | 56.243 | 43.305 | 43.47 | 35.127 | 25.916 | 3.558 | 1 | 0 | 57.902 | 54.226 | 44.035 | 18.278 | 0 | 0 | 55.855 | 30.928 | [5 empty] | 15.671 | 12.327 | 6 | 5.5603 | 5.2101 | 3.8157 | 3.5294 | 1.6807 | 30.2273
2006-03-12 | 21:50 | 0 | 15.694 | 0 | 3 | 0 | 55.774 | 56.321 | 43.41 | 43.456 | 35.301 | 26.144 | 3.568 | 2 | 0 | 57.957 | 54.191 | 44.044 | 18.314 | 0 | 0 | 55.911 | 30.987 | [5 empty] | 0 | 12.318 | 7 | 5.5574 | 5.2074 | 3.8156 | 3.5294 | 1.678 | 30.1934
2006-03-12 | 21:51 | 0 | 15.621 | 1 | 4 | 0 | 55.683 | 56.321 | 43.434 | 43.41 | 35.16 | 26.071 | 3.568 | 1 | 0 | 57.934 | 54.215 | 43.975 | 18.314 | 0 | 0 | 55.911 | 30.962 | [5 empty] | 0 | 12.273 | 8 | 5.5574 | 5.2074 | 3.8156 | 3.5294 | 1.678 | 30.1934
2006-03-12 | 21:52 | 0 | 15.659 | 0 | 4 | 0 | 55.946 | 56.197 | 43.329 | 43.377 | 35.033 | 25.99 | 3.684 | 1 | 0 | 57.902 | 54.182 | 44.104 | 18.278 | 0 | 0 | 55.879 | 30.975 | [5 empty] | 0 | 12.569 | 9 | 5.5236 | 5.1753 | 3.8142 | 3.5294 | 1.6459 | 29.7967
2006-03-12 | 21:53 | 0 | 15.671 | 0 | 4 | 0 | 55.841 | 56.298 | 43.362 | 43.386 | 34.713 | 26.071 | 3.645 | 1 | 0 | 57.911 | 54.191 | 44.092 | 18.289 | 0 | 0 | 55.888 | 31.009 | [5 empty] | 0 | 12.455 | 10 | 5.535 | 5.1861 | 3.8147 | 3.5294 | 1.6567 | 29.9306
2006-03-12 | 21:54 | 1 | 15.636 | 0 | 3 | 0 | 55.694 | 56.22 | 43.353 | 43.377 | 34.656 | 25.965 | 3.509 | 1 | 0 | 57.902 | 54.112 | 44.059 | 18.253 | 0 | 0 | 55.879 | 31.048 | [5 empty] | 15.636 | 12.317 | 11 | 5.5746 | 5.2237 | 3.8163 | 3.5294 | 1.6943 | 30.3933
2006-03-12 | 21:55 | 0 | 15.636 | 0 | 4 | 0 | 55.671 | 56.154 | 43.281 | 43.401 | 35.01 | 25.941 | 3.635 | 1 | 0 | 57.879 | 54.112 | 44.059 | 18.278 | 0 | 0 | 55.832 | 31.048 | [5 empty] | 0 | 12.27 | 12 | 5.5379 | 5.1888 | 3.8148 | 3.5294 | 1.6594 | 29.9649
2006-03-12 | 21:56 | 0 | 15.671 | 0 | 4 | 0 | 55.727 | 56.117 | 43.456 | 43.386 | 34.785 | 26.144 | 3.671 | 1 | 0 | 57.934 | 54.145 | 44.02 | 18.289 | 0 | 0 | 55.797 | 31.083 | [5 empty] | 0 | 12.341 | 13 | 5.5274 | 5.1789 | 3.8144 | 3.5294 | 1.6495 | 29.8414
2006-03-12 | 21:57 | 0 | 15.671 | 0 | 4 | 0 | 55.75 | 56.163 | 43.434 | 43.41 | 34.479 | 26.046 | 3.545 | 1 | 0 | 57.911 | 54.168 | 44.068 | 18.339 | 0 | 0 | 55.774 | 31.107 | [5 empty] | 0 | 12.34 | 14 | 5.5641 | 5.2137 | 3.8159 | 3.5294 | 1.6843 | 30.2714
2006-03-12 | 21:58 | 0 | 15.694 | 0 | 4 | 0 | 55.704 | 56.163 | 43.315 | 43.456 | 34.431 | 26.046 | 3.545 | 1 | 0 | 57.911 | 54.121 | 44.114 | 18.289 | 0 | 0 | 55.797 | 31.083 | [5 empty] | 0 | 12.248 | 15 | 5.5641 | 5.2137 | 3.8159 | 3.5294 | 1.6843 | 30.2714
2006-03-12 | 21:59 | 1 | 15.659 | 0 | 3 | 1 | 55.788 | 56.154 | 43.446 | 43.401 | 34.469 | 26.012 | 3.431 | 1 | 0 | 57.836 | 54.133 | 44.128 | 18.304 | 0 | 0 | 55.715 | 31.07 | [5 empty] | 15.659 | 12.387 | 16 | 5.5973 | 5.2453 | 3.8172 | 3.5294 | 1.7159 | 30.6557
2006-03-12 | 22:00 | 0 | 15.661 | 1 | 4 | 0 | 55.694 | 56.266 | 43.329 | 43.353 | 34.541 | 25.99 | 3.333 | 1 | 0 | 57.859 | 54.091 | 44.152 | 18.306 | 0 | 0 | 55.694 | 31.073 | [5 empty] | 0 | 12.341 | 0 | 5.6258 | 5.2724 | 3.8184 | 3.5294 | 1.743 | 30.9823
2006-03-12 | 22:01 | 0 | 15.697 | 0 | 4 | 0 | 55.774 | 56.364 | 43.41 | 43.434 | 34.574 | 26.218 | 3.596 | 1 | 0 | 57.891 | 54.1 | 44.068 | 18.291 | 0 | 0 | 55.82 | 31.107 | [5 empty] | 0 | 12.34 | 1 | 5.5492 | 5.1996 | 4.0359 | 3.75 | 1.4496 | 26.123
2006-03-12 | 22:02 | 0 | 15.722 | 0 | 4 | 0 | 55.75 | 56.14 | 43.434 | 43.41 | 34.457 | 26.144 | 3.547 | 1 | 0 | 57.868 | 54.1 | 44.068 | 18.291 | 0 | 0 | 55.797 | 31.156 | [5 empty] | 0 | 12.34 | 2 | 5.5635 | 5.2132 | 4.0364 | 3.75 | 1.4632 | 26.2998
2006-03-12 | 22:03 | 1 | 15.661 | 0 | 4 | 0 | 55.718 | 56.266 | 43.353 | 43.377 | 34.376 | 26.159 | 3.637 | 1 | 0 | 57.813 | 54.091 | 44.035 | 18.281 | 0 | 0 | 55.764 | 31.097 | [5 empty] | 15.661 | 12.341 | 3 | 5.5373 | 5.1883 | 4.0354 | 3.75 | 1.4383 | 25.9743
2006-03-12 | 22:04 | 0 | 15.661 | 0 | 3 | 0 | 55.718 | 56.177 | 43.353 | 43.401 | 34.775 | 26.11 | 3.46 | 2 | 0 | 57.813 | 54.021 | 44.106 | 18.331 | 0 | 0 | 55.741 | 31.146 | [5 empty] | 0 | 12.317 | 4 | 5.5888 | 5.2373 | 4.0375 | 3.75 | 1.4873 | 26.6114
2006-03-12 | 22:05 | 0 | 15.661 | 0 | 4 | 0 | 55.788 | 56.154 | 43.449 | 43.377 | 34.727 | 26.159 | 3.511 | 1 | 0 | 57.836 | 54.044 | 44.082 | 18.331 | 0 | 0 | 55.764 | 31.146 | [5 empty] | 0 | 12.411 | 5 | 5.574 | 5.2232 | 4.0369 | 3.75 | 1.4732 | 26.4291
2006-03-12 | 22:06 | 0 | 15.661 | 0 | 4 | 0 | 55.673 | 56.243 | 43.449 | 43.449 | 34.328 | 26.304 | 3.485 | 1 | 0 | 57.859 | 54.044 | 44.035 | 18.331 | 0 | 0 | 55.788 | 31.122 | [5 empty] | 0 | 12.224 | 6 | 5.5816 | 5.2304 | 4.0372 | 3.75 | 1.4804 | 26.5222
2006-03-12 | 22:07 | 0 | 15.661 | 0 | 4 | 0 | 55.694 | 56.2 | 43.449 | 43.425 | 34.658 | 26.11 | 3.586 | 1 | 0 | 57.813 | 54.021 | 44.176 | 18.281 | 0 | 0 | 55.741 | 31.146 | [5 empty] | 0 | 12.269 | 7 | 5.5522 | 5.2024 | 4.036 | 3.75 | 1.4524 | 26.1591
2006-03-12 | 22:08 | 1 | 15.656 | 0 | 4 | 0 | 55.713 | 56.126 | 43.396 | 43.396 | 34.864 | 26.105 | 3.581 | 1 | 0 | 57.809 | 53.993 | 44.102 | 18.301 | 0 | 0 | 55.713 | 31.141 | [5 empty] | 15.656 | 12.317 | 8 | 5.5536 | 5.2038 | 4.036 | 3.75 | 1.4538 | 26.1772
2006-03-12 | 22:09 | 0 | 15.712 | 1 | 3 | 0 | 55.603 | 56.154 | 43.329 | 43.425 | 34.94 | 26.233 | 3.586 | 1 | 0 | 57.813 | 53.974 | 44.106 | 18.331 | 0 | 0 | 55.694 | 31.146 | [5 empty] | 0 | 12.178 | 9 | 5.5522 | 5.2024 | 4.036 | 3.75 | 1.4524 | 26.1591
2006-03-12 | 22:10 | 0 | 15.656 | 0 | 4 | 0 | 55.484 | 56.035 | 43.396 | 43.396 | 34.723 | 26.154 | 3.581 | 1 | 0 | 57.809 | 53.993 | 44.171 | 18.324 | 0 | 0 | 55.69 | 31.166 | [5 empty] | 0 | 12.088 | 10 | 5.5536 | 5.2038 | 4.036 | 3.75 | 1.4538 | 26.1772
2006-03-12 | 22:11 | 0 | 15.656 | 0 | 4 | 0 | 55.232 | 55.874 | 43.066 | 43.583 | 34.888 | 26.225 | 3.429 | 1 | 0 | 57.809 | 53.946 | 44.102 | 18.301 | 0 | 0 | 55.713 | 31.166 | [5 empty] | 0 | 11.649 | 11 | 5.5979 | 5.2459 | 4.0378 | 3.75 | 1.4959 | 26.7218
2006-03-12 | 22:12 | 1 | 15.661 | 0 | 4 | 0 | 55.351 | 55.694 | 42.53 | 42.953 | 34.892 | 26.159 | 3.46 | 1 | 0 | 57.813 | 53.998 | 44.082 | 18.354 | 0 | 0 | 55.764 | 31.171 | [5 empty] | 15.661 | 12.398 | 12 | 5.5888 | 5.2373 | 4.0375 | 3.75 | 1.4873 | 26.6114
2006-03-12 | 22:13 | 0 | 15.687 | 0 | 5 | 0 | 55.26 | 55.902 | 42.32 | 42.695 | 35.457 | 26.328 | 3.46 | 1 | 0 | 57.831 | 53.946 | 44.078 | 18.301 | 0 | 0 | 55.713 | 31.188 | [5 empty] | 0 | 12.565 | 13 | 5.5888 | 5.2373 | 4.0375 | 3.75 | 1.4873 | 26.6114
2006-03-12 | 22:14 | 0 | 15.661 | 0 | 4 | 0 | 55.419 | 55.788 | 42.32 | 42.53 | 35.974 | 26.304 | 3.411 | 2 | 0 | 57.836 | 53.998 | 44.059 | 18.354 | 0 | 0 | 55.741 | 31.195 | [5 empty] | 0 | 12.889 | 14 | 5.6031 | 5.2508 | 4.0381 | 3.75 | 1.5008 | 26.7857
2006-03-12 | 22:15 | 0 | 15.712 | 0 | 4 | 1 | 55.557 | 55.925 | 42.25 | 42.65 | 36.069 | 26.184 | 3.663 | 1 | 0 | 57.79 | 53.953 | 44.152 | 18.306 | 0 | 0 | 55.741 | 31.217 | [5 empty] | 0 | 12.907 | 15 | 5.5297 | 5.1811 | 4.0351 | 3.75 | 1.4311 | 25.8798
2006-03-12 | 22:16 | 0 | 15.656 | 0 | 4 | 0 | 55.804 | 56.103 | 42.291 | 42.549 | 36.344 | 26.081 | 3.607 | 1 | 0 | 57.717 | 53.946 | 44.102 | 18.301 | 0 | 0 | 55.645 | 31.166 | [5 empty] | 0 | 13.255 | 0 | 5.546 | 5.1966 | 4.0357 | 3.75 | 1.4466 | 26.0832
2006-03-12 | 22:17 | 1 | 15.687 | 0 | 4 | 0 | 55.718 | 56.401 | 42.296 | 42.53 | 36.115 | 26.159 | 3.586 | 1 | 0 | 57.767 | 53.93 | 44.13 | 18.331 | 0 | 0 | 55.65 | 31.217 | [5 empty] | 15.687 | 13.188 | 1 | 5.5522 | 5.2024 | 4.286 | 4 | 1.2024 | 21.6564
2006-03-12 | 22:18 | 0 | 15.687 | 0 | 4 | 0 | 55.764 | 56.22 | 42.343 | 42.671 | 35.974 | 26.11 | 3.537 | 1 | 0 | 57.767 | 53.907 | 44.13 | 18.306 | 0 | 0 | 55.627 | 31.217 | [5 empty] | 0 | 13.093 | 2 | 5.5664 | 5.216 | 4.2866 | 4 | 1.216 | 21.8445
2006-03-12 | 22:19 | 0 | 15.656 | 1 | 4 | 0 | 55.69 | 56.172 | 42.315 | 42.597 | 35.758 | 26.034 | 3.529 | 1 | 0 | 57.763 | 53.925 | 44.054 | 18.276 | 0 | 0 | 55.624 | 31.191 | [5 empty] | 0 | 13.093 | 3 | 5.5688 | 5.2182 | 4.2867 | 4 | 1.2182 | 21.8751
2006-03-12 | 22:20 | 0 | 15.654 | 0 | 4 | 0 | 55.76 | 56.126 | 42.525 | 42.595 | 35.897 | 26.127 | 3.375 | 1 | 0 | 57.809 | 53.993 | 44.123 | 18.321 | 0 | 0 | 55.575 | 31.164 | [5 empty] | 0 | 13.165 | 4 | 5.6136 | 5.2608 | 4.2885 | 4 | 1.2608 | 22.4597
2006-03-12 | 22:21 | 1 | 15.654 | 0 | 4 | 0 | 55.643 | 56.396 | 42.501 | 42.666 | 35.804 | 25.936 | 3.501 | 1 | 0 | 57.717 | 53.879 | 44.171 | 18.273 | 0 | 0 | 55.529 | 31.164 | [5 empty] | 15.654 | 12.977 | 5 | 5.5769 | 5.2259 | 4.287 | 4 | 1.2259 | 21.9821
2006-03-12 | 22:22 | 0 | 15.709 | 0 | 4 | 0 | 55.694 | 56.177 | 42.578 | 42.764 | 35.643 | 25.965 | 3.532 | 2 | 0 | 57.724 | 53.907 | 44.08 | 18.329 | 0 | 0 | 55.603 | 31.193 | [5 empty] | 0 | 12.93 | 6 | 5.5679 | 5.2173 | 4.2866 | 4 | 1.2173 | 21.8637
2006-03-12 | 22:23 | 0 | 15.679 | 0 | 4 | 0 | 55.666 | 56.15 | 42.595 | 42.784 | 35.687 | 25.911 | 3.552 | 1 | 0 | 57.717 | 53.879 | 44.075 | 18.273 | 0 | 0 | 55.575 | 31.213 | [5 empty] | 0 | 12.882 | 7 | 5.5621 | 5.2118 | 4.2864 | 4 | 1.2118 | 21.787
2006-03-12 | 22:24 | 0 | 15.684 | 0 | 4 | 0 | 55.557 | 56.22 | 42.647 | 42.86 | 35.62 | 26.012 | 3.431 | 1 | 0 | 57.767 | 53.93 | 44.2 | 18.351 | 0 | 0 | 55.627 | 31.217 | [5 empty] | 0 | 12.697 | 8 | 5.5973 | 5.2453 | 4.2878 | 4 | 1.2453 | 22.2482
2006-03-12 | 22:25 | 1 | 15.659 | 0 | 4 | 0 | 55.58 | 56.016 | 42.719 | 42.977 | 35.55 | 26.012 | 3.509 | 1 | 0 | 57.724 | 53.883 | 44.104 | 18.329 | 0 | 0 | 55.58 | 31.217 | [5 empty] | 15.659 | 12.603 | 9 | 5.5746 | 5.2237 | 4.2869 | 4 | 1.2237 | 21.9516
2006-03-12 | 22:26 | 0 | 15.654 | 0 | 4 | 0 | 55.575 | 56.056 | 42.831 | 42.949 | 35.474 | 25.96 | 3.478 | 1 | 0 | 57.717 | 53.879 | 44.03 | 18.273 | 0 | 0 | 55.599 | 31.164 | [5 empty] | 0 | 12.626 | 10 | 5.5836 | 5.2323 | 4.2873 | 4 | 1.2323 | 22.0698
2006-03-12 | 22:27 | 0 | 15.629 | 0 | 4 | 0 | 55.622 | 56.056 | 42.853 | 43.042 | 35.615 | 25.862 | 3.501 | 1 | 0 | 57.674 | 53.855 | 44.123 | 18.273 | 0 | 0 | 55.552 | 31.213 | [5 empty] | 0 | 12.58 | 11 | 5.5769 | 5.2259 | 4.287 | 4 | 1.2259 | 21.9821
2006-03-12 | 22:28 | 0 | 15.606 | 1 | 4 | 0 | 55.505 | 56.033 | 42.925 | 42.994 | 35.615 | 25.96 | 3.578 | 1 | 0 | 57.717 | 53.832 | 44.03 | 18.248 | 0 | 0 | 55.622 | 31.188 | [5 empty] | 0 | 12.511 | 12 | 5.5545 | 5.2046 | 4.2861 | 4 | 1.2046 | 21.6871
2006-03-12 | 22:29 | 1 | 15.684 | 0 | 4 | 0 | 55.466 | 56.131 | 42.953 | 43.023 | 36.043 | 25.892 | 3.558 | 1 | 0 | 57.724 | 53.816 | 44.176 | 18.304 | 0 | 0 | 55.603 | 31.217 | [5 empty] | 15.684 | 12.443 | 13 | 5.5603 | 5.2101 | 4.2863 | 4 | 1.2101 | 21.764
2006-03-12 | 22:30 | 0 | 15.659 | 0 | 4 | 1 | 55.466 | 56.016 | 42.906 | 43.047 | 35.974 | 25.965 | 3.558 | 1 | 0 | 57.678 | 53.837 | 44.059 | 18.278 | 0 | 0 | 55.58 | 31.242 | [5 empty] | 0 | 12.419 | 14 | 5.5603 | 5.2101 | 4.2863 | 4 | 1.2101 | 21.764
2006-03-12 | 22:31 | 0 | 15.629 | 0 | 4 | 0 | 55.347 | 55.918 | 42.949 | 43.042 | 35.545 | 25.838 | 3.501 | 1 | 0 | 57.651 | 53.787 | 44.192 | 18.248 | 0 | 0 | 55.575 | 31.235 | [5 empty] | 0 | 12.305 | 0 | 5.5769 | 5.2259 | 4.287 | 4 | 1.2259 | 21.9821
2006-03-12 | 22:32 | 0 | 15.636 | 0 | 4 | 0 | 55.512 | 55.923 | 43.095 | 43.212 | 35.502 | 25.796 | 3.509 | 1 | 0 | 57.633 | 53.792 | 44.104 | 18.278 | 0 | 0 | 55.533 | 31.242 | [5 empty] | 0 | 12.3 | 1 | 5.5746 | 5.2237 | 4.0369 | 3.75 | 1.4737 | 26.4362
2006-03-12 | 22:33 | 0 | 15.606 | 0 | 4 | 0 | 55.368 | 56.012 | 43.111 | 43.183 | 35.545 | 25.838 | 3.63 | 1 | 0 | 57.697 | 53.764 | 44.334 | 18.248 | 0 | 0 | 55.529 | 31.213 | [5 empty] | 0 | 12.185 | 2 | 5.5393 | 5.1902 | 4.0355 | 3.75 | 1.4402 | 25.9998
2006-03-12 | 22:34 | 1 | 15.659 | 0 | 4 | 0 | 55.741 | 56.061 | 43.236 | 43.26 | 35.832 | 25.845 | 3.558 | 2 | 0 | 57.656 | 53.792 | 44.128 | 18.304 | 0 | 0 | 55.533 | 31.242 | [5 empty] | 15.659 | 12.481 | 3 | 5.5603 | 5.2101 | 4.0363 | 3.75 | 1.4601 | 26.2601
2006-03-12 | 22:35 | 0 | 15.606 | 0 | 4 | 0 | 55.736 | 56.193 | 43.183 | 43.231 | 35.756 | 25.887 | 3.604 | 1 | 0 | 57.628 | 53.741 | 44.123 | 18.273 | 0 | 0 | 55.529 | 31.235 | [5 empty] | 0 | 12.505 | 4 | 5.5469 | 5.1974 | 4.0358 | 3.75 | 1.4474 | 26.094
2006-03-12 | 22:36 | 0 | 15.636 | 0 | 3 | 0 | 55.694 | 56.177 | 43.071 | 43.212 | 36.232 | 25.965 | 3.583 | 1 | 0 | 57.633 | 53.792 | 44.269 | 18.253 | 0 | 0 | 55.512 | 31.264 | [5 empty] | 0 | 12.482 | 5 | 5.553 | 5.2032 | 4.036 | 3.75 | 1.4532 | 26.17
2006-03-12 | 22:37 | 0 | 15.636 | 1 | 4 | 0 | 55.741 | 56.22 | 43.164 | 43.329 | 36.256 | 25.845 | 3.635 | 1 | 0 | 57.61 | 53.699 | 44.128 | 18.253 | 0 | 0 | 55.557 | 31.242 | [5 empty] | 0 | 12.412 | 6 | 5.5379 | 5.1888 | 4.0354 | 3.75 | 1.4388 | 25.9816
2006-03-12 | 22:38 | 1 | 15.606 | 0 | 4 | 0 | 55.643 | 56.193 | 43.276 | 43.231 | 36.086 | 25.862 | 3.63 | 1 | 0 | 57.605 | 53.717 | 44.24 | 18.198 | 0 | 0 | 55.461 | 31.235 | [5 empty] | 15.606 | 12.412 | 7 | 5.5393 | 5.1902 | 4.0355 | 3.75 | 1.4402 | 25.9998
2006-03-12 | 22:39 | 0 | 15.606 | 0 | 4 | 0 | 55.552 | 56.056 | 43.231 | 43.3 | 35.873 | 25.96 | 3.604 | 1 | 0 | 57.628 | 53.741 | 44.135 | 18.236 | 0 | 0 | 55.449 | 31.247 | [5 empty] | 0 | 12.252 | 8 | 5.5469 | 5.1974 | 4.0358 | 3.75 | 1.4474 | 26.094
2006-03-12 | 22:40 | 0 | 15.649 | 0 | 4 | 0 | 55.545 | 56.051 | 43.41 | 43.434 | 35.586 | 25.904 | 3.697 | 1 | 0 | 57.599 | 53.687 | 44.188 | 18.241 | 0 | 0 | 55.477 | 31.301 | [5 empty] | 0 | 12.111 | 9 | 5.5198 | 5.1717 | 4.0347 | 3.75 | 1.4217 | 25.7557
2006-03-12 | 22:41 | 0 | 15.619 | 0 | 4 | 0 | 55.496 | 56 | 43.453 | 43.382 | 35.579 | 25.85 | 3.591 | 1 | 0 | 57.662 | 53.659 | 44.159 | 18.334 | 0 | 0 | 55.426 | 31.296 | [5 empty] | 0 | 12.114 | 10 | 5.5507 | 5.201 | 4.0359 | 3.75 | 1.451 | 26.141
2006-03-12 | 22:42 | 0 | 15.594 | 0 | 4 | 0 | 55.496 | 56.023 | 43.405 | 43.477 | 35.675 | 25.948 | 3.465 | 1 | 0 | 57.617 | 53.659 | 44.135 | 18.236 | 0 | 0 | 55.473 | 31.32 | [5 empty] | 0 | 12.019 | 11 | 5.5874 | 5.2359 | 4.0374 | 3.75 | 1.4859 | 26.5936
2006-03-12 | 22:43 | 1 | 15.619 | 0 | 4 | 0 | 55.426 | 56.044 | 43.571 | 43.501 | 35.696 | 25.875 | 3.514 | 1 | 0 | 57.594 | 53.659 | 44.159 | 18.236 | 0 | 0 | 55.517 | 31.32 | [5 empty] | 15.619 | 11.925 | 12 | 5.5731 | 5.2223 | 4.0368 | 3.75 | 1.4723 | 26.4183
2006-03-12 | 22:44 | 0 | 15.619 | 0 | 4 | 0 | 55.517 | 55.953 | 43.477 | 43.523 | 35.486 | 25.995 | 3.413 | 1 | 0 | 57.594 | 53.638 | 44.204 | 18.236 | 0 | 0 | 55.473 | 31.345 | [5 empty] | 0 | 11.994 | 13 | 5.6025 | 5.2503 | 4.038 | 3.75 | 1.5003 | 26.7786
2006-03-12 | 22:45 | 0 | 15.568 | 0 | 4 | 0 | 55.426 | 55.977 | 43.477 | 43.477 | 35.368 | 26.019 | 3.54 | 1 | 0 | 57.594 | 53.659 | 44.204 | 18.185 | 0 | 0 | 55.54 | 31.32 | [5 empty] | 0 | 11.949 | 14 | 5.5656 | 5.2151 | 4.0365 | 3.75 | 1.4651 | 26.3249
2006-03-12 | 22:46 | 0 | 15.619 | 1 | 4 | 1 | 55.426 | 55.977 | 43.288 | 43.429 | 35.486 | 25.85 | 3.666 | 1 | 0 | 57.594 | 53.615 | 44.183 | 18.236 | 0 | 0 | 55.496 | 31.271 | [5 empty] | 0 | 11.997 | 15 | 5.5289 | 5.1803 | 4.035 | 3.75 | 1.4303 | 25.8688
2006-03-12 | 22:47 | 1 | 15.619 | 0 | 4 | 0 | 55.358 | 55.839 | 43.36 | 43.382 | 35.557 | 25.97 | 3.64 | 1 | 0 | 57.594 | 53.659 | 44.204 | 18.211 | 0 | 0 | 55.473 | 31.271 | [5 empty] | 15.619 | 11.976 | 0 | 5.5364 | 5.1874 | 4.0353 | 3.75 | 1.4374 | 25.9634
2006-03-12 | 22:48 | 0 | 15.594 | 0 | 4 | 0 | 55.221 | 55.816 | 43.219 | 43.405 | 35.651 | 25.779 | 3.54 | 2 | 0 | 57.528 | 53.682 | 44.3 | 18.236 | 0 | 0 | 55.426 | 31.271 | [5 empty] | 0 | 11.816 | 1 | 5.5656 | 5.2151 | 6.2865 | 6 | -0.78487 | -14.1023
2006-03-12 | 22:49 | 0 | 15.543 | 0 | 4 | 0 | 55.151 | 55.631 | 43.24 | 43.429 | 35.344 | 25.85 | 3.514 | 1 | 0 | 57.617 | 53.729 | 44.393 | 18.261 | 0 | 0 | 55.379 | 31.247 | [5 empty] | 0 | 11.722 | 2 | 5.5731 | 5.2223 | 6.2868 | 6 | -0.77768 | -13.954
2006-03-12 | 22:50 | 0 | 15.568 | 0 | 4 | 0 | 55.083 | 55.678 | 43.312 | 43.405 | 35.251 | 25.875 | 3.514 | 1 | 0 | 57.571 | 53.638 | 44.159 | 18.261 | 0 | 0 | 55.379 | 31.271 | [5 empty] | 0 | 11.678 | 3 | 5.5731 | 5.2223 | 6.2868 | 6 | -0.77768 | -13.954
2006-03-12 | 22:51 | 0 | 15.568 | 0 | 4 | 0 | 55.174 | 55.564 | 43.312 | 43.477 | 35.651 | 25.97 | 3.591 | 1 | 0 | 57.571 | 53.615 | 44.228 | 18.236 | 0 | 0 | 55.358 | 31.345 | [5 empty] | 0 | 11.697 | 4 | 5.5507 | 5.201 | 6.2859 | 6 | -0.79899 | -14.3944
2006-03-12 | 22:52 | 1 | 15.568 | 0 | 4 | 0 | 55.104 | 55.678 | 43.24 | 43.405 | 35.72 | 25.948 | 3.617 | 1 | 0 | 57.551 | 53.615 | 44.252 | 18.261 | 0 | 0 | 55.312 | 31.345 | [5 empty] | 15.568 | 11.699 | 5 | 5.5431 | 5.1938 | 6.2856 | 6 | -0.80619 | -14.5439
2006-03-12 | 22:53 | 0 | 15.543 | 0 | 14 | 0 | 57.82 | 55.496 | 43.688 | 52.422 | 56.023 | 25.754 | 3.565 | 1 | 0 | 55.496 | 53.591 | 52.399 | 18.261 | 0 | 0 | 55.288 | 31.291 | [5 empty] | 0 | 5.398 | 6 | 5.5583 | 5.2082 | 6.2862 | 6 | -0.79179 | -14.2453
2006-03-12 | 22:54 | 1 | 15.543 | 1 | 15 | 0 | 65.757 | 55.197 | 45.45 | 56.72 | 364.463 | 25.875 | 3.666 | 2 | 0 | 63.806 | 53.454 | 57.281 | 18.286 | 0 | 0 | 55.288 | 32.041 | [5 empty] | 15.543 | 9.037 | 7 | 5.5289 | 5.1803 | 6.285 | 6 | -0.81975 | -14.8267
2006-03-12 | 22:55 | 1 | 15.568 | 0 | 15 | 0 | 69.637 | 54.922 | 47.651 | 61.204 | 247.314 | 25.705 | 3.617 | 0 | 0 | 68.143 | 53.524 | 61.161 | 18.236 | 0 | 0 | 55.335 | 35.486 | [5 empty] | 15.568 | 8.433 | 8 | 5.5431 | 5.1938 | 6.2856 | 6 | -0.80619 | -14.5439
2006-03-12 | 22:56 | 0 | 15.594 | 0 | 15 | 1 | 70.779 | 54.67 | 49.579 | 63.267 | 232.757 | 25.826 | 3.64 | 0 | 1 | 69.704 | 53.958 | 62.998 | 18.211 | 0 | 0 | 55.426 | 38.33 | [5 empty] | 0 | 7.512 | 9 | 5.5364 | 5.1874 | 6.2853 | 6 | -0.81255 | -14.6765
2006-03-12 | 22:57 | 1 | 15.594 | 0 | 15 | 0 | 70.998 | 54.509 | 51.024 | 64.321 | 253.294 | 25.803 | 3.64 | 1 | 0 | 70.12 | 54.509 | 64.052 | 18.261 | 0 | 0 | 55.54 | 40.375 | [5 empty] | 15.594 | 6.677 | 0 | 5.5364 | 5.1874 | 6.2853 | 6 | -0.81255 | -14.6765
2006-03-12 | 22:58 | 0 | 15.568 | 0 | 15 | 0 | 71.043 | 54.28 | 52.009 | 64.883 | 242.179 | 25.705 | 3.565 | 0 | 0 | 70.252 | 55.083 | 64.657 | 18.261 | 0 | 0 | 55.678 | 41.925 | [5 empty] | 0 | 5.152 | 1 | 5.6025 | 5.2503 | 7.788 | 7.5 | -2.2497 | -40.1554
2006-03-12 | 22:59 | 1 | 15.568 | 1 | 15 | 0 | 71.043 | 54.142 | 52.742 | 65.353 | 242.002 | 25.803 | 3.591 | 0 | 0 | 70.341 | 55.61 | 65.218 | 18.261 | 0 | 0 | 55.977 | 43.195 | [5 empty] | 0 | 4.906 | 2 | 5.5583 | 5.2082 | 7.7862 | 7.5 | -2.2918 | -41.2321
2006-03-12 | 23:00 | 0 | 15.594 | 0 | 15 | 0 | 71.043 | 53.914 | 53.386 | 65.891 | 245.727 | 25.705 | 3.413 | 0 | 0 | 70.406 | 56.091 | 65.645 | 18.261 | 0 | 0 | 56.227 | 44.183 | [5 empty] | 15.588 | 4.502 | 3 | 5.6264 | 5.273 | 7.789 | 7.5 | -2.227 | -39.5815
2006-03-12 | 23:01 | 0 | 15.594 | 0 | 15 | 0 | 71.021 | 53.706 | 53.958 | 66.115 | 242.002 | 25.73 | 3.565 | 1 | 0 | 70.428 | 56.519 | 66.138 | 18.211 | 0 | 0 | 56.451 | 45.084 | [5 empty] | 0 | 3.993 | 4 | 5.5673 | 5.2168 | 7.7866 | 7.5 | -2.2832 | -41.0111
2006-03-12 | 23:02 | 1 | 15.588 | 0 | 15 | 0 | 70.994 | 53.563 | 54.343 | 66.492 | 233.72 | 25.75 | 3.331 | 0 | 0 | 70.446 | 56.916 | 66.38 | 18.18 | 0 | 0 | 56.782 | 45.812 | [5 empty] | 0 | 3.766 | 5 | 5.5507 | 5.201 | 7.7859 | 7.5 | -2.299 | -41.418
2006-03-12 | 23:03 | 0 | 15.588 | 0 | 15 | 0 | 70.82 | 53.402 | 54.756 | 66.827 | 240.028 | 25.725 | 3.534 | 0 | 0 | 70.337 | 57.32 | 66.692 | 18.231 | 0 | 0 | 57.119 | 46.477 | [5 empty] | 15.588 | 3.299 | 6 | 5.5673 | 5.2168 | 7.7866 | 7.5 | -2.2832 | -41.0111
2006-03-12 | 23:04 | 0 | 15.619 | 1 | 15 | 0 | 70.846 | 53.178 | 55.013 | 67.08 | 237.103 | 25.754 | 3.591 | 0 | 0 | 70.274 | 57.685 | 67.012 | 18.261 | 0 | 0 | 57.259 | 47.033 | [5 empty] | 0 | 3.075 | 7 | 5.5822 | 5.2309 | 7.7872 | 7.5 | -2.2691 | -40.6491
2006-03-12 | 23:05 | 1 | 15.588 | 0 | 15 | 0 | 70.71 | 53.036 | 55.307 | 67.411 | 226.082 | 25.725 | 3.534 | 0 | 0 | 70.16 | 58.016 | 67.231 | 18.304 | 0 | 0 | 57.544 | 47.532 | [5 empty] | 0 | 2.88 | 0 | 5.5746 | 5.2237 | 7.7869 | 7.5 | -2.2763 | -40.8334
2006-03-12 | 23:06 | 0 | 15.588 | 0 | 15 | 1 | 70.643 | 52.898 | 55.673 | 67.568 | 214.303 | 25.87 | 3.483 | 0 | 1 | 70.16 | 58.329 | 67.411 | 18.18 | 0 | 0 | 57.77 | 47.99 | [5 empty] | 0 | 2.768 | 1 | 5.5746 | 5.2237 | 3.2869 | 3 | 2.2237 | 39.8902
2006-03-12 | 23:07 | 0 | 15.588 | 0 | 14 | 0 | 70.578 | 52.761 | 55.764 | 67.698 | 236.293 | 25.75 | 3.509 | 1 | 0 | 70.115 | 58.667 | 67.5 | 18.231 | 0 | 0 | 58.016 | 48.312 | [5 empty] | 15.594 | 2.504 | 2 | 5.5431 | 5.1938 | 3.2856 | 3 | 2.1938 | 39.5772
2006-03-12 | 23:08 | 0 | 15.588 | 0 | 15 | 0 | 70.665 | 52.555 | 56.016 | 67.897 | 217.764 | 25.821 | 3.509 | 0 | 0 | 70.138 | 58.913 | 67.83 | 18.231 | 0 | 0 | 58.263 | 48.748 | [5 empty] | 0 | 2.35 | 3 | 5.5798 | 5.2287 | 3.2871 | 3 | 2.2287 | 39.942
2006-03-12 | 23:09 | 1 | 15.594 | 0 | 15 | 0 | 70.625 | 52.469 | 56.181 | 68.121 | 217.423 | 25.634 | 3.617 | 0 | 0 | 70.142 | 59.232 | 67.969 | 18.261 | 0 | 0 | 58.514 | 49.073 | [5 empty] | 0 | 2.33 | 4 | 5.6331 | 5.2793 | 3.2893 | 3 | 2.2793 | 40.4634
2006-03-12 | 23:10 | 0 | 15.543 | 1 | 15 | 0 | 70.647 | 52.352 | 56.273 | 68.297 | 216.329 | 25.659 | 3.491 | 0 | 0 | 70.12 | 59.522 | 68.23 | 18.261 | 0 | 0 | 58.737 | 49.257 | [5 empty] | 0 | 2.153 | 5 | 5.5731 | 5.2223 | 3.2868 | 3 | 2.2223 | 39.8758
2006-03-12 | 23:11 | 0 | 15.563 | 0 | 15 | 0 | 70.71 | 52.186 | 56.446 | 68.38 | 237.81 | 25.485 | 3.308 | 0 | 0 | 70.16 | 59.698 | 68.248 | 18.206 | 0 | 0 | 58.867 | 49.435 | [5 empty] | 15.594 | 2.218 | 6 | 5.5583 | 5.2082 | 3.2862 | 3 | 2.2082 | 39.7283
2006-03-12 | 23:12 | 0 | 15.568 | 0 | 15 | 0 | 70.846 | 52.1 | 56.631 | 68.693 | 232.56 | 25.441 | 3.514 | 0 | 0 | 70.296 | 59.949 | 68.517 | 18.236 | 0 | 0 | 59.075 | 49.67 | [5 empty] | 0 | 2.153 | 7 | 5.6116 | 5.2589 | 3.2884 | 3 | 2.2589 | 40.2537
2006-03-12 | 23:13 | 1 | 15.594 | 0 | 15 | 0 | 71.021 | 51.941 | 56.809 | 68.803 | 246.788 | 25.416 | 3.565 | 1 | 0 | 70.428 | 60.129 | 68.671 | 18.261 | 0 | 0 | 59.276 | 49.852 | [5 empty] | 0 | 2.241 | 8 | 5.6331 | 5.2793 | 3.2893 | 3 | 2.2793 | 40.4634
2006-03-12 | 23:14 | 0 | 15.538 | 0 | 15 | 0 | 71.148 | 51.82 | 56.827 | 68.995 | 211.388 | 25.387 | 3.382 | 0 | 0 | 70.643 | 60.348 | 68.821 | 18.206 | 0 | 0 | 59.429 | 50.1 | [5 empty] | 0 | 2.353 | 9 | 5.6264 | 5.273 | 3.289 | 3 | 2.273 | 40.3984
2006-03-12 | 23:15 | 0 | 15.538 | 1 | 15 | 0 | 71.39 | 51.706 | 56.985 | 69.149 | 210.113 | 25.22 | 3.308 | 0 | 0 | 70.82 | 60.526 | 69.082 | 18.206 | 0 | 0 | 59.472 | 50.284 | [5 empty] | 0 | 2.088 | 10 | 5.6116 | 5.2589 | 3.2884 | 3 | 2.2589 | 40.2537
2006-03-12 | 23:16 | 0 | 15.538 | 0 | 15 | 0 | 71.721 | 51.568 | 57.254 | 69.368 | 211.244 | 25.171 | 3.331 | 0 | 0 | 71.061 | 60.707 | 69.237 | 18.206 | 0 | 0 | 59.675 | 50.583 | [5 empty] | 15.594 | 2.221 | 11 | 5.6098 | 5.2572 | 3.2883 | 3 | 2.2572 | 40.2367
2006-03-12 | 23:17 | 0 | 15.513 | 0 | 15 | 0 | 71.83 | 51.453 | 57.208 | 69.742 | 207.36 | 25.075 | 3.382 | 0 | 0 | 71.235 | 60.93 | 69.545 | 18.281 | 0 | 0 | 59.855 | 50.835 | [5 empty] | 0 | 2.131 | 12 | 5.595 | 5.2431 | 3.2877 | 3 | 2.2431 | 40.0911
2006-03-12 | 23:18 | 1 | 15.594 | 0 | 15 | 0 | 72.099 | 51.344 | 57.528 | 69.878 | 207.197 | 25.2 | 3.388 | 1 | 0 | 71.526 | 61.115 | 69.704 | 18.236 | 0 | 0 | 60.061 | 51.159 | [5 empty] | 0 | 2.109 | 13 | 5.6002 | 5.2481 | 3.2879 | 3 | 2.2481 | 40.1426
2006-03-12 | 23:19 | 0 | 15.594 | 0 | 15 | 0 | 72.273 | 51.229 | 57.662 | 70.142 | 210.118 | 25.176 | 3.439 | 0 | 0 | 71.725 | 61.339 | 69.948 | 18.261 | 0 | 0 | 60.221 | 51.414 | [5 empty] | 0 | 2.176 | 14 | 5.5935 | 5.2417 | 3.2877 | 3 | 2.2417 | 40.0768
2006-03-12 | 23:20 | 0 | 15.576 | 0 | 15 | 0 | 72.459 | 51.078 | 57.692 | 70.35 | 192.7 | 25.014 | 3.421 | 0 | 0 | 71.888 | 61.483 | 70.151 | 18.218 | 0 | 0 | 60.339 | 51.673 | [5 empty] | 0 | 2.108 | 15 | 5.5935 | 5.2417 | 3.2877 | 3 | 2.2417 | 40.0768
2006-03-12 | 23:21 | 0 | 15.576 | 1 | 15 | 0 | 72.7 | 51.008 | 57.895 | 70.524 | 206.402 | 24.992 | 3.444 | 0 | 0 | 72.15 | 61.683 | 70.328 | 18.243 | 0 | 0 | 60.497 | 51.948 | [5 empty] | 15.526 | 0.702 | 16 | 5.5559 | 5.206 | 3.2861 | 3 | 2.206 | 39.7051
2006-03-12 | 23:22 | 0 | 15.551 | 0 | 15 | 0 | 72.919 | 50.847 | 57.918 | 70.811 | 197.232 | 24.894 | 3.444 | 0 | 0 | 72.327 | 61.864 | 70.656 | 18.218 | 0 | 0 | 60.652 | 52.2 | [5 empty] | 0 | 1.053 | 17 | 5.5784 | 5.2273 | 3.287 | 3 | 2.2273 | 39.9276
2006-03-12 | 23:23 | 1 | 15.526 | 0 | 14 | 0 | 71.645 | 50.756 | 58.073 | 70.943 | 80.618 | 24.894 | 3.573 | 1 | 0 | 71.493 | 62.087 | 70.898 | 18.243 | 0 | 0 | 60.832 | 52.452 | [5 empty] | 0 | 16.78 | 18 | 5.5935 | 5.2417 | 3.2877 | 3 | 2.2417 | 40.0768
2006-03-12 | 23:24 | 0 | 15.576 | 0 | 13 | 0 | 71.403 | 59.577 | 51.995 | 70.35 | 37.631 | 24.847 | 3.496 | 0 | 0 | 70.524 | 62.268 | 70.019 | 18.243 | 0 | 0 | 61.056 | 52.156 | [5 empty] | 0 | 7.379 | 19 | 5.5987 | 5.2467 | 3.2879 | 3 | 2.2467 | 40.1283
2006-03-12 | 23:25 | 0 | 15.576 | 0 | 5 | 0 | 63.591 | 70.261 | 38.784 | 46.811 | 27.954 | 24.869 | 3.444 | 0 | 0 | 69.845 | 62.402 | 68.986 | 18.243 | 0 | 0 | 61.213 | 51.582 | [5 empty] | 0 | 2.469 | 0 | 5.5935 | 5.2417 | 3.2877 | 3 | 2.2417 | 40.0768
2006-03-12 | 23:26 | 0 | 15.606 | 0 | 6 | 1 | 42.807 | 52.067 | 34.299 | 35.428 | 24.707 | 24.899 | 3.426 | 0 | 0 | 69.321 | 62.519 | 67.249 | 18.223 | 0 | 0 | 61.352 | 50.945 | [5 empty] | 0 | 0.095 | 1 | 5.5621 | 5.2118 | 4.5721 | 4.2857 | 0.92609 | 16.6502
2006-03-12 | 23:27 | 0 | 15.551 | 0 | 6 | 0 | 35.517 | 38.454 | 33.237 | 33.048 | 21.015 | 25.038 | 3.444 | 0 | 0 | 68.789 | 62.58 | 65.362 | 18.243 | 0 | 0 | 61.528 | 50.275 | [5 empty] | 0 | -0.048 | 2 | 5.6151 | 5.2622 | 4.5742 | 4.2857 | 0.97647 | 17.3902
2006-03-12 | 23:28 | 0 | 15.606 | 0 | 6 | 0 | 33.971 | 34.935 | 34.653 | 33.876 | 19.261 | 24.923 | 3.552 | 0 | 0 | 68.443 | 62.63 | 63.707 | 18.273 | 0 | 0 | 61.599 | 49.705 | [5 empty] | 0 | 0.893 | 3 | 5.5784 | 5.2273 | 4.5728 | 4.2857 | 0.94159 | 16.8794
2006-03-12 | 23:29 | 0 | 15.551 | 1 | 7 | 0 | 35.517 | 35.093 | 34.694 | 35.565 | 17.675 | 24.918 | 3.37 | 0 | 0 | 68.152 | 62.649 | 62.29 | 18.193 | 0 | 0 | 61.594 | 49.129 | [5 empty] | 0 | 0.682 | 4 | 5.6002 | 5.2481 | 4.5736 | 4.2857 | 0.96235 | 17.1842
2006-03-12 | 23:30 | 0 | 15.551 | 0 | 6 | 0 | 35.376 | 36.363 | 33.802 | 34.483 | 16.292 | 24.992 | 3.496 | 0 | 0 | 67.955 | 62.671 | 61.124 | 18.218 | 0 | 0 | 61.617 | 48.578 | [5 empty] | 0 | 0.445 | 5 | 5.6369 | 5.2829 | 4.5751 | 4.2857 | 0.99723 | 17.6911
2006-03-12 | 23:31 | 0 | 15.576 | 0 | 7 | 0 | 34.412 | 35.376 | 33.237 | 33.73 | 14.616 | 24.918 | 3.421 | 0 | 0 | 67.756 | 62.671 | 60.294 | 18.218 | 0 | 0 | 61.348 | 48.118 | [5 empty] | 0 | 0.375 | 6 | 5.5935 | 5.2417 | 4.5734 | 4.2857 | 0.95599 | 17.091
2006-03-12 | 23:32 | 0 | 15.551 | 0 | 6 | 0 | 33.706 | 34.412 | 32.955 | 33.261 | 12.614 | 25.063 | 3.295 | 0 | 0 | 67.602 | 62.715 | 59.643 | 18.193 | 0 | 0 | 61.528 | 47.591 | [5 empty] | 0 | 0.378 | 7 | 5.6151 | 5.2622 | 4.5742 | 4.2857 | 0.97647 | 17.3902
2006-03-12 | 23:33 | 0 | 15.551 | 0 | 7 | 0 | 33.33 | 33.871 | 32.555 | 32.955 | 11.526 | 24.918 | 3.444 | 0 | 0 | 67.402 | 62.649 | 59.285 | 18.193 | 0 | 0 | 61.549 | 47.154 | [5 empty] | 0 | 9.055 | 8 | 5.6002 | 5.2481 | 4.5736 | 4.2857 | 0.96235 | 17.1842
2006-03-12 | 23:34 | 0 | 15.551 | 0 | 7 | 0 | 32.885 | 33.495 | 32.171 | 32.507 | 10.219 | 24.918 | 3.37 | 0 | 0 | 67.222 | 62.671 | 58.927 | 18.218 | 0 | 0 | 61.594 | 46.743 | [5 empty] | 15.606 | 17.15 | 9 | 5.5693 | 5.2187 | 4.5724 | 4.2857 | 0.93301 | 16.7527
2006-03-12 | 23:35 | 0 | 15.551 | 0 | 7 | 0 | 41.322 | 34.67 | 31.857 | 32.267 | 30.146 | 24.894 | 3.421 | 0 | 0 | 67.021 | 62.626 | 58.68 | 18.168 | 0 | 0 | 61.594 | 46.375 | [5 empty] | 0 | 20.188 | 10 | 5.5859 | 5.2345 | 4.5731 | 4.2857 | 0.94879 | 16.9853
2006-03-12 | 23:36 | 1 | 15.606 | 0 | 7 | 0 | 49.133 | 47.39 | 31.767 | 31.983 | 33.83 | 24.899 | 3.527 | 0 | 0 | 66.891 | 62.676 | 58.438 | 18.248 | 0 | 0 | 61.622 | 46.036 | [5 empty] | 15.526 | 20.465 | 11 | 5.5935 | 5.2417 | 4.5734 | 4.2857 | 0.95599 | 17.091
2006-03-12 | 23:37 | 0 | 15.551 | 0 | 6 | 0 | 51.925 | 51.512 | 31.762 | 31.737 | 35.211 | 24.823 | 3.47 | 1 | 0 | 66.685 | 62.626 | 58.185 | 18.193 | 0 | 0 | 61.572 | 45.665 | [5 empty] | 0 | 19.263 | 12 | 5.6445 | 5.2901 | 4.5754 | 4.2857 | 1.0044 | 17.7949
2006-03-12 | 23:38 | 1 | 15.526 | 0 | 7 | 0 | 53.255 | 53.255 | 33.306 | 32.79 | 36.27 | 24.847 | 3.444 | 3 | 0 | 66.571 | 62.626 | 57.872 | 18.218 | 0 | 0 | 61.549 | 45.32 | [5 empty] | 15.551 | 18.114 | 13 | 5.5784 | 5.2273 | 4.5728 | 4.2857 | 0.94159 | 16.8794
2006-03-12 | 23:39 | 0 | 15.551 | 1 | 7 | 0 | 54.287 | 54.539 | 35.234 | 35.024 | 38.126 | 24.823 | 3.269 | 3 | 0 | 66.416 | 62.649 | 57.836 | 18.206 | 0 | 0 | 61.514 | 45.009 | [5 empty] | 15.551 | 16.878 | 0 | 5.6151 | 5.2622 | 4.5742 | 4.2857 | 0.97647 | 17.3902
2006-03-12 | 23:40 | 1 | 15.551 | 0 | 7 | 1 | 55.111 | 55.456 | 37.067 | 36.997 | 39.746 | 24.749 | 3.496 | 3 | 0 | 66.279 | 62.601 | 57.69 | 18.218 | 0 | 0 | 61.457 | 44.746 | [5 empty] | 0 | 16.043 | 1 | 5.5784 | 5.2273 | 7.787 | 7.5 | -2.2727 | -40.7412
2006-03-12 | 23:41 | 1 | 15.551 | 0 | 7 | 0 | 55.638 | 56.075 | 38.736 | 38.76 | 41.181 | 24.823 | 3.37 | 3 | 0 | 66.256 | 62.646 | 57.601 | 18.268 | 0 | 0 | 61.435 | 44.446 | [5 empty] | 15.576 | 15.173 | 2 | 5.5417 | 5.1924 | 7.7856 | 7.5 | -2.3076 | -41.6403
2006-03-12 | 23:42 | 0 | 15.551 | 0 | 7 | 0 | 56.188 | 56.592 | 39.887 | 40.145 | 42.355 | 24.653 | 3.496 | 2 | 0 | 66.145 | 62.624 | 57.669 | 18.243 | 0 | 0 | 61.346 | 44.188 | [5 empty] | 0 | 14.143 | 3 | 5.5769 | 5.2259 | 7.787 | 7.5 | -2.2741 | -40.7767
2006-03-12 | 23:43 | 1 | 15.576 | 0 | 7 | 0 | 56.234 | 56.884 | 40.899 | 41.061 | 42.92 | 24.749 | 3.622 | 2 | 0 | 66.099 | 62.646 | 57.669 | 18.243 | 0 | 0 | 61.323 | 43.929 | [5 empty] | 0 | 13.551 | 4 | 5.6078 | 5.2553 | 7.7882 | 7.5 | -2.2447 | -40.029
2006-03-12 | 23:44 | 0 | 15.581 | 0 | 8 | 0 | 56.056 | 56.932 | 41.631 | 41.913 | 43.511 | 24.997 | 3.501 | 2 | 0 | 66.081 | 62.674 | 57.539 | 18.248 | 0 | 0 | 61.35 | 43.7 | [5 empty] | 15.576 | 13.034 | 5 | 5.6078 | 5.2553 | 7.7882 | 7.5 | -2.2447 | -40.029
2006-03-12 | 23:45 | 0 | 15.551 | 0 | 7 | 0 | 56.165 | 56.793 | 42.379 | 42.614 | 43.929 | 24.823 | 3.395 | 2 | 0 | 65.987 | 62.601 | 57.601 | 18.193 | 0 | 0 | 61.346 | 43.437 | [5 empty] | 0 | 12.403 | 6 | 5.6302 | 5.2766 | 7.7891 | 7.5 | -2.2234 | -39.491
2006-03-12 | 23:46 | 1 | 15.576 | 0 | 7 | 0 | 56.188 | 56.884 | 42.965 | 43.154 | 44.446 | 24.918 | 3.395 | 1 | 0 | 66.01 | 62.601 | 57.535 | 18.168 | 0 | 0 | 61.368 | 43.202 | [5 empty] | 15.576 | 11.952 | 7 | 5.6078 | 5.2553 | 7.7882 | 7.5 | -2.2447 | -40.029
2006-03-12 | 23:47 | 0 | 15.551 | 1 | 7 | 0 | 56.098 | 56.839 | 43.413 | 43.695 | 45.205 | 24.918 | 3.318 | 2 | 0 | 65.942 | 62.578 | 57.535 | 18.193 | 0 | 0 | 61.368 | 43.013 | [5 empty] | 0 | 11.487 | 0 | 5.6369 | 5.2829 | 7.7894 | 7.5 | -2.2171 | -39.3311
2006-03-12 | 23:48 | 1 | 15.576 | 0 | 8 | 1 | 56.188 | 56.816 | 43.977 | 44.236 | 45.457 | 25.038 | 3.395 | 1 | 0 | 66.031 | 62.669 | 57.535 | 18.218 | 0 | 0 | 61.391 | 42.803 | [5 empty] | 0 | 11.121 | 1 | 5.6002 | 5.2481 | 6.2879 | 6 | -0.75193 | -13.4269
2006-03-12 | 23:49 | 0 | 15.551 | 0 | 7 | 0 | 56.142 | 56.861 | 44.353 | 44.655 | 45.595 | 25.134 | 3.295 | 1 | 0 | 65.898 | 62.624 | 57.646 | 18.243 | 0 | 0 | 61.368 | 42.614 | [5 empty] | 15.576 | 10.711 | 2 | 5.6078 | 5.2553 | 6.2882 | 6 | -0.74474 | -13.2804
2006-03-12 | 23:50 | 0 | 15.576 | 0 | 7 | 0 | 56.142 | 56.793 | 44.746 | 45.021 | 45.938 | 25.159 | 3.421 | 2 | 0 | 65.898 | 62.624 | 57.555 | 18.218 | 0 | 0 | 61.346 | 42.425 | [5 empty] | 0 | 10.412 | 3 | 5.6002 | 5.2481 | 6.2879 | 6 | -0.75193 | -13.4269
2006-03-12 | 23:51 | 1 | 15.576 | 0 | 7 | 0 | 56.075 | 56.793 | 44.998 | 45.364 | 46.029 | 25.134 | 3.395 | 1 | 0 | 65.875 | 62.601 | 57.535 | 18.193 | 0 | 0 | 61.346 | 42.262 | [5 empty] | 15.541 | 10.136 | 4 | 5.6331 | 5.2793 | 6.2893 | 6 | -0.72065 | -12.7932
2006-03-12 | 23:52 | 0 | 15.599 | 0 | 8 | 0 | 56.075 | 56.816 | 45.364 | 45.663 | 46.144 | 25.279 | 3.421 | 1 | 0 | 65.898 | 62.601 | 57.466 | 18.218 | 0 | 0 | 61.3 | 42.073 | [5 empty] | 0 | 9.793 | 5 | 5.5964 | 5.2445 | 6.2878 | 6 | -0.75553 | -13.5003
2006-03-12 | 23:53 | 1 | 15.541 | 0 | 7 | 0 | 56.065 | 56.784 | 45.63 | 45.929 | 46.662 | 25.22 | 3.308 | 1 | 0 | 65.821 | 62.614 | 57.503 | 18.158 | 0 | 0 | 61.225 | 41.851 | [5 empty] | 0 | 9.586 | 6 | 5.6107 | 5.258 | 6.2884 | 6 | -0.74197 | -13.2242
2006-03-12 | 23:54 | 0 | 15.541 | 0 | 7 | 0 | 56.042 | 56.807 | 45.791 | 46.249 | 46.41 | 25.293 | 3.434 | 1 | 0 | 65.843 | 62.614 | 57.434 | 18.183 | 0 | 0 | 61.245 | 41.664 | [5 empty] | 15.516 | 9.404 | 7 | 5.6031 | 5.2508 | 6.2881 | 6 | -0.74916 | -13.3705
2006-03-12 | 23:55 | 0 | 15.516 | 0 | 7 | 0 | 56.042 | 56.738 | 45.906 | 46.456 | 46.776 | 25.269 | 3.385 | 2 | 0 | 65.843 | 62.592 | 57.48 | 18.158 | 0 | 0 | 60.91 | 41.547 | [5 empty] | 0 | 9.287 | 8 | 5.5708 | 5.2201 | 6.2867 | 6 | -0.77989 | -13.9996
2006-03-12 | 23:56 | 1 | 15.516 | 1 | 7 | 0 | 55.951 | 56.718 | 46.158 | 46.547 | 46.386 | 25.463 | 3.411 | 1 | 0 | 65.932 | 62.614 | 57.503 | 18.208 | 0 | 0 | 60.933 | 41.427 | [5 empty] | 0 | 0 | 9 | 6.5964 | 6.195 | 6.289 | 6 | 0.195 | 2.9562
2006-03-12 | 23:57 | 0 | 15.551 | 0 | 7 | 0 | 55.89 | 56.681 | 46.398 | 46.603 | 46.167 | 25.423 | 3.522 | 1 | 0 | 65.853 | 62.601 | 57.377 | 18.168 | 0 | 0 | 61.122 | 41.226 | [5 empty] | 5290.1739 | 12.225 | 0 | 5.4942 | 5.1473 | 6.3283 | 6 | -0.85274 | -15.5208
2006-03-12 | 23:58 | 0 | 15.49 | 0 | 8 | 1 | 55.743 | 56.56 | 46.41 | 46.732 | 46.272 | 25.463 | 3.333 | 1 | 0 | 65.798 | 62.592 | 57.322 | 18.158 | 0 | 0 | 61.111 | 41.052 | [5 empty] | 0 | 0 | 1 | 6.5964 | 6.195 | 30.2836 | 30 | -23.805 | -360.8787
2006-03-12 | 23:59 | 0 | 15.49 | 0 | 7 | 0 | 55.858 | 56.471 | 46.524 | 46.823 | 46.524 | 25.534 | 3.46 | 1 | 0 | 65.752 | 62.592 | 57.309 | 18.17 | 0 | 0 | 61.165 | 40.899
[29 empty] | #REF! | #VALUE! | 0 | #VALUE! | #VALUE! | 30.3283 | 30 | #VALUE! | #VALUE!
2006-03-12 | 1440 | 335 | 15.7916 | 1.56 | 6481 | 95 | 55.3528 |  |  | 43.1278 | 72.4463 | 25.9823 | 3.7852 | 1393 | 5 |  |  |  | 18.2622 | 6 | 0 |  |  | -1.159 | 0:01 | 8.798 | 13:21 | 9.957 | #REF!
|  | 1 | [18 empty] | 0 | [10 empty] | #VALUE! | #VALUE! |  | 96 | #VALUE! | #VALUE!