## Therm118
Windmill Logger - THERMAL2.IMS
File opened at 01:01:00 Mon 31 Oct 2005
File closed at 00:01:00 Tue 01 Nov 2005
Date | Time | Boiler_Gas | Gas_MeterT | Boiler_Elec | Boiler_Flow | Boiler_Heat | Boiler_FlowT | Rads_In | Rads_Out | Boiler_Retur | Flue_Gas | Kitchen | Outside | Rain_Gauge | DHW_Coil_Hea | DHW_Coil_In | DHW_Cylinder | DHW_Coil_Out | DHW_Ambient | DHW_Flow | DHW_Heat | DHW_Out | DHW_In | OT min | t OT min | OT max | t OT max | T swing | Wtd._Meter_T | Delta T | Time Interval | T.H. Plus | W.H.L + | Total Heat | Water Ht. | Gain + | Gain + %
Days | Secs | cubic_feet | Celsius | kWh | litres | kWh | Celsius | Celsius | Celsius | Celsius | Celsius | Celsius | Celsius | events | kWh | Celsius | Celsius | Celsius | Celsius | litres | kWh | Celsius | Celsius | Celsius | hh:mm:ss | Celsius | hh:mm:ss | Kelvin | Celsius |  | Minutes | kW | kW | kW | kW | kW | %
2005-10-31 | 0:00 | 0 | 21.515 | 0 | 2 | 0 | 32.615 | 39.502 | 27.584 | 27.537 | 20.116 | 24.693 | 15.842 | 0 | 0 | 58.977 | 56.736 | 50.214 | 22.525 | 0 | 0 | 56.243 | 36.024 | [5 empty] | 0 | 5.078 | 0 | 1.9832 | 1.8099 | 0.14136 | 0 | 1.8099 | 91.2629
2005-10-31 | 0:01 | 0 | 21.544 | 0 | 1 | 0 | 29.54 | 37.885 | 27.638 | 27.638 | 19.282 | 24.651 | 15.873 | 1 | 0 | 59.004 | 56.763 | 50.357 | 22.579 | 0 | 0 | 56.225 | 36.076 | [5 empty] | 0 | 1.902 | 1 | 1.9742 | 1.8014 | 2.0765 | 1.9355 | -0.13413 | -6.7942
2005-10-31 | 0:02 | 0 | 21.539 | 0 | 2 | 0 | 28.596 | 31.703 | 27.657 | 27.488 | 18.61 | 24.717 | 15.82 | 0 | 0 | 58.977 | 56.736 | 50.329 | 22.55 | 0 | 0 | 56.197 | 36.024 | [5 empty] | 0 | 1.108 | 2 | 1.9896 | 1.816 | 2.0771 | 1.9355 | -0.11946 | -6.0042
2005-10-31 | 0:03 | 0 | 21.539 | 0 | 2 | 0 | 28.282 | 29.656 | 27.777 | 27.682 | 18.361 | 24.646 | 15.82 | 0 | 0 | 58.977 | 56.713 | 50.329 | 22.55 | 0 | 0 | 56.22 | 35.976 | [5 empty] | 0 | 0.6 | 3 | 1.9896 | 1.816 | 2.0771 | 1.9355 | -0.11946 | -6.0042
2005-10-31 | 0:04 | 0 | 21.562 | 0 | 2 | 0 | 28.091 | 28.962 | 27.782 | 27.638 | 18.392 | 24.867 | 15.749 | 0 | 0 | 59.027 | 56.763 | 50.219 | 22.555 | 0 | 0 | 56.248 | 35.959 | [5 empty] | 0 | 0.453 | 4 | 2.0103 | 1.8357 | 2.0779 | 1.9355 | -0.099807 | -4.9648
2005-10-31 | 0:05 | 0 | 21.569 | 0 | 2 | 0 | 28.023 | 28.601 | 27.878 | 27.662 | 18.022 | 24.796 | 15.873 | 0 | 0 | 58.984 | 56.763 | 50.23 | 22.567 | 0 | 0 | 56.234 | 35.923 | [5 empty] | 0 | 0.361 | 5 | 1.9742 | 1.8014 | 2.0765 | 1.9355 | -0.13413 | -6.7942
2005-10-31 | 0:06 | 0 | 21.498 | 0 | 2 | 0 | 28 | 28.434 | 27.711 | 27.711 | 17.801 | 24.651 | 15.802 | 0 | 0 | 58.892 | 56.718 | 50.151 | 22.483 | 0 | 0 | 56.159 | 35.866 | [5 empty] | 0 | 0.289 | 6 | 1.9949 | 1.821 | 2.0773 | 1.9355 | -0.11448 | -5.7386
2005-10-31 | 0:07 | 0 | 21.498 | 1 | 2 | 0 | 27.976 | 28.336 | 27.662 | 27.687 | 17.778 | 24.651 | 15.777 | 0 | 0 | 58.892 | 56.674 | 50.265 | 22.461 | 0 | 0 | 56.202 | 35.842 | [5 empty] | 0 | 0.289 | 7 | 2.0021 | 1.8279 | 2.0776 | 1.9355 | -0.10756 | -5.3721
2005-10-31 | 0:08 | 0 | 21.52 | 0 | 2 | 0 | 27.927 | 28.265 | 27.64 | 27.64 | 17.605 | 24.749 | 15.727 | 0 | 0 | 58.892 | 56.674 | 50.128 | 22.483 | 0 | 0 | 56.179 | 35.842 | [5 empty] | 0 | 0.287 | 8 | 2.0167 | 1.8418 | 2.0782 | 1.9355 | -0.093717 | -4.6471
2005-10-31 | 0:09 | 0 | 21.52 | 0 | 2 | 0 | 29.325 | 28.192 | 27.64 | 27.64 | 25.183 | 24.7 | 15.727 | 0 | 0 | 58.87 | 56.652 | 50.128 | 22.483 | 0 | 0 | 56.135 | 35.794 | [5 empty] | 0 | 1.685 | 9 | 2.0167 | 1.8418 | 2.0782 | 1.9355 | -0.093717 | -4.6471
2005-10-31 | 0:10 | 0 | 21.53 | 0 | 2 | 0 | 42.922 | 28.248 | 27.623 | 27.672 | 21.915 | 24.707 | 15.734 | 1 | 0 | 58.899 | 56.658 | 50.205 | 22.515 | 0 | 0 | 56.142 | 35.801 | [5 empty] | 0 | 15.25 | 10 | 2.0147 | 1.8398 | 2.0781 | 1.9355 | -0.095655 | -4.748
2005-10-31 | 0:11 | 0 | 21.52 | 0 | 2 | 0 | 32.67 | 39.038 | 27.616 | 27.542 | 19.603 | 24.7 | 15.727 | 0 | 0 | 58.847 | 56.652 | 50.104 | 22.483 | 0 | 0 | 56.112 | 35.77 | [5 empty] | 0 | 5.128 | 11 | 2.0167 | 1.8418 | 2.0782 | 1.9355 | -0.093717 | -4.6471
2005-10-31 | 0:12 | 0 | 21.498 | 0 | 2 | 0 | 29.374 | 37.158 | 27.64 | 27.517 | 18.864 | 24.7 | 15.727 | 0 | 0 | 58.847 | 56.629 | 50.128 | 22.508 | 0 | 0 | 56.159 | 35.818 | [5 empty] | 0 | 1.857 | 12 | 2.0167 | 1.8418 | 2.0782 | 1.9355 | -0.093717 | -4.6471
2005-10-31 | 0:13 | 0 | 21.52 | 0 | 2 | 0 | 28.459 | 31.156 | 27.76 | 27.591 | 18.47 | 24.725 | 15.752 | 0 | 0 | 58.847 | 56.606 | 50.104 | 22.483 | 0 | 0 | 56.135 | 35.794 | [5 empty] | 0 | 0.868 | 13 | 2.0094 | 1.8348 | 2.0779 | 1.9355 | -0.10064 | -5.0083
2005-10-31 | 0:14 | 0 | 21.52 | 0 | 2 | 0 | 28.17 | 29.325 | 27.807 | 27.616 | 18.123 | 24.774 | 15.85 | 1 | 0 | 58.847 | 56.652 | 50.198 | 22.483 | 0 | 0 | 56.089 | 35.794 | [5 empty] | 0 | 0.554 | 14 | 1.9809 | 1.8077 | 2.0768 | 1.9355 | -0.12776 | -6.4499
2005-10-31 | 0:15 | 0 | 21.498 | 0 | 2 | 0 | 28.05 | 28.746 | 27.76 | 27.616 | 17.974 | 24.725 | 15.752 | 0 | 0 | 58.87 | 56.652 | 50.198 | 22.483 | 0 | 0 | 56.021 | 35.77 | [5 empty] | 0 | 0.434 | 15 | 2.0094 | 1.8348 | 2.0779 | 1.9355 | -0.10064 | -5.0083
2005-10-31 | 0:16 | 0 | 21.52 | 0 | 2 | 0 | 28.121 | 28.579 | 27.711 | 27.687 | 17.876 | 24.749 | 15.777 | 0 | 0 | 58.87 | 56.629 | 50.06 | 22.461 | 0 | 0 | 56.089 | 35.746 | [5 empty] | 0 | 0.434 | 16 | 2.0021 | 1.8279 | 2.0776 | 1.9355 | -0.10756 | -5.3721
2005-10-31 | 0:17 | 0 | 21.52 | 0 | 2 | 0 | 27.976 | 28.41 | 27.807 | 27.616 | 17.753 | 24.82 | 15.679 | 0 | 0 | 58.87 | 56.606 | 50.013 | 22.461 | 0 | 0 | 56.065 | 35.701 | [5 empty] | 0 | 0.36 | 17 | 2.0307 | 1.8551 | 2.0788 | 1.9355 | -0.080431 | -3.9608
2005-10-31 | 0:18 | 0 | 21.52 | 0 | 3 | 0 | 27.927 | 28.336 | 27.687 | 27.591 | 17.63 | 24.774 | 15.654 | 0 | 0 | 58.826 | 56.606 | 50.06 | 22.483 | 0 | 0 | 56.065 | 35.701 | [5 empty] | 0 | 0.336 | 18 | 2.038 | 1.862 | 2.0791 | 1.9355 | -0.073511 | -3.6071
2005-10-31 | 0:19 | 0 | 21.498 | 1 | 2 | 0 | 27.905 | 28.216 | 27.616 | 27.687 | 17.554 | 24.676 | 15.679 | 0 | 0 | 58.803 | 56.606 | 50.083 | 22.508 | 0 | 0 | 56.065 | 35.725 | [5 empty] | 0 | 0.218 | 19 | 2.0307 | 1.8551 | 2.0788 | 1.9355 | -0.080431 | -3.9608
2005-10-31 | 0:20 | 0 | 21.498 | 0 | 2 | 0 | 28.121 | 28.192 | 27.662 | 27.566 | 25.198 | 24.668 | 15.621 | 0 | 0 | 58.817 | 56.531 | 50.006 | 22.452 | 0 | 0 | 56.058 | 35.622 | [5 empty] | 0 | 0.555 | 20 | 2.0476 | 1.8711 | 2.0795 | 1.9355 | -0.064377 | -3.1441
2005-10-31 | 0:21 | 0 | 21.52 | 0 | 2 | 0 | 43.408 | 28.121 | 27.662 | 27.495 | 24.7 | 24.58 | 15.654 | 0 | 0 | 58.803 | 56.606 | 50.06 | 22.483 | 0 | 0 | 56.089 | 35.677 | [5 empty] | 0 | 15.913 | 21 | 2.038 | 1.862 | 2.0791 | 1.9355 | -0.073511 | -3.6071
2005-10-31 | 0:22 | 0 | 21.498 | 0 | 2 | 0 | 45.245 | 38.755 | 27.76 | 27.542 | 24.629 | 24.58 | 15.702 | 1 | 0 | 58.781 | 56.583 | 49.99 | 22.508 | 0 | 0 | 56.044 | 35.701 | [5 empty] | 0 | 17.703 | 22 | 2.024 | 1.8487 | 2.0785 | 1.9355 | -0.086797 | -4.2885
2005-10-31 | 0:23 | 1 | 21.512 | 0 | 3 | 0 | 45.124 | 44.711 | 27.75 | 27.584 | 24.644 | 24.573 | 15.669 | 2 | 0 | 58.774 | 56.531 | 49.96 | 22.452 | 0 | 0 | 55.991 | 35.67 | [5 empty] | 21.512 | 17.54 | 23 | 2.0336 | 1.8578 | 2.0789 | 1.9355 | -0.077663 | -3.819
2005-10-31 | 0:24 | 0 | 21.569 | 0 | 2 | 0 | 44.946 | 45.222 | 27.736 | 27.662 | 24.725 | 24.555 | 15.679 | 1 | 0 | 58.781 | 56.517 | 50.013 | 22.461 | 0 | 0 | 56.021 | 35.701 | [5 empty] | 0 | 17.284 | 24 | 2.0307 | 1.8551 | 2.0788 | 1.9355 | -0.080431 | -3.9608
2005-10-31 | 0:25 | 0 | 21.498 | 0 | 2 | 0 | 44.741 | 45.084 | 27.856 | 27.687 | 24.749 | 24.651 | 15.654 | 1 | 0 | 58.781 | 56.54 | 49.99 | 22.52 | 0 | 0 | 56.012 | 35.737 | [5 empty] | 0 | 17.054 | 25 | 2.038 | 1.862 | 2.0791 | 1.9355 | -0.073511 | -3.6071
2005-10-31 | 0:26 | 0 | 21.515 | 0 | 2 | 0 | 44.508 | 45.012 | 27.826 | 27.635 | 25.539 | 24.624 | 15.649 | 1 | 0 | 58.799 | 56.558 | 50.032 | 22.479 | 0 | 0 | 55.995 | 35.696 | [5 empty] | 0 | 16.873 | 26 | 2.0394 | 1.8634 | 2.0791 | 1.9355 | -0.072127 | -3.5367
2005-10-31 | 0:27 | 0 | 21.493 | 0 | 3 | 0 | 44.575 | 44.965 | 27.537 | 27.635 | 26.093 | 24.744 | 15.649 | 2 | 0 | 58.845 | 56.581 | 49.988 | 22.456 | 0 | 0 | 56.016 | 35.696 | [5 empty] | 0 | 16.94 | 27 | 2.0394 | 1.8634 | 2.0791 | 1.9355 | -0.072127 | -3.5367
2005-10-31 | 0:28 | 0 | 21.525 | 1 | 2 | 0 | 44.629 | 44.837 | 27.28 | 27.402 | 26.63 | 24.678 | 15.656 | 1 | 0 | 58.829 | 56.61 | 50.062 | 22.51 | 0 | 0 | 56.047 | 35.751 | [5 empty] | 0 | 17.227 | 28 | 2.0374 | 1.8614 | 2.079 | 1.9355 | -0.074065 | -3.6353
2005-10-31 | 0:29 | 1 | 21.571 | 0 | 3 | 0 | 44.858 | 44.881 | 27.088 | 27.113 | 26.534 | 24.752 | 15.656 | 1 | 0 | 58.897 | 56.61 | 50.041 | 22.51 | 0 | 0 | 56.07 | 35.751 | [5 empty] | 21.571 | 17.745 | 29 | 2.0374 | 1.8614 | 2.079 | 1.9355 | -0.074065 | -3.6353
2005-10-31 | 0:30 | 0 | 21.571 | 0 | 2 | 1 | 44.79 | 45.133 | 27.184 | 26.87 | 27.135 | 24.656 | 15.656 | 2 | 0 | 58.874 | 56.61 | 49.995 | 22.51 | 0 | 0 | 56.093 | 35.797 | [5 empty] | 0 | 17.92 | 30 | 2.0374 | 1.8614 | 2.079 | 1.9355 | -0.074065 | -3.6353
2005-10-31 | 0:31 | 0 | 21.547 | 0 | 3 | 0 | 45.042 | 45.133 | 27.329 | 26.895 | 27.015 | 24.607 | 15.631 | 1 | 0 | 58.897 | 56.588 | 50.062 | 22.488 | 0 | 0 | 56.047 | 35.797 | [5 empty] | 0 | 18.147 | 0 | 2.0447 | 1.8683 | 2.0793 | 1.9355 | -0.067145 | -3.2839
2005-10-31 | 0:32 | 0 | 21.539 | 0 | 2 | 0 | 44.851 | 45.334 | 27.755 | 27.032 | 27.177 | 24.671 | 15.649 | 2 | 0 | 58.913 | 56.581 | 49.964 | 22.479 | 0 | 0 | 56.016 | 35.744 | [5 empty] | 0 | 17.819 | 1 | 2.0394 | 1.8634 | 1.1963 | 1.0526 | 0.81073 | 39.7529
2005-10-31 | 0:33 | 1 | 21.571 | 0 | 3 | 0 | 44.743 | 45.294 | 28.268 | 27.449 | 27.424 | 24.678 | 15.682 | 1 | 0 | 58.963 | 56.61 | 50.062 | 22.51 | 0 | 0 | 56.047 | 35.82 | [5 empty] | 21.571 | 17.294 | 2 | 2.0298 | 1.8542 | 1.1959 | 1.0526 | 0.80159 | 39.4911
2005-10-31 | 0:34 | 0 | 21.547 | 0 | 2 | 0 | 44.767 | 45.226 | 28.991 | 28.076 | 27.28 | 24.656 | 15.631 | 1 | 0 | 58.963 | 56.633 | 50.132 | 22.488 | 0 | 0 | 55.979 | 35.82 | [5 empty] | 0 | 16.691 | 3 | 2.0447 | 1.8683 | 1.1965 | 1.0526 | 0.81571 | 39.8947
2005-10-31 | 0:35 | 0 | 21.525 | 0 | 3 | 0 | 44.974 | 45.364 | 29.641 | 28.726 | 27.039 | 24.801 | 15.533 | 2 | 0 | 58.963 | 56.61 | 50.132 | 22.51 | 0 | 0 | 55.956 | 35.82 | [5 empty] | 0 | 16.248 | 4 | 2.0732 | 1.8955 | 1.1976 | 1.0526 | 0.84283 | 40.654
2005-10-31 | 0:36 | 0 | 21.547 | 0 | 2 | 0 | 44.974 | 45.226 | 30.411 | 29.45 | 26.919 | 24.801 | 15.556 | 1 | 0 | 58.956 | 56.626 | 49.964 | 22.479 | 0 | 0 | 55.972 | 35.789 | [5 empty] | 0 | 15.524 | 5 | 2.0665 | 1.8891 | 1.1974 | 1.0526 | 0.83647 | 40.4776
2005-10-31 | 0:37 | 0 | 21.525 | 0 | 3 | 0 | 45.341 | 45.408 | 30.918 | 30.17 | 27.064 | 24.872 | 15.606 | 1 | 0 | 58.986 | 56.633 | 50.041 | 22.51 | 0 | 0 | 56.002 | 35.751 | [5 empty] | 0 | 15.171 | 6 | 2.0519 | 1.8753 | 1.1968 | 1.0526 | 0.82263 | 40.0904
2005-10-31 | 0:38 | 0 | 21.571 | 1 | 2 | 0 | 45.868 | 45.616 | 31.374 | 30.678 | 27.28 | 24.823 | 15.631 | 2 | 0 | 59.009 | 56.61 | 50.156 | 22.51 | 0 | 0 | 56.002 | 35.751 | [5 empty] | 0 | 15.19 | 7 | 2.0447 | 1.8683 | 1.1965 | 1.0526 | 0.81571 | 39.8947
2005-10-31 | 0:39 | 1 | 21.571 | 0 | 2 | 0 | 46.44 | 46.05 | 31.713 | 31.159 | 27.473 | 24.847 | 15.581 | 1 | 0 | 59.009 | 56.633 | 50.156 | 22.51 | 0 | 0 | 56.002 | 35.727 | [5 empty] | 21.571 | 15.281 | 8 | 2.0592 | 1.8822 | 1.1971 | 1.0526 | 0.82955 | 40.2847
2005-10-31 | 0:40 | 0 | 21.571 | 0 | 3 | 0 | 47.313 | 46.578 | 32.171 | 31.737 | 27.858 | 24.967 | 15.631 | 1 | 0 | 58.986 | 56.656 | 50.2 | 22.488 | 0 | 0 | 55.979 | 35.727 | [5 empty] | 0 | 15.576 | 9 | 2.0447 | 1.8683 | 1.1965 | 1.0526 | 0.81571 | 39.8947
2005-10-31 | 0:41 | 0 | 21.547 | 0 | 2 | 0 | 48.046 | 47.196 | 32.483 | 31.978 | 28.148 | 24.847 | 15.606 | 1 | 0 | 58.986 | 56.61 | 50.109 | 22.488 | 0 | 0 | 55.956 | 35.727 | [5 empty] | 0 | 16.068 | 10 | 2.0519 | 1.8753 | 1.1968 | 1.0526 | 0.82263 | 40.0904
2005-10-31 | 0:42 | 0 | 21.596 | 0 | 2 | 0 | 48.802 | 48.023 | 32.742 | 32.291 | 28.412 | 24.945 | 15.631 | 1 | 0 | 59.032 | 56.633 | 50.062 | 22.535 | 0 | 0 | 56.002 | 35.727 | [5 empty] | 0 | 16.511 | 11 | 2.0447 | 1.8683 | 1.1965 | 1.0526 | 0.81571 | 39.8947
2005-10-31 | 0:43 | 0 | 21.539 | 0 | 2 | 0 | 41.358 | 48.634 | 33.017 | 32.548 | 25.2 | 25.034 | 15.649 | 1 | 0 | 59.002 | 56.581 | 50.055 | 22.479 | 0 | 0 | 55.925 | 35.696 | [5 empty] | 0 | 8.81 | 12 | 2.0394 | 1.8634 | 1.1963 | 1.0526 | 0.81073 | 39.7529
2005-10-31 | 0:44 | 0 | 21.571 | 0 | 2 | 0 | 36.151 | 46.944 | 33.072 | 32.766 | 23.258 | 25.065 | 15.581 | 0 | 0 | 59.054 | 56.633 | 50.177 | 22.51 | 0 | 0 | 55.979 | 35.727 | [5 empty] | 0 | 3.385 | 13 | 2.0592 | 1.8822 | 1.1971 | 1.0526 | 0.82955 | 40.2847
2005-10-31 | 0:45 | 0 | 21.571 | 0 | 2 | 0 | 34.739 | 39.253 | 33.165 | 32.931 | 22.005 | 25.016 | 15.556 | 1 | 0 | 58.986 | 56.633 | 50.156 | 22.523 | 0 | 0 | 55.991 | 35.739 | [5 empty] | 0 | 1.808 | 14 | 2.0665 | 1.8891 | 1.1974 | 1.0526 | 0.83647 | 40.4776
2005-10-31 | 0:46 | 0 | 21.598 | 0 | 2 | 0 | 34.297 | 36.201 | 33.263 | 33.005 | 21.167 | 25.019 | 15.558 | 0 | 0 | 59.057 | 56.658 | 50.158 | 22.491 | 0 | 0 | 56.028 | 35.682 | [5 empty] | 0 | 1.292 | 15 | 2.0659 | 1.8885 | 1.1973 | 1.0526 | 0.83591 | 40.4623
2005-10-31 | 0:47 | 0 | 21.598 | 0 | 2 | 0 | 34.084 | 35.165 | 33.122 | 33.074 | 20.637 | 24.994 | 15.583 | 0 | 0 | 59.034 | 56.613 | 50.202 | 22.513 | 0 | 0 | 55.958 | 35.73 | [5 empty] | 0 | 1.01 | 16 | 2.0586 | 1.8816 | 1.1971 | 1.0526 | 0.82899 | 40.2692
2005-10-31 | 0:48 | 0 | 21.623 | 1 | 2 | 0 | 33.943 | 34.766 | 33.239 | 33.122 | 20.129 | 25.019 | 15.707 | 0 | 0 | 59.057 | 56.658 | 50.158 | 22.513 | 0 | 0 | 55.981 | 35.73 | [5 empty] | 0 | 0.821 | 17 | 2.0225 | 1.8473 | 1.1956 | 1.0526 | 0.79467 | 39.2911
2005-10-31 | 0:49 | 0 | 21.598 | 0 | 2 | 0 | 33.804 | 34.531 | 32.981 | 33.122 | 19.734 | 25.114 | 15.558 | 0 | 0 | 59.057 | 56.636 | 50.158 | 22.513 | 0 | 0 | 56.005 | 35.753 | [5 empty] | 0 | 0.682 | 18 | 2.0659 | 1.8885 | 1.1973 | 1.0526 | 0.83591 | 40.4623
2005-10-31 | 0:50 | 0 | 21.598 | 0 | 1 | 0 | 33.78 | 34.297 | 32.723 | 33.144 | 19.561 | 24.994 | 15.558 | 0 | 0 | 58.988 | 56.59 | 50.249 | 22.537 | 0 | 0 | 55.981 | 35.777 | [5 empty] | 0 | 0.636 | 19 | 2.0659 | 1.8885 | 1.1973 | 1.0526 | 0.83591 | 40.4623
2005-10-31 | 0:51 | 0 | 21.598 | 0 | 2 | 0 | 33.639 | 34.249 | 32.582 | 32.792 | 19.339 | 25.043 | 15.511 | 0 | 0 | 58.988 | 56.613 | 50.135 | 22.513 | 0 | 0 | 55.958 | 35.706 | [5 empty] | 0 | 0.847 | 20 | 2.0796 | 1.9016 | 1.1979 | 1.0526 | 0.84892 | 40.8215
2005-10-31 | 0:52 | 0 | 21.542 | 0 | 2 | 0 | 33.443 | 34.053 | 32.382 | 32.596 | 26.409 | 25.011 | 15.478 | 0 | 0 | 58.915 | 56.56 | 50.104 | 22.481 | 0 | 0 | 55.881 | 35.651 | [5 empty] | 0 | 0.847 | 21 | 2.0892 | 1.9107 | 1.1983 | 1.0526 | 0.85806 | 41.071
2005-10-31 | 0:53 | 0 | 21.623 | 0 | 2 | 0 | 46.856 | 33.921 | 32.22 | 32.485 | 25.259 | 25.092 | 15.46 | 0 | 0 | 58.968 | 56.59 | 50.111 | 22.491 | 0 | 0 | 55.911 | 35.706 | [5 empty] | 0 | 14.371 | 22 | 2.0944 | 1.9157 | 1.1985 | 1.0526 | 0.86304 | 41.2061
2005-10-31 | 0:54 | 0 | 21.574 | 0 | 2 | 0 | 41.698 | 35.847 | 31.764 | 32.198 | 21.959 | 25.068 | 15.435 | 1 | 0 | 58.922 | 56.547 | 50.065 | 22.513 | 0 | 0 | 55.935 | 35.706 | [5 empty] | 0 | 9.5 | 23 | 2.1017 | 1.9226 | 1.1988 | 1.0526 | 0.86996 | 41.3926
2005-10-31 | 0:55 | 0 | 21.574 | 0 | 2 | 0 | 35.519 | 45.985 | 31.45 | 31.98 | 20.613 | 25.019 | 15.46 | 0 | 0 | 58.945 | 56.567 | 50.088 | 22.513 | 0 | 0 | 55.911 | 35.682 | [5 empty] | 0 | 3.539 | 24 | 2.0944 | 1.9157 | 1.1985 | 1.0526 | 0.86304 | 41.2061
2005-10-31 | 0:56 | 0 | 21.598 | 0 | 1 | 0 | 33.708 | 39.841 | 31.186 | 31.691 | 20.104 | 25.092 | 15.511 | 0 | 0 | 58.945 | 56.59 | 50.272 | 22.635 | 0 | 0 | 55.911 | 35.777 | [5 empty] | 0 | 2.017 | 25 | 2.0796 | 1.9016 | 1.1979 | 1.0526 | 0.84892 | 40.8215
2005-10-31 | 0:57 | 0 | 21.574 | 0 | 1 | 0 | 32.864 | 35.565 | 30.992 | 31.33 | 19.362 | 25.114 | 15.387 | 1 | 0 | 58.899 | 56.547 | 50.088 | 22.491 | 0 | 0 | 55.911 | 35.682 | [5 empty] | 0 | 1.534 | 26 | 2.1157 | 1.9359 | 1.1994 | 1.0526 | 0.88325 | 41.7472
2005-10-31 | 0:58 | 0 | 21.574 | 0 | 2 | 0 | 32.39 | 33.991 | 30.825 | 31.112 | 18.967 | 25.164 | 15.485 | 0 | 0 | 58.876 | 56.524 | 50.044 | 22.513 | 0 | 0 | 55.867 | 35.706 | [5 empty] | 0 | 1.278 | 27 | 2.0872 | 1.9088 | 1.1982 | 1.0526 | 0.85612 | 41.0183
2005-10-31 | 0:59 | 0 | 21.574 | 0 | 2 | 0 | 32.054 | 33.309 | 30.582 | 30.97 | 19.018 | 25.043 | 15.511 | 0 | 0 | 58.922 | 56.547 | 50.158 | 22.562 | 0 | 0 | 55.776 | 35.706 | [5 empty] | 0 | 1.084 | 28 | 2.0796 | 1.9016 | 1.1979 | 1.0526 | 0.84892 | 40.8215
2005-10-31 | 1:00 | 0 | 21.574 | 1 | 1 | 0 | 31.666 | 32.816 | 30.416 | 30.703 | 18.671 | 24.97 | 15.46 | 0 | 0 | 58.833 | 56.501 | 50.111 | 22.491 | 0 | 0 | 55.753 | 35.636 | [5 empty] | 0 | 0.963 | 29 | 2.0944 | 1.9157 | 1.1985 | 1.0526 | 0.86304 | 41.2061
2005-10-31 | 1:01 | 0 | 21.598 | 0 | 2 | 0 | 31.426 | 32.365 | 30.487 | 30.511 | 18.573 | 25.092 | 15.413 | 0 | 0 | 58.833 | 56.501 | 49.997 | 22.466 | 0 | 0 | 55.797 | 35.636 | [5 empty] | 0 | 0.915 | 30 | 2.1081 | 1.9287 | 1.1991 | 1.0526 | 0.87605 | 41.5557
2005-10-31 | 1:02 | 0 | 21.574 | 0 | 2 | 0 | 31.137 | 32.054 | 30.271 | 30.391 | 18.449 | 24.97 | 15.46 | 0 | 0 | 58.787 | 56.478 | 50.02 | 22.491 | 0 | 0 | 55.797 | 35.682 | [5 empty] | 0 | 0.746 | 31 | 2.0944 | 1.9157 | 1.1985 | 1.0526 | 0.86304 | 41.2061
2005-10-31 | 1:03 | 0 | 21.628 | 0 | 2 | 0 | 30.999 | 31.794 | 30.082 | 30.445 | 22.351 | 24.953 | 15.516 | 0 | 0 | 58.815 | 56.483 | 50.048 | 22.542 | 0 | 0 | 55.848 | 35.71 | [5 empty] | 0 | 0.554 | 32 | 2.0781 | 1.9002 | 1.1978 | 1.0526 | 0.84754 | 40.7836
2005-10-31 | 1:04 | 1 | 21.598 | 0 | 1 | 0 | 43.391 | 31.499 | 29.982 | 30.222 | 24.779 | 24.994 | 15.558 | 0 | 0 | 58.765 | 56.501 | 50.02 | 22.513 | 0 | 0 | 55.797 | 35.66 | [5 empty] | 21.598 | 13.169 | 33 | 2.0659 | 1.8885 | 1.1973 | 1.0526 | 0.83591 | 40.4623
2005-10-31 | 1:05 | 0 | 21.598 | 0 | 2 | 0 | 41.652 | 32.149 | 29.763 | 30.173 | 21.454 | 24.874 | 15.435 | 0 | 0 | 58.742 | 56.478 | 49.936 | 22.454 | 0 | 0 | 55.806 | 35.622 | [5 empty] | 0 | 11.479 | 34 | 2.1017 | 1.9226 | 1.1988 | 1.0526 | 0.86996 | 41.3926
2005-10-31 | 1:06 | 0 | 21.527 | 0 | 2 | 0 | 33.849 | 43.953 | 29.643 | 29.837 | 19.835 | 24.852 | 15.314 | 1 | 0 | 58.628 | 56.387 | 49.95 | 22.42 | 0 | 0 | 55.727 | 35.588 | [5 empty] | 0 | 4.012 | 35 | 2.137 | 1.9561 | 1.2002 | 1.0526 | 0.90345 | 42.2774
2005-10-31 | 1:07 | 0 | 21.532 | 0 | 2 | 0 | 31.649 | 38.861 | 29.553 | 29.866 | 19 | 24.906 | 15.395 | 0 | 0 | 58.724 | 56.391 | 49.885 | 22.425 | 0 | 0 | 55.778 | 35.641 | [5 empty] | 0 | 1.783 | 36 | 2.1134 | 1.9337 | 1.1993 | 1.0526 | 0.88103 | 41.6884
2005-10-31 | 1:08 | 0 | 21.532 | 0 | 2 | 0 | 30.806 | 33.713 | 29.312 | 29.602 | 18.482 | 24.808 | 15.37 | 0 | 0 | 58.655 | 56.369 | 49.978 | 22.449 | 0 | 0 | 55.664 | 35.665 | [5 empty] | 0 | 1.204 | 37 | 2.1207 | 1.9406 | 1.1996 | 1.0526 | 0.88795 | 41.8716
2005-10-31 | 1:09 | 0 | 21.532 | 0 | 1 | 0 | 30.396 | 31.963 | 29.312 | 29.361 | 18.16 | 24.857 | 15.37 | 0 | 0 | 58.678 | 56.391 | 49.864 | 22.449 | 0 | 0 | 55.664 | 35.641 | [5 empty] | 0 | 1.035 | 38 | 2.1207 | 1.9406 | 1.1996 | 1.0526 | 0.88795 | 41.8716
2005-10-31 | 1:10 | 0 | 21.581 | 0 | 2 | 0 | 30.107 | 31.191 | 29.386 | 29.312 | 18.012 | 24.857 | 15.37 | 0 | 0 | 58.632 | 56.369 | 49.885 | 22.449 | 0 | 0 | 55.641 | 35.617 | [5 empty] | 0 | 0.795 | 39 | 2.1207 | 1.9406 | 1.1996 | 1.0526 | 0.88795 | 41.8716
2005-10-31 | 1:11 | 0 | 21.591 | 1 | 2 | 0 | 29.925 | 30.791 | 29.202 | 29.202 | 17.972 | 24.771 | 15.38 | 0 | 0 | 58.644 | 56.378 | 49.897 | 22.483 | 0 | 0 | 55.627 | 35.603 | [5 empty] | 0 | 0.723 | 40 | 2.1177 | 1.9378 | 1.1994 | 1.0526 | 0.88518 | 41.7985
2005-10-31 | 1:12 | 0 | 21.581 | 0 | 2 | 0 | 29.771 | 30.541 | 29.097 | 29.121 | 17.665 | 24.737 | 15.395 | 0 | 0 | 58.655 | 56.346 | 49.908 | 22.449 | 0 | 0 | 55.617 | 35.524 | [5 empty] | 0 | 0.65 | 41 | 2.1134 | 1.9337 | 1.1993 | 1.0526 | 0.88103 | 41.6884
2005-10-31 | 1:13 | 0 | 21.557 | 0 | 1 | 0 | 29.651 | 30.251 | 29.072 | 29.097 | 17.592 | 24.737 | 15.345 | 0 | 0 | 58.589 | 56.346 | 49.841 | 22.471 | 0 | 0 | 55.664 | 35.548 | [5 empty] | 0 | 0.554 | 42 | 2.1279 | 1.9475 | 1.1999 | 1.0526 | 0.89487 | 42.0535
2005-10-31 | 1:14 | 0 | 21.581 | 0 | 2 | 0 | 29.506 | 30.131 | 29.047 | 28.976 | 17.469 | 24.712 | 15.42 | 1 | 0 | 58.612 | 56.346 | 49.794 | 22.425 | 0 | 0 | 55.617 | 35.569 | [5 empty] | 0 | 0.53 | 43 | 2.1061 | 1.9267 | 1.199 | 1.0526 | 0.87411 | 41.5039
2005-10-31 | 1:15 | 0 | 21.557 | 0 | 2 | 0 | 38.813 | 29.987 | 28.976 | 28.998 | 23.964 | 24.808 | 15.395 | 0 | 0 | 58.566 | 56.325 | 49.771 | 22.449 | 0 | 0 | 55.526 | 35.593 | [5 empty] | 0 | 9.815 | 44 | 2.1134 | 1.9337 | 1.1993 | 1.0526 | 0.88103 | 41.6884
2005-10-31 | 1:16 | 0 | 21.557 | 0 | 2 | 0 | 41.327 | 30.347 | 28.832 | 28.927 | 21.15 | 24.882 | 15.395 | 0 | 0 | 58.612 | 56.302 | 49.771 | 22.4 | 0 | 0 | 55.389 | 35.593 | [5 empty] | 0 | 12.4 | 45 | 2.1134 | 1.9337 | 1.1993 | 1.0526 | 0.88103 | 41.6884
2005-10-31 | 1:17 | 0 | 21.557 | 0 | 2 | 0 | 32.986 | 42.432 | 28.712 | 28.903 | 19.716 | 24.688 | 15.42 | 0 | 0 | 58.543 | 56.28 | 49.771 | 22.449 | 0 | 0 | 55.526 | 35.524 | [5 empty] | 0 | 4.083 | 46 | 2.1061 | 1.9267 | 1.199 | 1.0526 | 0.87411 | 41.5039
2005-10-31 | 1:18 | 0 | 21.557 | 0 | 2 | 0 | 30.565 | 37.545 | 28.687 | 28.712 | 19.123 | 24.761 | 15.42 | 1 | 0 | 58.543 | 56.302 | 49.841 | 22.449 | 0 | 0 | 55.594 | 35.524 | [5 empty] | 0 | 1.853 | 47 | 2.1061 | 1.9267 | 1.199 | 1.0526 | 0.87411 | 41.5039
2005-10-31 | 1:19 | 0 | 21.532 | 0 | 2 | 0 | 29.746 | 32.419 | 28.687 | 28.589 | 18.801 | 24.761 | 15.566 | 0 | 0 | 58.52 | 56.28 | 49.726 | 22.425 | 0 | 0 | 55.664 | 35.5 | [5 empty] | 0 | 1.157 | 48 | 2.0636 | 1.8863 | 1.1973 | 1.0526 | 0.8337 | 40.4006
2005-10-31 | 1:20 | 0 | 21.566 | 0 | 2 | 0 | 29.467 | 30.769 | 28.672 | 28.697 | 18.467 | 24.771 | 15.553 | 0 | 0 | 58.552 | 56.334 | 49.736 | 22.459 | 0 | 0 | 55.65 | 35.51 | [5 empty] | 0 | 0.77 | 49 | 2.0674 | 1.8899 | 1.1974 | 1.0526 | 0.8373 | 40.5007
2005-10-31 | 1:21 | 0 | 21.532 | 0 | 1 | 0 | 29.192 | 30.082 | 28.613 | 28.567 | 18.283 | 24.761 | 15.518 | 0 | 0 | 58.477 | 56.234 | 49.726 | 22.449 | 0 | 0 | 55.594 | 35.452 | [5 empty] | 0 | 0.625 | 50 | 2.0776 | 1.8996 | 1.1978 | 1.0526 | 0.84699 | 40.7683
2005-10-31 | 1:22 | 0 | 21.532 | 0 | 2 | 0 | 29.047 | 29.817 | 28.613 | 28.518 | 18.135 | 24.882 | 15.493 | 0 | 0 | 58.543 | 56.257 | 49.703 | 22.425 | 0 | 0 | 55.571 | 35.476 | [5 empty] | 0 | 0.529 | 51 | 2.0848 | 1.9065 | 1.1981 | 1.0526 | 0.85391 | 40.9579
2005-10-31 | 1:23 | 0 | 21.532 | 1 | 2 | 0 | 28.952 | 29.481 | 28.518 | 28.567 | 17.987 | 24.906 | 15.468 | 0 | 0 | 58.52 | 56.234 | 49.656 | 22.4 | 0 | 0 | 55.571 | 35.476 | [5 empty] | 0 | 0.385 | 52 | 2.0921 | 1.9135 | 1.1984 | 1.0526 | 0.86083 | 41.1461
2005-10-31 | 1:24 | 0 | 21.51 | 0 | 2 | 0 | 28.903 | 29.386 | 28.373 | 28.398 | 17.788 | 24.808 | 15.468 | 0 | 0 | 58.498 | 56.234 | 49.794 | 22.425 | 0 | 0 | 55.526 | 35.5 | [5 empty] | 0 | 0.505 | 53 | 2.0921 | 1.9135 | 1.1984 | 1.0526 | 0.86083 | 41.1461
2005-10-31 | 1:25 | 0 | 21.566 | 0 | 2 | 0 | 28.842 | 29.251 | 28.432 | 28.479 | 17.776 | 24.796 | 15.455 | 0 | 0 | 58.463 | 56.223 | 49.736 | 22.483 | 0 | 0 | 55.606 | 35.533 | [5 empty] | 0 | 0.363 | 54 | 2.0959 | 1.9171 | 1.1986 | 1.0526 | 0.86442 | 41.2435
2005-10-31 | 1:26 | 0 | 21.574 | 0 | 2 | 0 | 35.493 | 29.209 | 28.39 | 28.344 | 24.006 | 24.825 | 15.435 | 0 | 0 | 58.493 | 56.186 | 49.652 | 22.417 | 0 | 0 | 55.545 | 35.447 | [5 empty] | 0 | 7.149 | 55 | 2.1017 | 1.9226 | 1.1988 | 1.0526 | 0.86996 | 41.3926
2005-10-31 | 1:27 | 0 | 21.549 | 0 | 2 | 1 | 46.12 | 29.668 | 28.319 | 28.319 | 24.126 | 24.874 | 15.413 | 1 | 0 | 58.45 | 56.186 | 49.698 | 22.442 | 0 | 0 | 55.498 | 35.471 | [5 empty] | 0 | 17.801 | 56 | 2.1081 | 1.9287 | 1.1991 | 1.0526 | 0.87605 | 41.5557
2005-10-31 | 1:28 | 0 | 21.527 | 0 | 3 | 0 | 46.718 | 42.542 | 28.295 | 28.415 | 24.175 | 24.803 | 15.46 | 1 | 0 | 58.427 | 56.163 | 49.628 | 22.417 | 0 | 0 | 55.589 | 35.541 | [5 empty] | 0 | 18.303 | 0 | 2.0944 | 1.9157 | 1.1985 | 1.0526 | 0.86304 | 41.2061
2005-10-31 | 1:29 | 1 | 21.549 | 0 | 2 | 0 | 46.076 | 46.167 | 28.439 | 28.27 | 24.2 | 24.994 | 15.413 | 1 | 0 | 58.473 | 56.186 | 49.628 | 22.442 | 0 | 0 | 55.475 | 35.541 | [5 empty] | 21.549 | 17.806 | 1 | 2.1081 | 1.9287 | 2.6464 | 2.5 | -0.57132 | -27.1007
2005-10-31 | 1:30 | 0 | 21.549 | 0 | 2 | 0 | 46.076 | 46.281 | 28.366 | 28.199 | 24.44 | 24.899 | 15.485 | 1 | 0 | 58.427 | 56.163 | 49.698 | 22.417 | 0 | 0 | 55.407 | 35.565 | [5 empty] | 0 | 17.877 | 2 | 2.0872 | 1.9088 | 2.6456 | 2.5 | -0.59125 | -28.3278
2005-10-31 | 1:31 | 0 | 21.579 | 0 | 1 | 0 | 46.47 | 46.081 | 28.42 | 28.204 | 24.59 | 24.928 | 15.465 | 2 | 0 | 58.454 | 56.191 | 49.703 | 22.471 | 0 | 0 | 55.412 | 35.569 | [5 empty] | 0 | 18.266 | 3 | 2.093 | 1.9143 | 2.6458 | 2.5 | -0.58571 | -27.9844
2005-10-31 | 1:32 | 0 | 21.603 | 0 | 2 | 0 | 46.905 | 46.263 | 28.515 | 28.251 | 24.855 | 24.975 | 15.443 | 1 | 0 | 58.454 | 56.191 | 49.68 | 22.471 | 0 | 0 | 55.389 | 35.569 | [5 empty] | 0 | 18.654 | 4 | 2.0994 | 1.9204 | 2.6461 | 2.5 | -0.57962 | -27.609
2005-10-31 | 1:33 | 0 | 21.549 | 1 | 2 | 0 | 47.014 | 46.762 | 28.535 | 28.39 | 25.235 | 24.923 | 15.435 | 1 | 0 | 58.45 | 56.163 | 49.698 | 22.442 | 0 | 0 | 55.314 | 35.517 | [5 empty] | 0 | 18.624 | 5 | 2.1017 | 1.9226 | 2.6462 | 2.5 | -0.57741 | -27.473
2005-10-31 | 1:34 | 0 | 21.527 | 0 | 2 | 0 | 47.222 | 47.129 | 28.729 | 28.344 | 25.477 | 25.043 | 15.413 | 1 | 0 | 58.45 | 56.163 | 49.605 | 22.442 | 0 | 0 | 55.407 | 35.471 | [5 empty] | 0 | 18.878 | 6 | 2.1081 | 1.9287 | 2.6464 | 2.5 | -0.57132 | -27.1007
2005-10-31 | 1:35 | 1 | 21.603 | 0 | 2 | 0 | 47.479 | 47.294 | 28.734 | 28.42 | 25.867 | 25.024 | 15.443 | 1 | 0 | 58.5 | 56.213 | 49.656 | 22.471 | 0 | 0 | 55.389 | 35.521 | [5 empty] | 21.603 | 19.059 | 7 | 2.0994 | 1.9204 | 2.6461 | 2.5 | -0.57962 | -27.609
2005-10-31 | 1:36 | 0 | 21.574 | 0 | 2 | 0 | 48.207 | 47.588 | 28.729 | 28.56 | 26.247 | 24.923 | 15.485 | 1 | 0 | 58.493 | 56.163 | 49.652 | 22.417 | 0 | 0 | 55.428 | 35.541 | [5 empty] | 0 | 19.647 | 8 | 2.0872 | 1.9088 | 2.6456 | 2.5 | -0.59125 | -28.3278
2005-10-31 | 1:37 | 0 | 21.549 | 0 | 2 | 0 | 48.781 | 47.887 | 28.849 | 28.655 | 26.488 | 24.97 | 15.46 | 2 | 0 | 58.539 | 56.14 | 49.652 | 22.417 | 0 | 0 | 55.337 | 35.517 | [5 empty] | 0 | 20.126 | 9 | 2.0944 | 1.9157 | 2.6459 | 2.5 | -0.58433 | -27.8989
2005-10-31 | 1:38 | 0 | 21.549 | 0 | 2 | 0 | 48.506 | 48.643 | 29.018 | 28.775 | 26.657 | 24.945 | 15.46 | 1 | 0 | 58.493 | 56.14 | 49.652 | 22.442 | 0 | 0 | 55.246 | 35.517 | [5 empty] | 0 | 19.731 | 10 | 2.0944 | 1.9157 | 2.6459 | 2.5 | -0.58433 | -27.8989
2005-10-31 | 1:39 | 0 | 21.549 | 0 | 2 | 0 | 48.368 | 48.94 | 29.04 | 28.849 | 26.897 | 25.043 | 15.46 | 1 | 0 | 58.562 | 56.207 | 49.628 | 22.417 | 0 | 0 | 55.223 | 35.493 | [5 empty] | 0 | 19.519 | 11 | 2.0944 | 1.9157 | 2.6459 | 2.5 | -0.58433 | -27.8989
2005-10-31 | 1:40 | 1 | 21.549 | 0 | 2 | 0 | 48.345 | 48.688 | 29.114 | 28.895 | 26.993 | 24.97 | 15.511 | 1 | 0 | 58.562 | 56.163 | 49.743 | 22.417 | 0 | 0 | 55.2 | 35.517 | [5 empty] | 21.549 | 19.45 | 12 | 2.0796 | 1.9016 | 2.6453 | 2.5 | -0.59844 | -28.777
2005-10-31 | 1:41 | 0 | 21.574 | 0 | 1 | 0 | 48.391 | 48.62 | 29.329 | 28.895 | 27.162 | 25.114 | 15.511 | 2 | 0 | 58.562 | 56.207 | 49.675 | 22.442 | 0 | 0 | 55.223 | 35.517 | [5 empty] | 0 | 19.496 | 13 | 2.0796 | 1.9016 | 2.6453 | 2.5 | -0.59844 | -28.777
2005-10-31 | 1:42 | 0 | 21.549 | 1 | 2 | 0 | 48.597 | 48.667 | 29.45 | 28.994 | 27.38 | 25.164 | 15.485 | 1 | 0 | 58.651 | 56.186 | 49.628 | 22.442 | 0 | 0 | 55.246 | 35.493 | [5 empty] | 0 | 19.603 | 14 | 2.0872 | 1.9088 | 2.6456 | 2.5 | -0.59125 | -28.3278
2005-10-31 | 1:43 | 0 | 21.549 | 0 | 2 | 0 | 48.986 | 48.734 | 29.739 | 29.114 | 27.547 | 25.09 | 15.536 | 1 | 0 | 58.605 | 56.207 | 49.743 | 22.417 | 0 | 0 | 55.176 | 35.517 | [5 empty] | 0 | 19.872 | 15 | 2.0723 | 1.8946 | 2.645 | 2.5 | -0.60536 | -29.212
2005-10-31 | 1:44 | 0 | 21.549 | 0 | 2 | 0 | 48.919 | 49.077 | 30.102 | 29.354 | 27.741 | 25.114 | 15.536 | 1 | 0 | 58.605 | 56.207 | 49.605 | 22.417 | 0 | 0 | 55.155 | 35.493 | [5 empty] | 0 | 19.565 | 16 | 2.0723 | 1.8946 | 2.645 | 2.5 | -0.60536 | -29.212
2005-10-31 | 1:45 | 0 | 21.549 | 0 | 2 | 0 | 49.148 | 49.309 | 30.462 | 29.714 | 27.79 | 25.164 | 15.485 | 2 | 0 | 58.673 | 56.186 | 49.628 | 22.417 | 0 | 0 | 55.132 | 35.495 | [5 empty] | 0 | 19.434 | 17 | 2.0872 | 1.9088 | 2.6456 | 2.5 | -0.59125 | -28.3278
2005-10-31 | 1:46 | 1 | 21.601 | 0 | 2 | 0 | 49.381 | 49.358 | 30.899 | 30.055 | 28.152 | 25.141 | 15.538 | 1 | 0 | 58.701 | 56.234 | 49.633 | 22.444 | 0 | 0 | 55.158 | 35.521 | [5 empty] | 21.601 | 19.326 | 18 | 2.0717 | 1.8941 | 2.645 | 2.5 | -0.60592 | -29.2469
2005-10-31 | 1:47 | 0 | 21.601 | 0 | 2 | 0 | 46.216 | 49.563 | 31.308 | 30.465 | 25.96 | 25.166 | 15.538 | 1 | 0 | 58.678 | 56.28 | 49.838 | 22.564 | 0 | 0 | 55.137 | 35.498 | [5 empty] | 0 | 15.751 | 19 | 2.0717 | 1.8941 | 2.645 | 2.5 | -0.60592 | -29.2469
2005-10-31 | 1:48 | 0 | 21.576 | 0 | 2 | 0 | 36.624 | 49.701 | 31.718 | 30.874 | 23.697 | 25.215 | 15.513 | 0 | 0 | 58.655 | 56.211 | 49.656 | 22.469 | 0 | 0 | 55.09 | 35.498 | [5 empty] | 0 | 5.75 | 20 | 2.079 | 1.901 | 2.6452 | 2.5 | -0.599 | -28.8117
2005-10-31 | 1:49 | 0 | 21.576 | 0 | 2 | 0 | 33.782 | 42.781 | 32.032 | 31.284 | 22.204 | 25.166 | 15.513 | 0 | 0 | 58.678 | 56.188 | 49.701 | 22.469 | 0 | 0 | 55.09 | 35.521 | [5 empty] | 0 | 2.498 | 21 | 2.079 | 1.901 | 2.6452 | 2.5 | -0.599 | -28.8117
2005-10-31 | 1:50 | 0 | 21.625 | 0 | 1 | 0 | 33.125 | 36.438 | 32.321 | 31.767 | 21.576 | 25.166 | 15.488 | 1 | 0 | 58.678 | 56.211 | 49.794 | 22.469 | 0 | 0 | 55.09 | 35.521 | [5 empty] | 0 | 1.358 | 22 | 2.0863 | 1.9079 | 2.6455 | 2.5 | -0.59208 | -28.3794
2005-10-31 | 1:51 | 0 | 21.601 | 0 | 2 | 1 | 32.89 | 34.323 | 32.584 | 32.056 | 20.858 | 25.19 | 15.513 | 0 | 0 | 58.655 | 56.188 | 49.724 | 22.469 | 0 | 0 | 55.067 | 35.498 | [5 empty] | 0 | 0.834 | 23 | 2.079 | 1.901 | 2.6452 | 2.5 | -0.599 | -28.8117
2005-10-31 | 1:52 | 0 | 21.576 | 0 | 2 | 0 | 32.936 | 33.665 | 32.819 | 32.367 | 20.47 | 25.166 | 15.488 | 0 | 0 | 58.655 | 56.211 | 49.794 | 22.444 | 0 | 0 | 55.043 | 35.426 | [5 empty] | 0 | 0.569 | 0 | 2.0863 | 1.9079 | 2.6455 | 2.5 | -0.59208 | -28.3794
2005-10-31 | 1:53 | 0 | 21.576 | 1 | 2 | 0 | 33.007 | 33.452 | 32.984 | 32.63 | 19.686 | 25.141 | 15.463 | 0 | 0 | 58.632 | 56.168 | 49.701 | 22.444 | 0 | 0 | 55.043 | 35.474 | [5 empty] | 0 | 0.377 | 1 | 2.0936 | 1.9148 | 1.0689 | 0.92308 | 0.99176 | 47.3718
2005-10-31 | 1:54 | 0 | 21.576 | 0 | 2 | 0 | 33.17 | 33.407 | 32.96 | 32.984 | 19.266 | 25.166 | 15.463 | 0 | 0 | 58.655 | 56.211 | 49.794 | 22.444 | 0 | 0 | 55.02 | 35.498 | [5 empty] | 0 | 0.186 | 2 | 2.0936 | 1.9148 | 1.0689 | 0.92308 | 0.99176 | 47.3718
2005-10-31 | 1:55 | 0 | 21.576 | 0 | 2 | 0 | 33.218 | 33.476 | 32.912 | 32.936 | 19.168 | 25.215 | 15.463 | 0 | 0 | 58.632 | 56.257 | 49.701 | 22.54 | 0 | 0 | 55.067 | 35.591 | [5 empty] | 0 | 0.282 | 3 | 2.0936 | 1.9148 | 1.0689 | 0.92308 | 0.99176 | 47.3718
2005-10-31 | 1:56 | 0 | 21.601 | 0 | 2 | 0 | 33.359 | 33.5 | 32.725 | 32.866 | 19.093 | 25.141 | 15.438 | 0 | 0 | 58.589 | 56.168 | 49.701 | 22.469 | 0 | 0 | 54.999 | 35.545 | [5 empty] | 0 | 0.493 | 4 | 2.1009 | 1.9218 | 1.0692 | 0.92308 | 0.99868 | 47.5371
2005-10-31 | 1:57 | 0 | 21.601 | 0 | 2 | 0 | 40.549 | 33.594 | 32.677 | 32.866 | 26.13 | 25.24 | 15.488 | 0 | 0 | 58.589 | 56.168 | 49.68 | 22.444 | 0 | 0 | 54.952 | 35.567 | [5 empty] | 0 | 7.683 | 5 | 2.0863 | 1.9079 | 1.0686 | 0.92308 | 0.98484 | 47.2055
2005-10-31 | 1:58 | 0 | 21.601 | 0 | 2 | 0 | 45.413 | 33.948 | 32.223 | 32.677 | 22.638 | 25.141 | 15.488 | 1 | 0 | 58.566 | 56.145 | 49.771 | 22.444 | 0 | 0 | 54.884 | 35.567 | [5 empty] | 0 | 12.736 | 6 | 2.0863 | 1.9079 | 1.0686 | 0.92308 | 0.98484 | 47.2055
2005-10-31 | 1:59 | 0 | 21.601 | 0 | 1 | 0 | 36.954 | 44.589 | 31.887 | 32.536 | 20.809 | 25.166 | 15.415 | 0 | 0 | 58.543 | 56.121 | 49.747 | 22.469 | 0 | 0 | 54.861 | 35.545 | [5 empty] | 0 | 4.418 | 7 | 2.1076 | 1.9281 | 1.0695 | 0.92308 | 1.0051 | 47.6881
2005-10-31 | 2:00 | 0 | 21.576 | 0 | 2 | 0 | 34.347 | 41.865 | 31.647 | 32.152 | 19.762 | 25.19 | 15.365 | 1 | 0 | 58.475 | 56.098 | 49.656 | 22.444 | 0 | 0 | 54.929 | 35.498 | [5 empty] | 0 | 2.195 | 8 | 2.1221 | 1.942 | 1.0701 | 0.92308 | 1.0189 | 48.0131
2005-10-31 | 2:01 | 0 | 21.608 | 0 | 2 | 0 | 33.414 | 36.538 | 31.46 | 31.823 | 19.103 | 25.127 | 15.423 | 0 | 0 | 58.505 | 56.128 | 49.801 | 22.452 | 0 | 0 | 54.936 | 35.529 | [5 empty] | 0 | 1.591 | 9 | 2.1052 | 1.9259 | 1.0694 | 0.92308 | 1.0028 | 47.6357
2005-10-31 | 2:02 | 0 | 21.576 | 0 | 2 | 0 | 32.842 | 34.534 | 31.139 | 31.598 | 18.673 | 25.141 | 15.365 | 0 | 0 | 58.454 | 56.075 | 49.68 | 22.444 | 0 | 0 | 54.929 | 35.521 | [5 empty] | 0 | 1.244 | 10 | 2.1221 | 1.942 | 1.0701 | 0.92308 | 1.0189 | 48.0131
2005-10-31 | 2:03 | 0 | 21.576 | 0 | 1 | 0 | 32.441 | 33.711 | 31.092 | 31.259 | 18.402 | 25.19 | 15.415 | 0 | 0 | 58.475 | 56.054 | 49.633 | 22.493 | 0 | 0 | 54.905 | 35.498 | [5 empty] | 0 | 1.182 | 11 | 2.1076 | 1.9281 | 1.0695 | 0.92308 | 1.0051 | 47.6881
2005-10-31 | 2:04 | 0 | 21.554 | 0 | 2 | 0 | 32.056 | 33.218 | 30.803 | 31.164 | 18.329 | 25.07 | 15.365 | 0 | 0 | 58.409 | 56.03 | 49.61 | 22.42 | 0 | 0 | 54.814 | 35.474 | [5 empty] | 0 | 0.892 | 12 | 2.1221 | 1.942 | 1.0701 | 0.92308 | 1.0189 | 48.0131
2005-10-31 | 2:05 | 0 | 21.608 | 1 | 2 | 0 | 31.774 | 32.78 | 30.761 | 30.882 | 18.434 | 25.222 | 15.448 | 0 | 0 | 58.505 | 56.105 | 49.617 | 22.452 | 0 | 0 | 54.845 | 35.517 | [5 empty] | 0 | 0.892 | 13 | 2.0979 | 1.919 | 1.0691 | 0.92308 | 0.99592 | 47.4711
2005-10-31 | 2:06 | 0 | 21.574 | 0 | 2 | 0 | 31.426 | 32.365 | 30.607 | 30.727 | 18.399 | 25.164 | 15.362 | 0 | 0 | 58.429 | 56.028 | 49.54 | 22.393 | 0 | 0 | 54.789 | 35.423 | [5 empty] | 0 | 0.699 | 14 | 2.123 | 1.9428 | 1.0701 | 0.92308 | 1.0197 | 48.0324
2005-10-31 | 2:07 | 0 | 21.557 | 0 | 2 | 0 | 31.264 | 32.154 | 30.516 | 30.612 | 18.552 | 25.048 | 15.443 | 0 | 0 | 58.411 | 56.056 | 49.544 | 22.447 | 0 | 0 | 54.793 | 35.452 | [5 empty] | 0 | 0.652 | 15 | 2.0994 | 1.9204 | 1.0691 | 0.92308 | 0.9973 | 47.5041
2005-10-31 | 2:08 | 0 | 21.549 | 0 | 1 | 0 | 34.648 | 31.764 | 30.342 | 30.511 | 25.718 | 24.97 | 15.435 | 0 | 0 | 58.361 | 55.981 | 49.54 | 22.393 | 0 | 0 | 54.789 | 35.447 | [5 empty] | 0 | 4.137 | 16 | 2.1017 | 1.9226 | 1.0692 | 0.92308 | 0.99952 | 47.5568
2005-10-31 | 2:09 | 0 | 21.549 | 0 | 2 | 0 | 45.847 | 31.571 | 30.151 | 30.511 | 22.947 | 24.948 | 15.46 | 1 | 0 | 58.338 | 55.981 | 49.584 | 22.393 | 0 | 0 | 54.698 | 35.447 | [5 empty] | 0 | 15.336 | 17 | 2.0944 | 1.9157 | 1.0689 | 0.92308 | 0.9926 | 47.3917
2005-10-31 | 2:10 | 0 | 21.549 | 0 | 2 | 0 | 35.682 | 41.157 | 29.957 | 30.222 | 21.12 | 25.019 | 15.485 | 0 | 0 | 58.317 | 55.981 | 49.493 | 22.417 | 0 | 0 | 54.698 | 35.447 | [5 empty] | 0 | 5.46 | 18 | 2.0872 | 1.9088 | 1.0687 | 0.92308 | 0.98568 | 47.2255
2005-10-31 | 2:11 | 0 | 21.549 | 0 | 2 | 0 | 32.439 | 41.511 | 29.763 | 30.102 | 20.179 | 24.923 | 15.511 | 0 | 0 | 58.295 | 55.935 | 49.493 | 22.417 | 0 | 0 | 54.651 | 35.402 | [5 empty] | 0 | 2.337 | 19 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:12 | 0 | 21.549 | 0 | 2 | 0 | 31.257 | 34.978 | 29.717 | 29.788 | 19.684 | 24.923 | 15.609 | 0 | 0 | 58.272 | 55.958 | 49.47 | 22.393 | 0 | 0 | 54.674 | 35.354 | [5 empty] | 0 | 1.469 | 20 | 2.0511 | 1.8744 | 1.0672 | 0.92308 | 0.95135 | 46.3834
2005-10-31 | 2:13 | 0 | 21.527 | 0 | 2 | 0 | 30.776 | 32.627 | 29.619 | 29.717 | 19.191 | 24.994 | 15.536 | 0 | 0 | 58.295 | 55.935 | 49.423 | 22.393 | 0 | 0 | 54.698 | 35.354 | [5 empty] | 0 | 1.059 | 21 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:14 | 0 | 21.549 | 0 | 1 | 0 | 30.438 | 31.644 | 29.548 | 29.619 | 19.09 | 25.068 | 15.583 | 1 | 0 | 58.317 | 55.935 | 49.446 | 22.393 | 0 | 0 | 54.698 | 35.33 | [5 empty] | 0 | 0.819 | 22 | 2.0586 | 1.8816 | 1.0675 | 0.92308 | 0.95855 | 46.5624
2005-10-31 | 2:15 | 0 | 21.549 | 0 | 2 | 0 | 30.246 | 31.137 | 29.428 | 29.597 | 18.967 | 24.899 | 15.558 | 0 | 0 | 58.249 | 55.911 | 49.423 | 22.417 | 0 | 0 | 54.698 | 35.354 | [5 empty] | 0 | 0.649 | 23 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:16 | 0 | 21.549 | 1 | 2 | 0 | 30.126 | 30.847 | 29.354 | 29.548 | 18.894 | 24.85 | 15.536 | 0 | 0 | 58.249 | 55.935 | 49.493 | 22.417 | 0 | 0 | 54.628 | 35.402 | [5 empty] | 0 | 0.578 | 24 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:17 | 0 | 21.495 | 0 | 2 | 0 | 29.925 | 30.575 | 29.3 | 29.3 | 18.739 | 24.842 | 15.526 | 0 | 0 | 58.219 | 55.881 | 49.439 | 22.385 | 0 | 0 | 54.597 | 35.392 | [5 empty] | 0 | 0.625 | 25 | 2.0752 | 1.8974 | 1.0682 | 0.92308 | 0.97433 | 46.9503
2005-10-31 | 2:18 | 0 | 21.527 | 0 | 2 | 0 | 29.812 | 30.391 | 29.258 | 29.283 | 18.721 | 24.825 | 15.511 | 0 | 0 | 58.249 | 55.89 | 49.493 | 22.393 | 0 | 0 | 54.628 | 35.402 | [5 empty] | 0 | 0.529 | 26 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:19 | 0 | 21.527 | 0 | 1 | 0 | 30.801 | 30.246 | 29.187 | 29.283 | 26.321 | 24.923 | 15.511 | 0 | 0 | 58.249 | 55.867 | 49.332 | 22.368 | 0 | 0 | 54.674 | 35.471 | [5 empty] | 0 | 1.518 | 27 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:20 | 0 | 21.527 | 0 | 2 | 0 | 45.915 | 30.173 | 29.018 | 29.089 | 22.586 | 24.779 | 15.583 | 0 | 0 | 58.183 | 55.89 | 49.332 | 22.393 | 0 | 0 | 54.651 | 35.378 | [5 empty] | 0 | 16.826 | 28 | 2.0586 | 1.8816 | 1.0675 | 0.92308 | 0.95855 | 46.5624
2005-10-31 | 2:21 | 0 | 21.527 | 0 | 2 | 0 | 35.282 | 38.456 | 28.922 | 29.018 | 20.613 | 24.803 | 15.558 | 1 | 0 | 58.183 | 55.867 | 49.423 | 22.393 | 0 | 0 | 54.607 | 35.402 | [5 empty] | 0 | 6.264 | 29 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:22 | 0 | 21.527 | 0 | 2 | 0 | 31.379 | 41.205 | 28.922 | 28.944 | 19.634 | 24.923 | 15.536 | 0 | 0 | 58.183 | 55.844 | 49.285 | 22.368 | 0 | 0 | 54.607 | 35.354 | [5 empty] | 0 | 2.435 | 30 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:23 | 0 | 21.527 | 0 | 2 | 0 | 30.197 | 34.132 | 28.753 | 28.778 | 19.116 | 24.803 | 15.558 | 0 | 0 | 58.16 | 55.844 | 49.402 | 22.393 | 0 | 0 | 54.56 | 35.33 | [5 empty] | 0 | 1.419 | 31 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:24 | 0 | 21.527 | 0 | 2 | 0 | 29.692 | 31.499 | 28.824 | 28.729 | 18.696 | 24.803 | 15.511 | 0 | 0 | 58.183 | 55.82 | 49.264 | 22.393 | 0 | 0 | 54.513 | 35.306 | [5 empty] | 0 | 0.963 | 32 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:25 | 0 | 21.503 | 0 | 1 | 0 | 29.403 | 30.511 | 28.729 | 28.753 | 18.475 | 24.874 | 15.536 | 0 | 0 | 58.183 | 55.82 | 49.309 | 22.368 | 0 | 0 | 54.537 | 35.354 | [5 empty] | 0 | 0.65 | 33 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:26 | 0 | 21.549 | 0 | 2 | 0 | 29.258 | 30.151 | 28.729 | 28.68 | 18.399 | 24.825 | 15.558 | 0 | 0 | 58.137 | 55.844 | 49.309 | 22.442 | 0 | 0 | 54.56 | 35.33 | [5 empty] | 0 | 0.578 | 34 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:27 | 0 | 21.542 | 0 | 2 | 0 | 29.131 | 29.852 | 28.697 | 28.601 | 18.319 | 24.793 | 15.551 | 0 | 0 | 58.13 | 55.813 | 49.255 | 22.385 | 0 | 0 | 54.506 | 35.299 | [5 empty] | 0 | 0.53 | 35 | 2.0679 | 1.8905 | 1.0679 | 0.92308 | 0.96741 | 46.781
2005-10-31 | 2:28 | 0 | 21.549 | 1 | 2 | 0 | 29.065 | 29.692 | 28.633 | 28.584 | 18.128 | 24.754 | 15.536 | 0 | 0 | 58.137 | 55.82 | 49.285 | 22.417 | 0 | 0 | 54.513 | 35.354 | [5 empty] | 0 | 0.481 | 36 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:29 | 0 | 21.549 | 0 | 2 | 0 | 29.043 | 29.499 | 28.584 | 28.704 | 18.03 | 24.779 | 15.536 | 0 | 0 | 58.114 | 55.797 | 49.355 | 22.393 | 0 | 0 | 54.469 | 35.33 | [5 empty] | 0 | 0.339 | 37 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:30 | 0 | 21.542 | 0 | 2 | 0 | 29.011 | 29.347 | 28.528 | 28.503 | 26.144 | 24.698 | 15.478 | 1 | 0 | 58.062 | 55.746 | 49.234 | 22.385 | 0 | 0 | 54.415 | 35.299 | [5 empty] | 0 | 0.508 | 38 | 2.0892 | 1.9107 | 1.0687 | 0.92308 | 0.98761 | 47.2721
2005-10-31 | 2:31 | 1 | 21.574 | 0 | 2 | 0 | 44.86 | 29.307 | 28.584 | 28.535 | 22.611 | 24.754 | 15.511 | 0 | 0 | 58.091 | 55.797 | 49.218 | 22.417 | 0 | 0 | 54.399 | 35.354 | [5 empty] | 21.574 | 16.325 | 39 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:32 | 0 | 21.549 | 0 | 2 | 0 | 34.955 | 36.928 | 28.535 | 28.488 | 20.468 | 24.683 | 15.485 | 0 | 0 | 58.071 | 55.753 | 49.218 | 22.417 | 0 | 0 | 54.376 | 35.306 | [5 empty] | 0 | 6.467 | 40 | 2.0872 | 1.9088 | 1.0687 | 0.92308 | 0.98568 | 47.2255
2005-10-31 | 2:33 | 0 | 21.527 | 0 | 2 | 0 | 30.703 | 40.054 | 28.488 | 28.415 | 19.362 | 24.729 | 15.485 | 1 | 0 | 58.071 | 55.776 | 49.241 | 22.393 | 0 | 0 | 54.399 | 35.282 | [5 empty] | 0 | 2.288 | 41 | 2.0872 | 1.9088 | 1.0687 | 0.92308 | 0.98568 | 47.2255
2005-10-31 | 2:34 | 0 | 21.549 | 0 | 2 | 0 | 29.499 | 33.122 | 28.488 | 28.368 | 18.869 | 24.825 | 15.485 | 0 | 0 | 58.091 | 55.753 | 49.218 | 22.417 | 0 | 0 | 54.422 | 35.306 | [5 empty] | 0 | 1.131 | 42 | 2.0872 | 1.9088 | 1.0687 | 0.92308 | 0.98568 | 47.2255
2005-10-31 | 2:35 | 0 | 21.549 | 0 | 2 | 0 | 29.114 | 30.607 | 28.513 | 28.344 | 18.449 | 24.85 | 15.511 | 0 | 0 | 58.071 | 55.753 | 49.171 | 22.393 | 0 | 0 | 54.446 | 35.306 | [5 empty] | 0 | 0.77 | 43 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:36 | 0 | 21.495 | 0 | 2 | 0 | 28.866 | 29.756 | 28.287 | 28.358 | 18.17 | 24.627 | 15.478 | 0 | 0 | 57.996 | 55.699 | 49.278 | 22.41 | 0 | 0 | 54.345 | 35.275 | [5 empty] | 0 | 0.508 | 44 | 2.0892 | 1.9107 | 1.0687 | 0.92308 | 0.98761 | 47.2721
2005-10-31 | 2:37 | 0 | 21.549 | 0 | 2 | 0 | 28.753 | 29.452 | 28.368 | 28.27 | 18.004 | 24.658 | 15.536 | 0 | 0 | 58.071 | 55.776 | 49.285 | 22.442 | 0 | 0 | 54.352 | 35.33 | [5 empty] | 0 | 0.483 | 45 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:38 | 0 | 21.542 | 0 | 2 | 0 | 28.697 | 29.202 | 28.263 | 28.336 | 17.899 | 24.627 | 15.526 | 0 | 0 | 57.996 | 55.676 | 49.14 | 22.385 | 0 | 0 | 54.322 | 35.299 | [5 empty] | 0 | 0.361 | 46 | 2.0752 | 1.8974 | 1.0682 | 0.92308 | 0.97433 | 46.9503
2005-10-31 | 2:39 | 0 | 21.549 | 0 | 2 | 0 | 28.633 | 29.089 | 28.199 | 28.199 | 17.733 | 24.634 | 15.536 | 0 | 0 | 58.025 | 55.706 | 49.194 | 22.417 | 0 | 0 | 54.331 | 35.306 | [5 empty] | 0 | 0.434 | 47 | 2.0723 | 1.8946 | 1.0681 | 0.92308 | 0.97156 | 46.8827
2005-10-31 | 2:40 | 0 | 21.574 | 1 | 2 | 0 | 28.488 | 29.018 | 28.224 | 28.079 | 17.66 | 24.705 | 15.634 | 0 | 0 | 58.025 | 55.683 | 49.126 | 22.417 | 0 | 0 | 54.376 | 35.306 | [5 empty] | 0 | 0.409 | 48 | 2.0438 | 1.8675 | 1.0669 | 0.92308 | 0.94443 | 46.2101
2005-10-31 | 2:41 | 0 | 21.495 | 0 | 2 | 0 | 28.457 | 28.891 | 28.192 | 28.118 | 23.759 | 24.698 | 15.526 | 0 | 0 | 57.996 | 55.652 | 49.211 | 22.361 | 0 | 0 | 54.301 | 35.251 | [5 empty] | 0 | 0.339 | 49 | 2.0752 | 1.8974 | 1.0682 | 0.92308 | 0.97433 | 46.9503
2005-10-31 | 2:42 | 0 | 21.549 | 0 | 3 | 0 | 43.743 | 28.8 | 28.199 | 28.126 | 24.683 | 24.85 | 15.558 | 1 | 0 | 58.048 | 55.659 | 49.08 | 22.393 | 0 | 0 | 54.376 | 35.306 | [5 empty] | 0 | 15.617 | 50 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:43 | 0 | 21.549 | 0 | 2 | 0 | 45.985 | 36.27 | 28.246 | 28.103 | 24.729 | 24.803 | 15.558 | 1 | 0 | 57.98 | 55.683 | 49.126 | 22.417 | 0 | 0 | 54.331 | 35.306 | [5 empty] | 0 | 17.882 | 51 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:44 | 0 | 21.549 | 0 | 2 | 0 | 45.938 | 45.044 | 28.199 | 28.103 | 24.634 | 24.85 | 15.558 | 1 | 0 | 57.98 | 55.659 | 49.15 | 22.442 | 0 | 0 | 54.261 | 35.306 | [5 empty] | 0 | 17.835 | 52 | 2.0659 | 1.8885 | 1.0678 | 0.92308 | 0.96547 | 46.7333
2005-10-31 | 2:45 | 0 | 21.549 | 0 | 2 | 0 | 45.938 | 45.962 | 28.103 | 28.03 | 24.585 | 24.899 | 15.511 | 1 | 0 | 57.957 | 55.638 | 49.103 | 22.417 | 0 | 0 | 54.238 | 35.294 | [5 empty] | 0 | 17.908 | 53 | 2.0796 | 1.9016 | 1.0683 | 0.92308 | 0.97848 | 47.0513
2005-10-31 | 2:46 | 1 | 21.53 | 0 | 2 | 0 | 45.943 | 45.873 | 28.275 | 28.01 | 24.565 | 24.999 | 15.44 | 1 | 0 | 57.939 | 55.596 | 49.014 | 22.373 | 0 | 0 | 54.196 | 35.194 | [5 empty] | 21.53 | 17.933 | 54 | 2.1003 | 1.9212 | 1.0692 | 0.92308 | 0.99813 | 47.5239
2005-10-31 | 2:47 | 0 | 21.53 | 0 | 2 | 0 | 45.92 | 46.057 | 28.3 | 27.986 | 24.734 | 24.904 | 15.465 | 1 | 0 | 57.939 | 55.62 | 49.129 | 22.398 | 0 | 0 | 54.196 | 35.218 | [5 empty] | 0 | 17.934 | 55 | 2.093 | 1.9143 | 1.0689 | 0.92308 | 0.99121 | 47.3586
2005-10-31 | 2:48 | 0 | 21.554 | 0 | 2 | 0 | 46.057 | 46.104 | 28.371 | 28.081 | 24.83 | 24.879 | 15.415 | 2 | 0 | 57.939 | 55.62 | 49.084 | 22.398 | 0 | 0 | 54.219 | 35.218 | [5 empty] | 0 | 17.976 | 56 | 2.1076 | 1.9281 | 1.0695 | 0.92308 | 1.0051 | 47.6881
2005-10-31 | 2:49 | 0 | 21.53 | 1 | 2 | 0 | 46.172 | 46.242 | 28.395 | 28.13 | 25.119 | 24.904 | 15.39 | 1 | 0 | 57.984 | 55.62 | 49.152 | 22.398 | 0 | 0 | 54.175 | 35.218 | [5 empty] | 0 | 18.042 | 57 | 2.1148 | 1.935 | 1.0698 | 0.92308 | 1.012 | 47.8511
2005-10-31 | 2:50 | 0 | 21.562 | 0 | 2 | 0 | 46.363 | 46.34 | 28.547 | 28.236 | 25.369 | 24.886 | 15.448 | 1 | 0 | 57.991 | 55.627 | 49.115 | 22.43 | 0 | 0 | 54.182 | 35.225 | [5 empty] | 0 | 18.127 | 58 | 2.0979 | 1.919 | 1.0691 | 0.92308 | 0.99592 | 47.4711
2005-10-31 | 2:51 | 1 | 21.53 | 0 | 2 | 0 | 46.309 | 46.585 | 28.685 | 28.3 | 25.553 | 24.904 | 15.44 | 1 | 0 | 58.007 | 55.62 | 49.061 | 22.373 | 0 | 0 | 54.105 | 35.218 | [5 empty] | 21.53 | 18.009 | 59 | 2.1003 | 1.9212 | 1.0692 | 0.92308 | 0.99813 | 47.5239
2005-10-31 | 2:52 | 0 | 21.53 | 0 | 2 | 0 | 46.309 | 46.676 | 28.636 | 28.395 | 25.747 | 24.928 | 15.44 | 2 | 0 | 58.03 | 55.62 | 49.199 | 22.398 | 0 | 0 | 54.105 | 35.242 | [5 empty] | 0 | 17.914 | 60 | 2.1003 | 1.9212 | 1.0692 | 0.92308 | 0.99813 | 47.5239
2005-10-31 | 2:53 | 0 | 21.579 | 0 | 2 | 0 | 46.379 | 46.631 | 28.756 | 28.444 | 26.012 | 25.048 | 15.415 | 1 | 0 | 58.05 | 55.62 | 49.038 | 22.398 | 0 | 0 | 54.082 | 35.218 | [5 empty] | 0 | 17.935 | 61 | 2.1076 | 1.9281 | 1.0695 | 0.92308 | 1.0051 | 47.6881
2005-10-31 | 2:54 | 0 | 21.53 | 0 | 2 | 0 | 46.928 | 46.631 | 28.925 | 28.564 | 26.348 | 25.07 | 15.415 | 1 | 0 | 58.073 | 55.62 | 49.061 | 22.373 | 0 | 0 | 54.105 | 35.194 | [5 empty] | 0 | 18.364 | 62 | 2.1076 | 1.9281 | 1.0695 | 0.92308 | 1.0051 | 47.6881
2005-10-31 | 2:55 | 0 | 21.554 | 0 | 2 | 0 | 47.707 | 46.837 | 28.974 | 28.636 | 26.613 | 25.119 | 15.465 | 1 | 0 | 58.073 | 55.664 | 49.061 | 22.398 | 0 | 0 | 54.061 | 35.218 | [5 empty] | 0 | 19.071 | 63 | 2.093 | 1.9143 | 1.0689 | 0.92308 | 0.99121 | 47.3586
2005-10-31 | 2:56 | 0 | 21.579 | 0 | 2 | 1 | 47.455 | 47.549 | 29.119 | 28.636 | 26.757 | 25.144 | 15.44 | 1 | 0 | 58.096 | 55.62 | 49.061 | 22.373 | 0 | 0 | 54.082 | 35.218 | [5 empty] | 0 | 18.819 | 64 | 2.1003 | 1.9212 | 1.0692 | 0.92308 | 0.99813 | 47.5239
2005-10-31 | 2:57 | 1 | 21.53 | 0 | 2 | 0 | 47.411 | 47.915 | 29.334 | 28.78 | 26.926 | 25.144 | 15.44 | 2 | 0 | 58.119 | 55.62 | 49.084 | 22.349 | 0 | 0 | 54.082 | 35.242 | [5 empty] | 21.53 | 18.631 | 0 | 2.1003 | 1.9212 | 1.0692 | 0.92308 | 0.99813 | 47.5239
2005-10-31 | 2:58 | 0 | 21.562 | 0 | 2 | 0 | 47.462 | 47.761 | 29.68 | 29.03 | 27.054 | 25.102 | 15.473 | 1 | 0 | 58.149 | 55.671 | 49.115 | 22.43 | 0 | 0 | 54.112 | 35.294 | [5 empty] | 0 | 18.432 | 1 | 2.0907 | 1.9121 | 1.0412 | 0.89552 | 1.0166 | 48.6234
2005-10-31 | 2:59 | 0 | 21.554 | 1 | 2 | 0 | 47.686 | 47.707 | 30.129 | 29.408 | 27.216 | 25.119 | 15.44 | 1 | 0 | 58.096 | 55.62 | 49.084 | 22.373 | 0 | 0 | 54.061 | 35.263 | [5 empty] | 0 | 18.278 | 2 | 2.1003 | 1.9212 | 1.0416 | 0.89552 | 1.0257 | 48.8358
2005-10-31 | 3:00 | 0 | 21.562 | 0 | 3 | 0 | 47.922 | 47.808 | 30.668 | 29.849 | 27.392 | 25.127 | 15.498 | 1 | 0 | 58.171 | 55.65 | 49.206 | 22.43 | 0 | 0 | 54.091 | 35.294 | [5 empty] | 0 | 18.073 | 3 | 2.0834 | 1.9052 | 1.0409 | 0.89552 | 1.0096 | 48.4612
2005-10-31 | 3:01 | 0 | 21.554 | 0 | 2 | 0 | 48.282 | 48.097 | 31.237 | 30.251 | 27.552 | 25.193 | 15.44 | 1 | 0 | 58.165 | 55.641 | 49.199 | 22.398 | 0 | 0 | 54.082 | 35.287 | [5 empty] | 0 | 18.031 | 4 | 2.1003 | 1.9212 | 1.0416 | 0.89552 | 1.0257 | 48.8358
2005-10-31 | 3:02 | 0 | 21.554 | 0 | 1 | 0 | 48.809 | 48.419 | 31.72 | 30.828 | 27.841 | 25.215 | 15.415 | 2 | 0 | 58.142 | 55.62 | 49.084 | 22.373 | 0 | 0 | 54.037 | 35.311 | [5 empty] | 0 | 17.981 | 5 | 2.1076 | 1.9281 | 1.0419 | 0.89552 | 1.0326 | 48.9955
2005-10-31 | 3:03 | 1 | 21.611 | 0 | 2 | 0 | 49.435 | 48.839 | 32.257 | 31.414 | 27.248 | 25.2 | 15.473 | 1 | 0 | 58.238 | 55.671 | 49.115 | 22.43 | 0 | 0 | 54.112 | 35.366 | [5 empty] | 21.611 | 18.021 | 6 | 2.0907 | 1.9121 | 1.0412 | 0.89552 | 1.0166 | 48.6234
2005-10-31 | 3:04 | 0 | 21.611 | 0 | 2 | 0 | 41.1 | 49.32 | 32.57 | 31.921 | 24.283 | 25.2 | 15.423 | 1 | 0 | 58.194 | 55.671 | 49.183 | 22.43 | 0 | 0 | 54.135 | 35.342 | [5 empty] | 0 | 9.179 | 7 | 2.1052 | 1.9259 | 1.0418 | 0.89552 | 1.0304 | 48.9445
2005-10-31 | 3:05 | 0 | 21.579 | 0 | 2 | 0 | 35.78 | 47.686 | 32.914 | 32.345 | 22.856 | 25.215 | 15.402 | 0 | 0 | 58.176 | 55.631 | 49.119 | 22.361 | 0 | 0 | 54.096 | 35.277 | [5 empty] | 0 | 3.435 | 8 | 2.1113 | 1.9317 | 1.0421 | 0.89552 | 1.0362 | 49.0781
2005-10-31 | 3:06 | 0 | 21.554 | 0 | 2 | 0 | 34.395 | 39.588 | 33.055 | 32.632 | 21.797 | 25.193 | 15.367 | 0 | 0 | 58.165 | 55.62 | 49.131 | 22.398 | 0 | 0 | 54.061 | 35.311 | [5 empty] | 0 | 1.763 | 9 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:07 | 0 | 21.579 | 0 | 2 | 0 | 33.995 | 35.993 | 33.244 | 32.845 | 20.836 | 25.362 | 15.367 | 0 | 0 | 58.187 | 55.643 | 49.108 | 22.373 | 0 | 0 | 54.084 | 35.311 | [5 empty] | 0 | 1.15 | 10 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:08 | 0 | 21.554 | 0 | 2 | 0 | 33.83 | 34.935 | 33.22 | 32.914 | 20.426 | 25.313 | 15.367 | 1 | 0 | 58.21 | 55.62 | 49.108 | 22.373 | 0 | 0 | 54.061 | 35.335 | [5 empty] | 0 | 0.916 | 11 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:09 | 0 | 21.554 | 1 | 2 | 0 | 33.809 | 34.536 | 33.314 | 33.079 | 19.54 | 25.193 | 15.342 | 0 | 0 | 58.165 | 55.596 | 49.155 | 22.373 | 0 | 0 | 54.016 | 35.311 | [5 empty] | 0 | 0.73 | 12 | 2.1288 | 1.9483 | 1.0428 | 0.89552 | 1.0528 | 49.4554
2005-10-31 | 3:10 | 0 | 21.586 | 0 | 1 | 0 | 33.84 | 34.357 | 33.204 | 33.321 | 19.327 | 25.249 | 15.4 | 0 | 0 | 58.174 | 55.627 | 49.276 | 22.38 | 0 | 0 | 54 | 35.366 | [5 empty] | 0 | 0.519 | 13 | 2.1119 | 1.9323 | 1.0421 | 0.89552 | 1.0368 | 49.0908
2005-10-31 | 3:11 | 0 | 21.554 | 0 | 2 | 0 | 33.737 | 34.208 | 33.079 | 33.22 | 19.171 | 25.217 | 15.367 | 0 | 0 | 58.144 | 55.596 | 49.201 | 22.373 | 0 | 0 | 53.923 | 35.335 | [5 empty] | 0 | 0.517 | 14 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:12 | 0 | 21.579 | 0 | 2 | 0 | 33.785 | 34.136 | 33.031 | 33.173 | 18.799 | 25.289 | 15.342 | 0 | 0 | 58.121 | 55.596 | 49.131 | 22.349 | 0 | 0 | 53.946 | 35.335 | [5 empty] | 0 | 0.612 | 15 | 2.1288 | 1.9483 | 1.0428 | 0.89552 | 1.0528 | 49.4554
2005-10-31 | 3:13 | 0 | 21.554 | 0 | 2 | 0 | 33.644 | 34.091 | 32.704 | 33.01 | 23.891 | 25.289 | 15.342 | 0 | 0 | 58.144 | 55.575 | 49.108 | 22.349 | 0 | 0 | 53.923 | 35.289 | [5 empty] | 0 | 0.634 | 16 | 2.1288 | 1.9483 | 1.0428 | 0.89552 | 1.0528 | 49.4554
2005-10-31 | 3:14 | 0 | 21.554 | 0 | 2 | 0 | 45.21 | 34.043 | 32.468 | 32.914 | 25.794 | 25.144 | 15.39 | 0 | 0 | 58.053 | 55.552 | 49.131 | 22.373 | 0 | 0 | 53.902 | 35.311 | [5 empty] | 0 | 12.296 | 17 | 2.1148 | 1.935 | 1.0422 | 0.89552 | 1.0395 | 49.1541
2005-10-31 | 3:15 | 0 | 21.579 | 0 | 1 | 0 | 43.583 | 34.794 | 32.203 | 32.61 | 21.939 | 25.24 | 15.367 | 0 | 0 | 58.076 | 55.552 | 49.108 | 22.373 | 0 | 0 | 53.879 | 35.266 | [5 empty] | 0 | 10.973 | 18 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:16 | 0 | 21.554 | 0 | 2 | 0 | 36.392 | 45.647 | 31.96 | 32.394 | 20.426 | 25.338 | 15.342 | 1 | 0 | 58.03 | 55.552 | 49.084 | 22.349 | 0 | 0 | 53.902 | 35.218 | [5 empty] | 0 | 3.998 | 19 | 2.1288 | 1.9483 | 1.0428 | 0.89552 | 1.0528 | 49.4554
2005-10-31 | 3:17 | 0 | 21.554 | 0 | 2 | 0 | 34.184 | 41.327 | 31.551 | 32.059 | 19.442 | 25.24 | 15.317 | 0 | 0 | 58.009 | 55.529 | 49.084 | 22.349 | 0 | 0 | 53.879 | 35.242 | [5 empty] | 0 | 2.125 | 20 | 2.1361 | 1.9553 | 1.0431 | 0.89552 | 1.0597 | 49.6108
2005-10-31 | 3:18 | 0 | 21.586 | 0 | 2 | 0 | 33.393 | 36.354 | 31.487 | 31.801 | 18.907 | 25.176 | 15.375 | 0 | 0 | 58.016 | 55.536 | 49.138 | 22.38 | 0 | 0 | 53.886 | 35.249 | [5 empty] | 0 | 1.592 | 21 | 2.1192 | 1.9392 | 1.0424 | 0.89552 | 1.0437 | 49.2487
2005-10-31 | 3:19 | 0 | 21.579 | 0 | 1 | 0 | 32.914 | 34.536 | 31.141 | 31.526 | 18.676 | 25.095 | 15.367 | 0 | 0 | 57.964 | 55.529 | 49.084 | 22.373 | 0 | 0 | 53.832 | 35.242 | [5 empty] | 0 | 1.388 | 22 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:20 | 0 | 21.579 | 0 | 2 | 0 | 32.468 | 33.761 | 31.021 | 31.262 | 18.354 | 25.217 | 15.39 | 0 | 0 | 57.987 | 55.529 | 49.063 | 22.373 | 0 | 0 | 53.832 | 35.194 | [5 empty] | 0 | 1.206 | 23 | 2.1148 | 1.935 | 1.0422 | 0.89552 | 1.0395 | 49.1541
2005-10-31 | 3:21 | 0 | 21.579 | 1 | 2 | 0 | 32.105 | 33.244 | 30.757 | 31.021 | 18.158 | 25.073 | 15.317 | 0 | 0 | 57.941 | 55.505 | 49.131 | 22.373 | 0 | 0 | 53.808 | 35.242 | [5 empty] | 0 | 1.084 | 24 | 2.1361 | 1.9553 | 1.0431 | 0.89552 | 1.0597 | 49.6108
2005-10-31 | 3:22 | 0 | 21.554 | 0 | 1 | 0 | 31.794 | 32.821 | 30.732 | 30.877 | 17.934 | 25.095 | 15.367 | 0 | 0 | 57.941 | 55.505 | 49.04 | 22.349 | 0 | 0 | 53.808 | 35.242 | [5 empty] | 0 | 0.917 | 25 | 2.1215 | 1.9414 | 1.0425 | 0.89552 | 1.0459 | 49.299
2005-10-31 | 3:23 | 0 | 21.554 | 0 | 2 | 0 | 31.526 | 32.443 | 30.565 | 30.636 | 17.984 | 25.024 | 15.415 | 1 | 0 | 57.918 | 55.482 | 49.084 | 22.349 | 0 | 0 | 53.808 | 35.266 | [5 empty] | 0 | 0.89 | 26 | 2.1076 | 1.9281 | 1.0419 | 0.89552 | 1.0326 | 48.9955
2005-10-31 | 3:24 | 0 | 21.554 | 0 | 2 | 0 | 31.335 | 32.13 | 30.492 | 30.612 | 17.786 | 25.073 | 15.342 | 0 | 0 | 57.918 | 55.505 | 48.993 | 22.349 | 0 | 0 | 53.832 | 35.218 | [5 empty] | 0 | 0.723 | 27 | 2.1288 | 1.9483 | 1.0428 | 0.89552 | 1.0528 | 49.4554
2005-10-31 | 3:25 | 0 | 21.611 | 0 | 2 | 0 | 40.349 | 31.872 | 30.33 | 30.619 | 24.717 | 24.985 | 15.35 | 0 | 0 | 57.927 | 55.491 | 49.024 | 22.38 | 0 | 0 | 53.816 | 35.225 | [5 empty] | 0 | 9.73 | 28 | 2.1265 | 1.9461 | 1.0427 | 0.89552 | 1.0506 | 49.4055
2005-10-31 | 3:26 | 0 | 21.547 | 0 | 1 | 0 | 44.446 | 31.857 | 30.099 | 30.364 | 21.571 | 25.041 | 15.36 | 0 | 0 | 57.868 | 55.477 | 49.08 | 22.366 | 0 | 0 | 53.734 | 35.187 | [5 empty] | 0 | 14.082 | 29 | 2.1236 | 1.9434 | 1.0426 | 0.89552 | 1.0478 | 49.3429
2005-10-31 | 3:27 | 0 | 21.596 | 0 | 2 | 0 | 35.141 | 42.941 | 29.93 | 30.22 | 19.656 | 24.97 | 15.385 | 0 | 0 | 57.868 | 55.454 | 48.986 | 22.39 | 0 | 0 | 53.734 | 35.187 | [5 empty] | 0 | 4.921 | 30 | 2.1163 | 1.9364 | 1.0423 | 0.89552 | 1.0409 | 49.1856
2005-10-31 | 3:28 | 0 | 21.539 | 0 | 2 | 0 | 32.26 | 41.102 | 29.803 | 29.996 | 18.809 | 24.96 | 15.4 | 1 | 0 | 57.815 | 55.4 | 48.956 | 22.334 | 0 | 0 | 53.68 | 35.155 | [5 empty] | 0 | 2.264 | 31 | 2.1119 | 1.9323 | 1.0421 | 0.89552 | 1.0368 | 49.0908
2005-10-31 | 3:29 | 0 | 21.596 | 0 | 2 | 0 | 31.377 | 34.907 | 29.665 | 29.835 | 18.299 | 25.041 | 15.458 | 0 | 0 | 57.913 | 55.522 | 49.033 | 22.344 | 0 | 0 | 53.71 | 35.187 | [5 empty] | 0 | 1.542 | 32 | 2.095 | 1.9162 | 1.0414 | 0.89552 | 1.0207 | 48.7202
2005-10-31 | 3:30 | 0 | 21.571 | 0 | 1 | 0 | 30.869 | 32.579 | 29.545 | 29.763 | 18.125 | 24.896 | 15.407 | 0 | 0 | 57.822 | 55.431 | 49.056 | 22.39 | 0 | 0 | 53.71 | 35.211 | [5 empty] | 0 | 1.106 | 33 | 2.1099 | 1.9303 | 1.042 | 0.89552 | 1.0348 | 49.0464
2005-10-31 | 3:31 | 0 | 21.539 | 0 | 2 | 0 | 30.452 | 31.705 | 29.442 | 29.464 | 17.821 | 24.913 | 15.352 | 0 | 0 | 57.793 | 55.377 | 48.842 | 22.334 | 0 | 0 | 53.657 | 35.155 | [5 empty] | 0 | 0.988 | 34 | 2.1259 | 1.9456 | 1.0427 | 0.89552 | 1.05 | 49.393
2005-10-31 | 3:32 | 0 | 21.571 | 0 | 2 | 0 | 30.244 | 31.232 | 29.401 | 29.425 | 17.68 | 24.945 | 15.385 | 0 | 0 | 57.799 | 55.407 | 48.986 | 22.39 | 0 | 0 | 53.664 | 35.187 | [5 empty] | 0 | 0.819 | 35 | 2.1163 | 1.9364 | 1.0423 | 0.89552 | 1.0409 | 49.1856
2005-10-31 | 3:33 | 0 | 21.539 | 1 | 2 | 0 | 30.043 | 30.862 | 29.322 | 29.298 | 17.698 | 24.921 | 15.36 | 0 | 0 | 57.779 | 55.407 | 48.963 | 22.366 | 0 | 0 | 53.664 | 35.165 | [5 empty] | 0 | 0.745 | 36 | 2.1236 | 1.9434 | 1.0426 | 0.89552 | 1.0478 | 49.3429
2005-10-31 | 3:34 | 0 | 21.571 | 0 | 1 | 0 | 29.906 | 30.604 | 29.28 | 29.28 | 17.311 | 24.872 | 15.36 | 0 | 0 | 57.756 | 55.384 | 48.872 | 22.366 | 0 | 0 | 53.664 | 35.187 | [5 empty] | 0 | 0.626 | 37 | 2.1236 | 1.9434 | 1.0426 | 0.89552 | 1.0478 | 49.3429
2005-10-31 | 3:35 | 0 | 21.571 | 0 | 2 | 0 | 29.81 | 30.413 | 29.16 | 29.329 | 17.285 | 24.825 | 15.385 | 0 | 0 | 57.779 | 55.361 | 48.872 | 22.39 | 0 | 0 | 53.664 | 35.187 | [5 empty] | 0 | 0.481 | 38 | 2.1163 | 1.9364 | 1.0423 | 0.89552 | 1.0409 | 49.1856
2005-10-31 | 3:36 | 0 | 21.539 | 0 | 2 | 0 | 35.086 | 30.188 | 29.055 | 29.128 | 24.116 | 24.793 | 15.352 | 0 | 0 | 57.726 | 55.33 | 48.818 | 22.312 | 0 | 0 | 53.657 | 35.134 | [5 empty] | 0 | 5.958 | 39 | 2.1259 | 1.9456 | 1.0427 | 0.89552 | 1.05 | 49.393
2005-10-31 | 3:37 | 0 | 21.539 | 0 | 2 | 0 | 44.624 | 30.163 | 28.91 | 29.153 | 21.275 | 24.815 | 15.302 | 1 | 0 | 57.681 | 55.286 | 48.818 | 22.334 | 0 | 0 | 53.657 | 35.155 | [5 empty] | 0 | 15.471 | 40 | 2.1405 | 1.9594 | 1.0433 | 0.89552 | 1.0639 | 49.7036
2005-10-31 | 3:38 | 0 | 21.596 | 0 | 1 | 0 | 34.366 | 40.803 | 28.895 | 28.942 | 19.41 | 24.896 | 15.335 | 0 | 0 | 57.756 | 55.316 | 48.781 | 22.39 | 0 | 0 | 53.664 | 35.187 | [5 empty] | 0 | 5.424 | 41 | 2.1308 | 1.9503 | 1.0429 | 0.89552 | 1.0547 | 49.4991
2005-10-31 | 3:39 | 0 | 21.571 | 0 | 2 | 0 | 31.134 | 40.382 | 28.751 | 28.895 | 18.52 | 24.825 | 15.284 | 0 | 0 | 57.71 | 55.293 | 48.828 | 22.39 | 0 | 0 | 53.664 | 35.141 | [5 empty] | 0 | 2.239 | 42 | 2.1457 | 1.9644 | 1.0435 | 0.89552 | 1.0689 | 49.8144
2005-10-31 | 3:40 | 0 | 21.515 | 0 | 2 | 0 | 30.092 | 33.747 | 28.719 | 28.839 | 17.896 | 24.769 | 15.327 | 1 | 0 | 57.681 | 55.263 | 48.818 | 22.312 | 0 | 0 | 53.589 | 35.086 | [5 empty] | 0 | 1.253 | 43 | 2.1332 | 1.9525 | 1.043 | 0.89552 | 1.057 | 49.5488
2005-10-31 | 3:41 | 0 | 21.571 | 0 | 2 | 0 | 29.619 | 31.352 | 28.702 | 28.606 | 17.607 | 24.801 | 15.335 | 0 | 0 | 57.71 | 55.316 | 48.872 | 22.366 | 0 | 0 | 53.596 | 35.069 | [5 empty] | 0 | 1.013 | 44 | 2.1308 | 1.9503 | 1.0429 | 0.89552 | 1.0547 | 49.4991
2005-10-31 | 3:42 | 0 | 21.539 | 0 | 2 | 0 | 29.344 | 30.428 | 28.645 | 28.599 | 17.202 | 24.864 | 15.277 | 0 | 0 | 57.681 | 55.263 | 48.727 | 22.312 | 0 | 0 | 53.589 | 35.062 | [5 empty] | 0 | 0.745 | 45 | 2.1477 | 1.9663 | 1.0436 | 0.89552 | 1.0708 | 49.8573
2005-10-31 | 3:43 | 0 | 21.571 | 0 | 1 | 0 | 29.209 | 30.05 | 28.655 | 28.631 | 17.162 | 24.872 | 15.309 | 0 | 0 | 57.71 | 55.293 | 48.711 | 22.344 | 0 | 0 | 53.596 | 35.069 | [5 empty] | 0 | 0.578 | 46 | 2.1384 | 1.9575 | 1.0432 | 0.89552 | 1.0619 | 49.6603
2005-10-31 | 3:44 | 0 | 21.571 | 1 | 2 | 0 | 29.087 | 29.786 | 28.582 | 28.582 | 17.014 | 24.896 | 15.309 | 0 | 0 | 57.688 | 55.27 | 48.734 | 22.366 | 0 | 0 | 53.573 | 35.069 | [5 empty] | 0 | 0.505 | 47 | 2.1384 | 1.9575 | 1.0432 | 0.89552 | 1.0619 | 49.6603
2005-10-31 | 3:45 | 0 | 21.539 | 0 | 2 | 0 | 28.984 | 29.513 | 28.479 | 28.479 | 16.883 | 24.695 | 15.327 | 0 | 0 | 57.635 | 55.216 | 48.774 | 22.334 | 0 | 0 | 53.475 | 35.014 | [5 empty] | 0 | 0.505 | 48 | 2.1332 | 1.9525 | 1.043 | 0.89552 | 1.057 | 49.5488
2005-10-31 | 3:46 | 0 | 21.552 | 0 | 2 | 0 | 28.851 | 29.405 | 28.537 | 28.466 | 16.82 | 24.683 | 15.264 | 0 | 0 | 57.626 | 55.228 | 48.671 | 22.324 | 0 | 0 | 53.486 | 35.026 | [5 empty] | 0 | 0.385 | 49 | 2.1515 | 1.9699 | 1.0437 | 0.89552 | 1.0744 | 49.9368
2005-10-31 | 3:47 | 1 | 21.584 | 0 | 2 | 0 | 31.146 | 29.317 | 28.618 | 28.498 | 24.379 | 24.859 | 15.347 | 0 | 0 | 57.656 | 55.235 | 48.678 | 22.356 | 0 | 0 | 53.517 | 35.057 | [5 empty] | 21.584 | 2.648 | 50 | 2.1274 | 1.947 | 1.0427 | 0.89552 | 1.0514 | 49.4242
2005-10-31 | 3:48 | 0 | 21.559 | 0 | 2 | 0 | 44.059 | 29.244 | 28.4 | 28.474 | 20.527 | 24.668 | 15.42 | 1 | 0 | 57.633 | 55.214 | 48.793 | 22.378 | 0 | 0 | 53.517 | 35.105 | [5 empty] | 0 | 15.585 | 51 | 2.1061 | 1.9267 | 1.0419 | 0.89552 | 1.0312 | 48.9637
2005-10-31 | 3:49 | 0 | 21.576 | 0 | 2 | 0 | 33.687 | 39.916 | 28.368 | 28.297 | 18.55 | 24.707 | 15.387 | 0 | 0 | 57.626 | 55.228 | 48.601 | 22.324 | 0 | 0 | 53.486 | 35.05 | [5 empty] | 0 | 5.39 | 52 | 2.1157 | 1.9359 | 1.0423 | 0.89552 | 1.0404 | 49.173
2005-10-31 | 3:50 | 0 | 21.608 | 0 | 2 | 0 | 30.401 | 38.724 | 28.305 | 28.354 | 17.791 | 24.715 | 15.347 | 0 | 0 | 57.61 | 55.214 | 48.678 | 22.378 | 0 | 0 | 53.517 | 35.081 | [5 empty] | 0 | 2.047 | 53 | 2.1274 | 1.947 | 1.0427 | 0.89552 | 1.0514 | 49.4242
2005-10-31 | 3:51 | 0 | 21.584 | 0 | 2 | 0 | 29.388 | 32.52 | 28.4 | 28.28 | 17.298 | 24.788 | 15.322 | 0 | 0 | 57.633 | 55.19 | 48.632 | 22.356 | 0 | 0 | 53.517 | 35.057 | [5 empty] | 0 | 1.108 | 54 | 2.1346 | 1.9539 | 1.043 | 0.89552 | 1.0583 | 49.5798
2005-10-31 | 3:52 | 0 | 21.584 | 0 | 2 | 0 | 29.028 | 30.425 | 28.329 | 28.258 | 17.001 | 24.693 | 15.272 | 0 | 0 | 57.564 | 55.167 | 48.723 | 22.356 | 0 | 0 | 53.493 | 35.081 | [5 empty] | 0 | 0.77 | 55 | 2.1492 | 1.9677 | 1.0436 | 0.89552 | 1.0722 | 49.8879
2005-10-31 | 3:53 | 0 | 21.584 | 0 | 2 | 0 | 28.81 | 29.727 | 28.305 | 28.233 | 16.828 | 24.668 | 15.322 | 0 | 0 | 57.564 | 55.214 | 48.746 | 22.356 | 0 | 0 | 53.47 | 35.105 | [5 empty] | 0 | 0.577 | 56 | 2.1346 | 1.9539 | 1.043 | 0.89552 | 1.0583 | 49.5798
2005-10-31 | 3:54 | 0 | 21.608 | 0 | 2 | 0 | 28.667 | 29.388 | 28.233 | 28.184 | 16.68 | 24.693 | 15.347 | 1 | 0 | 57.564 | 55.19 | 48.632 | 22.356 | 0 | 0 | 53.447 | 35.129 | [5 empty] | 0 | 0.483 | 57 | 2.1274 | 1.947 | 1.0427 | 0.89552 | 1.0514 | 49.4242
2005-10-31 | 3:55 | 0 | 21.584 | 0 | 2 | 0 | 28.569 | 29.148 | 28.184 | 28.184 | 16.458 | 24.788 | 15.347 | 0 | 0 | 57.587 | 55.167 | 48.608 | 22.331 | 0 | 0 | 53.447 | 35.081 | [5 empty] | 0 | 0.385 | 58 | 2.1274 | 1.947 | 1.0427 | 0.89552 | 1.0514 | 49.4242
2005-10-31 | 3:56 | 0 | 21.552 | 1 | 2 | 0 | 28.537 | 28.971 | 28.297 | 28.202 | 16.549 | 24.707 | 15.264 | 0 | 0 | 57.557 | 55.137 | 48.534 | 22.324 | 0 | 0 | 53.393 | 35.026 | [5 empty] | 0 | 0.335 | 59 | 2.1515 | 1.9699 | 1.0437 | 0.89552 | 1.0744 | 49.9368
2005-10-31 | 3:57 | 0 | 21.527 | 0 | 2 | 0 | 28.393 | 28.876 | 28.226 | 28.081 | 16.35 | 24.636 | 15.264 | 0 | 0 | 57.512 | 55.137 | 48.564 | 22.378 | 0 | 0 | 53.423 | 35.036 | [5 empty] | 0 | 0.312 | 60 | 2.1515 | 1.9699 | 1.0437 | 0.89552 | 1.0744 | 49.9368
2005-10-31 | 3:58 | 0 | 21.527 | 0 | 2 | 0 | 28.851 | 28.802 | 28.057 | 27.983 | 25.335 | 24.661 | 15.314 | 0 | 0 | 57.535 | 55.113 | 48.648 | 22.3 | 0 | 0 | 53.393 | 35.005 | [5 empty] | 0 | 0.868 | 61 | 2.137 | 1.9561 | 1.0431 | 0.89552 | 1.0606 | 49.6294
2005-10-31 | 3:59 | 0 | 21.527 | 0 | 2 | 0 | 44.566 | 28.731 | 28.081 | 28.128 | 24.082 | 24.636 | 15.216 | 0 | 0 | 57.468 | 55.067 | 48.555 | 22.324 | 0 | 0 | 53.393 | 35.005 | [5 empty] | 0 | 16.438 | 62 | 2.1655 | 1.9832 | 1.0443 | 0.89552 | 1.0877 | 50.228
2005-10-31 | 4:00 | 0 | 21.552 | 0 | 2 | 0 | 46.309 | 39.21 | 28.032 | 28.032 | 24.129 | 24.707 | 15.264 | 1 | 0 | 57.468 | 55.09 | 48.51 | 22.3 | 0 | 0 | 53.393 | 34.981 | [5 empty] | 0 | 18.277 | 63 | 2.1515 | 1.9699 | 1.0437 | 0.89552 | 1.0744 | 49.9368
2005-10-31 | 4:01 | 0 | 21.552 | 0 | 2 | 0 | 46.354 | 45.668 | 28.032 | 28.008 | 23.888 | 24.803 | 15.365 | 2 | 0 | 57.512 | 55.183 | 48.51 | 22.395 | 0 | 0 | 53.349 | 35.026 | [5 empty] | 0 | 18.346 | 64 | 2.1221 | 1.942 | 1.0425 | 0.89552 | 1.0464 | 49.3115
2005-10-31 | 4:02 | 0 | 21.584 | 0 | 2 | 0 | 45.857 | 46.477 | 28.04 | 28.089 | 23.849 | 24.764 | 15.297 | 1 | 0 | 57.498 | 55.053 | 48.564 | 22.331 | 0 | 0 | 53.447 | 35.057 | [5 empty] | 0 | 17.768 | 65 | 2.1419 | 1.9608 | 1.0433 | 0.89552 | 1.0653 | 49.7344
2005-10-31 | 4:03 | 1 | 21.552 | 0 | 2 | 1 | 45.941 | 46.195 | 28.177 | 27.888 | 23.913 | 24.828 | 15.289 | 1 | 0 | 57.491 | 55.067 | 48.464 | 22.3 | 0 | 0 | 53.393 | 35.074 | [5 empty] | 21.552 | 18.053 | 66 | 2.1442 | 1.963 | 1.0434 | 0.89552 | 1.0675 | 49.7836
2005-10-31 | 4:04 | 0 | 21.576 | 0 | 2 | 0 | 46.034 | 46.011 | 28.368 | 27.983 | 24.202 | 24.901 | 15.314 | 1 | 0 | 57.491 | 55.067 | 48.51 | 22.324 | 0 | 0 | 53.37 | 35.005 | [5 empty] | 0 | 18.051 | 0 | 2.137 | 1.9561 | 1.0431 | 0.89552 | 1.0606 | 49.6294
2005-10-31 | 4:05 | 0 | 21.576 | 0 | 2 | 0 | 46.034 | 46.172 | 28.393 | 27.983 | 24.538 | 24.948 | 15.365 | 2 | 0 | 57.535 | 55.046 | 48.534 | 22.3 | 0 | 0 | 53.393 | 35.005 | [5 empty] | 0 | 18.051 | 1 | 2.1221 | 1.942 | 1.647 | 1.5 | 0.44197 | 20.8268
2005-10-31 | 4:06 | 0 | 21.542 | 1 | 2 | 0 | 46.23 | 46.253 | 28.358 | 27.998 | 25.036 | 24.867 | 15.402 | 1 | 0 | 57.503 | 55.034 | 48.613 | 22.29 | 0 | 0 | 53.36 | 35.017 | [5 empty] | 0 | 18.232 | 2 | 2.1113 | 1.9317 | 1.6466 | 1.5 | 0.43173 | 20.448
2005-10-31 | 4:07 | 0 | 21.566 | 0 | 2 | 0 | 46.825 | 46.298 | 28.481 | 28.118 | 25.325 | 24.987 | 15.38 | 1 | 0 | 57.546 | 55.057 | 48.475 | 22.29 | 0 | 0 | 53.384 | 35.065 | [5 empty] | 0 | 18.707 | 3 | 2.1177 | 1.9378 | 1.6468 | 1.5 | 0.43782 | 20.6737
2005-10-31 | 4:08 | 1 | 21.542 | 0 | 2 | 0 | 46.895 | 46.757 | 28.552 | 28.167 | 25.637 | 24.891 | 15.38 | 1 | 0 | 57.526 | 55.057 | 48.613 | 22.29 | 0 | 0 | 53.314 | 35.089 | [5 empty] | 21.542 | 18.728 | 4 | 2.1177 | 1.9378 | 1.6468 | 1.5 | 0.43782 | 20.6737
2005-10-31 | 4:09 | 0 | 21.574 | 0 | 2 | 0 | 46.947 | 47.154 | 28.8 | 28.368 | 25.911 | 24.994 | 15.435 | 1 | 0 | 57.69 | 55.132 | 48.529 | 22.393 | 0 | 0 | 53.321 | 35.072 | [5 empty] | 0 | 18.579 | 5 | 2.1017 | 1.9226 | 1.6462 | 1.5 | 0.42259 | 20.1069
2005-10-31 | 4:10 | 0 | 21.566 | 0 | 2 | 0 | 46.916 | 47.238 | 28.746 | 28.383 | 26.289 | 24.987 | 15.38 | 2 | 0 | 57.569 | 55.057 | 48.499 | 22.314 | 0 | 0 | 53.29 | 35.017 | [5 empty] | 0 | 18.533 | 6 | 2.1177 | 1.9378 | 1.6468 | 1.5 | 0.43782 | 20.6737
2005-10-31 | 4:11 | 0 | 21.542 | 0 | 2 | 0 | 47.719 | 47.238 | 28.746 | 28.503 | 26.554 | 24.938 | 15.402 | 1 | 0 | 57.546 | 55.057 | 48.545 | 22.314 | 0 | 0 | 53.314 | 35.017 | [5 empty] | 0 | 19.216 | 7 | 2.1113 | 1.9317 | 1.6466 | 1.5 | 0.43173 | 20.448
2005-10-31 | 4:12 | 0 | 21.566 | 0 | 2 | 0 | 48.179 | 47.49 | 28.962 | 28.528 | 26.698 | 25.132 | 15.453 | 1 | 0 | 57.615 | 55.057 | 48.499 | 22.265 | 0 | 0 | 53.314 | 34.993 | [5 empty] | 0 | 19.651 | 8 | 2.0965 | 1.9176 | 1.646 | 1.5 | 0.41761 | 19.9195
2005-10-31 | 4:13 | 0 | 21.542 | 0 | 2 | 0 | 47.88 | 48.202 | 28.962 | 28.577 | 26.819 | 25.036 | 15.428 | 1 | 0 | 57.615 | 55.057 | 48.499 | 22.29 | 0 | 0 | 53.269 | 35.017 | [5 empty] | 0 | 19.303 | 9 | 2.1038 | 1.9245 | 1.6462 | 1.5 | 0.42453 | 20.1795
2005-10-31 | 4:14 | 1 | 21.542 | 0 | 2 | 0 | 47.833 | 48.431 | 29.226 | 28.842 | 26.963 | 25.011 | 15.402 | 2 | 0 | 57.615 | 55.034 | 48.522 | 22.314 | 0 | 0 | 53.269 | 35.017 | [5 empty] | 21.542 | 18.991 | 10 | 2.1113 | 1.9317 | 1.6466 | 1.5 | 0.43173 | 20.448
2005-10-31 | 4:15 | 0 | 21.598 | 1 | 2 | 0 | 47.843 | 48.254 | 29.619 | 28.873 | 27.115 | 25.139 | 15.46 | 1 | 0 | 57.667 | 55.064 | 48.552 | 22.322 | 0 | 0 | 53.321 | 35.072 | [5 empty] | 0 | 18.97 | 11 | 2.0944 | 1.9157 | 1.6459 | 1.5 | 0.41567 | 19.8464
2005-10-31 | 4:16 | 0 | 21.542 | 0 | 2 | 0 | 48.065 | 48.132 | 30.094 | 29.177 | 27.155 | 25.181 | 15.453 | 1 | 0 | 57.637 | 55.057 | 48.475 | 22.314 | 0 | 0 | 53.269 | 35.065 | [5 empty] | 0 | 18.888 | 12 | 2.0965 | 1.9176 | 1.646 | 1.5 | 0.41761 | 19.9195
2005-10-31 | 4:17 | 0 | 21.598 | 0 | 2 | 0 | 48.347 | 48.254 | 30.656 | 29.668 | 27.427 | 25.308 | 15.435 | 1 | 0 | 57.802 | 55.155 | 48.552 | 22.368 | 0 | 0 | 53.344 | 35.048 | [5 empty] | 0 | 18.679 | 13 | 2.1017 | 1.9226 | 1.6462 | 1.5 | 0.42259 | 20.1069
2005-10-31 | 4:18 | 0 | 21.574 | 0 | 2 | 0 | 48.667 | 48.576 | 31.065 | 30.173 | 27.62 | 25.333 | 15.435 | 2 | 0 | 57.71 | 55.088 | 48.506 | 22.297 | 0 | 0 | 53.367 | 35.048 | [5 empty] | 0 | 18.494 | 14 | 2.1017 | 1.9226 | 1.6462 | 1.5 | 0.42259 | 20.1069
2005-10-31 | 4:19 | 0 | 21.517 | 0 | 2 | 0 | 49.096 | 48.821 | 31.539 | 30.671 | 27.927 | 25.203 | 15.428 | 1 | 0 | 57.681 | 55.034 | 48.613 | 22.29 | 0 | 0 | 53.269 | 34.993 | [5 empty] | 0 | 18.425 | 15 | 2.1038 | 1.9245 | 1.6462 | 1.5 | 0.42453 | 20.1795
2005-10-31 | 4:20 | 1 | 21.574 | 0 | 2 | 0 | 49.103 | 49.171 | 32.029 | 31.401 | 26.441 | 25.333 | 15.46 | 1 | 0 | 57.667 | 55.111 | 48.576 | 22.346 | 0 | 0 | 53.321 | 35.002 | [5 empty] | 21.574 | 17.702 | 16 | 2.0944 | 1.9157 | 1.6459 | 1.5 | 0.41567 | 19.8464
2005-10-31 | 4:21 | 0 | 21.542 | 0 | 2 | 0 | 38.801 | 49.691 | 32.382 | 31.588 | 23.035 | 25.203 | 15.453 | 1 | 0 | 57.704 | 55.057 | 48.522 | 22.314 | 0 | 0 | 53.269 | 34.993 | [5 empty] | 0 | 7.213 | 17 | 2.0965 | 1.9176 | 1.646 | 1.5 | 0.41761 | 19.9195
2005-10-31 | 4:22 | 0 | 21.566 | 0 | 2 | 0 | 34.923 | 45.77 | 32.644 | 31.997 | 21.64 | 25.203 | 15.428 | 0 | 0 | 57.681 | 55.057 | 48.545 | 22.29 | 0 | 0 | 53.29 | 34.971 | [5 empty] | 0 | 2.926 | 18 | 2.1038 | 1.9245 | 1.6462 | 1.5 | 0.42453 | 20.1795
2005-10-31 | 4:23 | 0 | 21.542 | 0 | 2 | 0 | 33.959 | 38.236 | 32.809 | 32.382 | 20.63 | 25.325 | 15.38 | 0 | 0 | 57.704 | 55.034 | 48.522 | 22.265 | 0 | 0 | 53.269 | 34.993 | [5 empty] | 0 | 1.577 | 19 | 2.1177 | 1.9378 | 1.6468 | 1.5 | 0.43782 | 20.6737
2005-10-31 | 4:24 | 0 | 21.542 | 0 | 1 | 0 | 33.701 | 35.416 | 32.926 | 32.668 | 19.923 | 25.203 | 15.453 | 0 | 0 | 57.704 | 55.057 | 48.706 | 22.314 | 0 | 0 | 53.223 | 35.017 | [5 empty] | 0 | 1.033 | 20 | 2.0965 | 1.9176 | 1.646 | 1.5 | 0.41761 | 19.9195
2005-10-31 | 4:25 | 0 | 21.598 | 0 | 2 | 0 | 33.639 | 34.579 | 33.122 | 32.816 | 19.387 | 25.164 | 15.511 | 0 | 0 | 57.733 | 55.088 | 48.643 | 22.368 | 0 | 0 | 53.206 | 35.048 | [5 empty] | 0 | 0.823 | 21 | 2.0796 | 1.9016 | 1.6453 | 1.5 | 0.40156 | 19.3093
2005-10-31 | 4:26 | 0 | 21.527 | 1 | 2 | 0 | 33.546 | 34.203 | 33.216 | 32.888 | 19.166 | 25.188 | 15.387 | 0 | 0 | 57.667 | 55.041 | 48.643 | 22.3 | 0 | 0 | 53.162 | 34.955 | [5 empty] | 0 | 0.658 | 22 | 2.1157 | 1.9359 | 1.6467 | 1.5 | 0.43588 | 20.602
2005-10-31 | 4:27 | 0 | 21.562 | 0 | 2 | 0 | 33.579 | 34.096 | 33.18 | 33.062 | 18.93 | 25.2 | 15.423 | 1 | 0 | 57.699 | 55.074 | 48.655 | 22.334 | 0 | 0 | 53.216 | 34.964 | [5 empty] | 0 | 0.517 | 23 | 2.1052 | 1.9259 | 1.6463 | 1.5 | 0.42591 | 20.2313
2005-10-31 | 4:28 | 0 | 21.527 | 0 | 2 | 0 | 33.57 | 33.945 | 33.098 | 33.074 | 18.673 | 25.166 | 15.34 | 0 | 0 | 57.599 | 54.997 | 48.599 | 22.3 | 0 | 0 | 53.206 | 34.978 | [5 empty] | 0 | 0.496 | 24 | 2.1294 | 1.9489 | 1.6473 | 1.5 | 0.44889 | 21.0806
2005-10-31 | 4:29 | 0 | 21.503 | 0 | 1 | 0 | 33.639 | 33.945 | 32.771 | 32.957 | 18.427 | 25.188 | 15.365 | 0 | 0 | 57.621 | 55.018 | 48.643 | 22.275 | 0 | 0 | 53.183 | 34.978 | [5 empty] | 0 | 0.682 | 25 | 2.1221 | 1.942 | 1.647 | 1.5 | 0.44197 | 20.8268
2005-10-31 | 4:30 | 0 | 21.552 | 0 | 2 | 0 | 34.132 | 33.969 | 32.63 | 32.888 | 27.5 | 25.117 | 15.438 | 0 | 0 | 57.621 | 55.018 | 48.508 | 22.3 | 0 | 0 | 53.183 | 34.978 | [5 empty] | 0 | 1.244 | 26 | 2.1009 | 1.9218 | 1.6461 | 1.5 | 0.42176 | 20.0757
2005-10-31 | 4:31 | 0 | 21.537 | 0 | 2 | 0 | 48.93 | 33.955 | 32.353 | 32.78 | 23.584 | 25.2 | 15.4 | 0 | 0 | 57.631 | 55.029 | 48.655 | 22.334 | 0 | 0 | 53.195 | 34.988 | [5 empty] | 0 | 16.15 | 27 | 2.1119 | 1.9323 | 1.6466 | 1.5 | 0.43228 | 20.4686
2005-10-31 | 4:32 | 0 | 21.527 | 0 | 2 | 0 | 39.397 | 39.397 | 32.029 | 32.534 | 21.12 | 25.188 | 15.314 | 1 | 0 | 57.555 | 54.997 | 48.529 | 22.3 | 0 | 0 | 53.139 | 34.955 | [5 empty] | 0 | 6.863 | 28 | 2.137 | 1.9561 | 1.6476 | 1.5 | 0.45608 | 21.3427
2005-10-31 | 4:33 | 0 | 21.552 | 0 | 2 | 0 | 35.144 | 45.481 | 31.86 | 32.247 | 19.908 | 25.262 | 15.365 | 0 | 0 | 57.576 | 54.926 | 48.529 | 22.371 | 0 | 0 | 53.069 | 34.931 | [5 empty] | 0 | 2.897 | 29 | 2.1221 | 1.942 | 1.647 | 1.5 | 0.44197 | 20.8268
2005-10-31 | 4:34 | 0 | 21.527 | 0 | 1 | 0 | 33.804 | 38.645 | 31.573 | 32.005 | 19.118 | 25.286 | 15.387 | 0 | 0 | 57.532 | 54.926 | 48.508 | 22.275 | 0 | 0 | 53.115 | 34.955 | [5 empty] | 0 | 1.799 | 30 | 2.1157 | 1.9359 | 1.6467 | 1.5 | 0.43588 | 20.602
2005-10-31 | 4:35 | 0 | 21.527 | 0 | 2 | 0 | 33.122 | 35.354 | 31.284 | 31.62 | 18.673 | 25.141 | 15.365 | 0 | 0 | 57.487 | 54.926 | 48.485 | 22.275 | 0 | 0 | 53.115 | 34.955 | [5 empty] | 0 | 1.502 | 31 | 2.1221 | 1.942 | 1.647 | 1.5 | 0.44197 | 20.8268
2005-10-31 | 4:36 | 0 | 21.527 | 0 | 2 | 0 | 32.723 | 34.156 | 31.019 | 31.379 | 18.203 | 25.092 | 15.314 | 0 | 0 | 57.464 | 54.95 | 48.485 | 22.3 | 0 | 0 | 53.092 | 34.955 | [5 empty] | 0 | 1.344 | 32 | 2.137 | 1.9561 | 1.6476 | 1.5 | 0.45608 | 21.3427
2005-10-31 | 4:37 | 0 | 21.527 | 0 | 1 | 0 | 32.318 | 33.546 | 30.874 | 31.115 | 18.055 | 25.068 | 15.289 | 0 | 0 | 57.464 | 54.926 | 48.461 | 22.275 | 0 | 0 | 53.069 | 34.955 | [5 empty] | 0 | 1.203 | 33 | 2.1442 | 1.963 | 1.6479 | 1.5 | 0.463 | 21.5929
2005-10-31 | 4:38 | 0 | 21.527 | 1 | 2 | 0 | 31.983 | 33.098 | 30.73 | 30.921 | 17.982 | 25.068 | 15.289 | 0 | 0 | 57.464 | 54.903 | 48.529 | 22.275 | 0 | 0 | 53.048 | 35.026 | [5 empty] | 0 | 1.062 | 34 | 2.1442 | 1.963 | 1.6479 | 1.5 | 0.463 | 21.5929
2005-10-31 | 4:39 | 0 | 21.552 | 0 | 2 | 0 | 31.693 | 32.699 | 30.705 | 30.754 | 17.612 | 25.141 | 15.314 | 0 | 0 | 57.441 | 54.903 | 48.438 | 22.275 | 0 | 0 | 53.048 | 34.978 | [5 empty] | 0 | 0.939 | 35 | 2.137 | 1.9561 | 1.6476 | 1.5 | 0.45608 | 21.3427
2005-10-31 | 4:40 | 0 | 21.552 | 0 | 1 | 0 | 31.45 | 32.343 | 30.56 | 30.631 | 17.363 | 25.117 | 15.264 | 1 | 0 | 57.421 | 54.88 | 48.461 | 22.275 | 0 | 0 | 53.069 | 35.05 | [5 empty] | 0 | 0.819 | 36 | 2.1515 | 1.9699 | 1.6482 | 1.5 | 0.46992 | 21.8415
2005-10-31 | 4:41 | 0 | 21.552 | 0 | 2 | 0 | 31.235 | 32.029 | 30.32 | 30.631 | 27.454 | 24.997 | 15.242 | 0 | 0 | 57.398 | 54.88 | 48.461 | 22.275 | 0 | 0 | 53.115 | 35.12 | [5 empty] | 0 | 0.604 | 37 | 2.1579 | 1.976 | 1.6484 | 1.5 | 0.47601 | 22.0588
2005-10-31 | 4:42 | 0 | 21.527 | 0 | 2 | 0 | 48.002 | 31.74 | 30.271 | 30.44 | 23.02 | 24.972 | 15.216 | 0 | 0 | 57.375 | 54.859 | 48.391 | 22.275 | 0 | 0 | 53.024 | 35.026 | [5 empty] | 0 | 17.562 | 38 | 2.1655 | 1.9832 | 1.6488 | 1.5 | 0.48321 | 22.3141
2005-10-31 | 4:43 | 0 | 21.527 | 0 | 2 | 1 | 39.162 | 34.672 | 30.08 | 30.271 | 19.882 | 24.948 | 15.264 | 0 | 0 | 57.352 | 54.88 | 48.391 | 22.3 | 0 | 0 | 53.024 | 35.026 | [5 empty] | 0 | 8.891 | 39 | 2.1515 | 1.9699 | 1.6482 | 1.5 | 0.46992 | 21.8415
2005-10-31 | 4:44 | 0 | 21.527 | 0 | 1 | 0 | 33.405 | 44.953 | 29.862 | 30.126 | 18.847 | 25.141 | 15.242 | 0 | 0 | 57.329 | 54.88 | 48.324 | 22.275 | 0 | 0 | 53.001 | 35.002 | [5 empty] | 0 | 3.279 | 0 | 2.1579 | 1.976 | 1.6484 | 1.5 | 0.47601 | 22.0588
2005-10-31 | 4:45 | 0 | 21.527 | 0 | 2 | 0 | 31.715 | 37.846 | 29.67 | 29.911 | 18.253 | 24.923 | 15.289 | 1 | 0 | 57.329 | 54.859 | 48.37 | 22.275 | 0 | 0 | 53.024 | 34.978 | [5 empty] | 0 | 1.804 | 1 | 2.1442 | 1.963 | 1.3724 | 1.2245 | 0.73852 | 34.4418
2005-10-31 | 4:46 | 0 | 21.554 | 0 | 2 | 0 | 31.046 | 33.644 | 29.648 | 29.719 | 17.811 | 24.928 | 15.342 | 0 | 0 | 57.357 | 54.861 | 48.466 | 22.302 | 0 | 0 | 53.027 | 34.981 | [5 empty] | 0 | 1.327 | 2 | 2.1288 | 1.9483 | 1.3718 | 1.2245 | 0.72384 | 34.0023
2005-10-31 | 4:47 | 0 | 21.554 | 0 | 1 | 0 | 30.683 | 32.154 | 29.575 | 29.575 | 17.416 | 24.999 | 15.367 | 0 | 0 | 57.357 | 54.861 | 48.373 | 22.277 | 0 | 0 | 53.073 | 34.935 | [5 empty] | 0 | 1.108 | 3 | 2.1215 | 1.9414 | 1.3715 | 1.2245 | 0.71692 | 33.7928
2005-10-31 | 4:48 | 0 | 21.554 | 0 | 2 | 0 | 30.372 | 31.48 | 29.383 | 29.408 | 17.416 | 24.928 | 15.342 | 0 | 0 | 57.334 | 54.861 | 48.443 | 22.302 | 0 | 0 | 53.006 | 34.935 | [5 empty] | 0 | 0.964 | 4 | 2.1288 | 1.9483 | 1.3718 | 1.2245 | 0.72384 | 34.0023
2005-10-31 | 4:49 | 0 | 21.554 | 0 | 2 | 0 | 30.153 | 31.046 | 29.383 | 29.359 | 17.195 | 24.975 | 15.342 | 0 | 0 | 57.311 | 54.84 | 48.349 | 22.277 | 0 | 0 | 53.027 | 34.935 | [5 empty] | 0 | 0.794 | 5 | 2.1288 | 1.9483 | 1.3718 | 1.2245 | 0.72384 | 34.0023
2005-10-31 | 4:50 | 0 | 21.53 | 1 | 2 | 0 | 29.984 | 30.757 | 29.239 | 29.239 | 16.996 | 24.879 | 15.342 | 0 | 0 | 57.311 | 54.817 | 48.443 | 22.302 | 0 | 0 | 52.959 | 34.935 | [5 empty] | 0 | 0.745 | 6 | 2.1288 | 1.9483 | 1.3718 | 1.2245 | 0.72384 | 34.0023
2005-10-31 | 4:51 | 0 | 21.554 | 0 | 1 | 0 | 29.842 | 30.467 | 29.143 | 29.263 | 17.145 | 24.806 | 15.317 | 0 | 0 | 57.311 | 54.817 | 48.419 | 22.302 | 0 | 0 | 52.936 | 34.935 | [5 empty] | 0 | 0.579 | 7 | 2.1361 | 1.9553 | 1.372 | 1.2245 | 0.73076 | 34.2104
2005-10-31 | 4:52 | 0 | 21.53 | 0 | 2 | 0 | 29.697 | 30.273 | 29.214 | 29.165 | 23.577 | 24.855 | 15.267 | 0 | 0 | 57.288 | 54.84 | 48.258 | 22.302 | 0 | 0 | 52.912 | 34.935 | [5 empty] | 0 | 0.532 | 8 | 2.1506 | 1.9691 | 1.3726 | 1.2245 | 0.7446 | 34.6223
2005-10-31 | 4:53 | 0 | 21.554 | 0 | 2 | 0 | 45.738 | 30.129 | 29.045 | 29.07 | 23.096 | 24.83 | 15.342 | 0 | 0 | 57.311 | 54.84 | 48.258 | 22.277 | 0 | 0 | 52.891 | 34.912 | [5 empty] | 0 | 16.668 | 9 | 2.1288 | 1.9483 | 1.3718 | 1.2245 | 0.72384 | 34.0023
2005-10-31 | 4:54 | 0 | 21.53 | 0 | 2 | 0 | 39.212 | 32.154 | 28.854 | 29.045 | 19.588 | 24.879 | 15.367 | 1 | 0 | 57.245 | 54.77 | 48.258 | 22.277 | 0 | 0 | 52.891 | 34.935 | [5 empty] | 0 | 10.167 | 10 | 2.1215 | 1.9414 | 1.3715 | 1.2245 | 0.71692 | 33.7928
2005-10-31 | 4:55 | 0 | 21.554 | 0 | 1 | 0 | 32.466 | 43.841 | 28.756 | 28.878 | 18.256 | 24.783 | 15.292 | 0 | 0 | 57.222 | 54.77 | 48.282 | 22.277 | 0 | 0 | 52.912 | 34.888 | [5 empty] | 0 | 3.588 | 11 | 2.1434 | 1.9622 | 1.3723 | 1.2245 | 0.73768 | 34.4171
2005-10-31 | 4:56 | 0 | 21.53 | 0 | 2 | 0 | 30.538 | 37.026 | 28.709 | 28.805 | 17.861 | 24.806 | 15.292 | 0 | 0 | 57.199 | 54.77 | 48.235 | 22.302 | 0 | 0 | 52.936 | 34.935 | [5 empty] | 0 | 1.733 | 12 | 2.1434 | 1.9622 | 1.3723 | 1.2245 | 0.73768 | 34.4171
2005-10-31 | 4:57 | 0 | 21.554 | 0 | 2 | 0 | 29.864 | 32.466 | 28.829 | 28.709 | 17.243 | 24.904 | 15.317 | 1 | 0 | 57.199 | 54.747 | 48.191 | 22.302 | 0 | 0 | 52.912 | 34.935 | [5 empty] | 0 | 1.155 | 13 | 2.1361 | 1.9553 | 1.372 | 1.2245 | 0.73076 | 34.2104
2005-10-31 | 4:58 | 0 | 21.554 | 0 | 2 | 0 | 29.528 | 30.877 | 28.709 | 28.564 | 16.996 | 24.855 | 15.317 | 0 | 0 | 57.199 | 54.747 | 48.212 | 22.277 | 0 | 0 | 52.912 | 34.959 | [5 empty] | 0 | 0.964 | 14 | 2.1361 | 1.9553 | 1.372 | 1.2245 | 0.73076 | 34.2104
2005-10-31 | 4:59 | 0 | 21.498 | 0 | 2 | 0 | 29.278 | 30.242 | 28.533 | 28.484 | 16.989 | 24.752 | 15.284 | 0 | 0 | 57.17 | 54.716 | 48.205 | 22.27 | 0 | 0 | 52.861 | 34.95 | [5 empty] | 0 | 0.794 | 15 | 2.1457 | 1.9644 | 1.3724 | 1.2245 | 0.7399 | 34.4829
2005-10-31 | 5:00 | 0 | 21.522 | 0 | 1 | 0 | 29.111 | 29.857 | 28.604 | 28.484 | 16.765 | 24.798 | 15.357 | 0 | 0 | 57.17 | 54.74 | 48.16 | 22.341 | 0 | 0 | 52.861 | 34.928 | [5 empty] | 0 | 0.627 | 16 | 2.1244 | 1.9442 | 1.3716 | 1.2245 | 0.71969 | 33.8768
2005-10-31 | 5:01 | 0 | 21.53 | 1 | 2 | 0 | 28.998 | 29.648 | 28.515 | 28.491 | 16.675 | 24.759 | 15.317 | 0 | 0 | 57.156 | 54.702 | 48.212 | 22.277 | 0 | 0 | 52.868 | 34.912 | [5 empty] | 0 | 0.507 | 17 | 2.1361 | 1.9553 | 1.372 | 1.2245 | 0.73076 | 34.2104
2005-10-31 | 5:02 | 0 | 21.579 | 0 | 2 | 0 | 28.925 | 29.455 | 28.589 | 28.469 | 16.649 | 24.855 | 15.342 | 0 | 0 | 57.156 | 54.702 | 48.144 | 22.277 | 0 | 0 | 52.868 | 34.912 | [5 empty] | 0 | 0.456 | 18 | 2.1288 | 1.9483 | 1.3718 | 1.2245 | 0.72384 | 34.0023
2005-10-31 | 5:03 | 0 | 21.554 | 0 | 2 | 0 | 28.805 | 29.31 | 28.444 | 28.371 | 20.257 | 24.685 | 15.317 | 0 | 0 | 57.176 | 54.702 | 48.258 | 22.302 | 0 | 0 | 52.868 | 34.864 | [5 empty] | 0 | 0.434 | 19 | 2.1361 | 1.9553 | 1.372 | 1.2245 | 0.73076 | 34.2104
2005-10-31 | 5:04 | 1 | 21.554 | 0 | 2 | 0 | 42.432 | 29.214 | 28.395 | 28.324 | 23.217 | 24.661 | 15.317 | 0 | 0 | 57.156 | 54.679 | 48.121 | 22.302 | 0 | 0 | 52.868 | 34.842 | [5 empty] | 21.554 | 14.108 | 20 | 2.1361 | 1.9553 | 1.372 | 1.2245 | 0.73076 | 34.2104
2005-10-31 | 5:05 | 0 | 21.554 | 0 | 2 | 0 | 39.047 | 30.852 | 28.324 | 28.324 | 19.985 | 24.661 | 15.292 | 0 | 0 | 57.176 | 54.679 | 48.235 | 22.302 | 0 | 0 | 52.868 | 34.864 | [5 empty] | 0 | 10.723 | 21 | 2.1434 | 1.9622 | 1.3723 | 1.2245 | 0.73768 | 34.4171
2005-10-31 | 5:06 | 0 | 21.547 | 0 | 2 | 0 | 31.833 | 42.776 | 28.268 | 28.388 | 18.002 | 24.703 | 15.237 | 1 | 0 | 57.126 | 54.649 | 48.137 | 22.319 | 0 | 0 | 52.884 | 34.904 | [5 empty] | 0 | 3.445 | 22 | 2.1594 | 1.9774 | 1.373 | 1.2245 | 0.75291 | 34.8668
2005-10-31 | 5:07 | 0 | 21.547 | 0 | 2 | 0 | 29.81 | 35.61 | 28.341 | 28.172 | 17.162 | 24.752 | 15.309 | 0 | 0 | 57.172 | 54.672 | 48.093 | 22.295 | 0 | 0 | 52.884 | 34.835 | [5 empty] | 0 | 1.638 | 23 | 2.1384 | 1.9575 | 1.3721 | 1.2245 | 0.73298 | 34.2767
2005-10-31 | 5:08 | 0 | 21.547 | 0 | 2 | 0 | 29.16 | 31.328 | 28.268 | 28.148 | 17.039 | 24.631 | 15.309 | 0 | 0 | 57.103 | 54.649 | 48.16 | 22.439 | 0 | 0 | 52.929 | 34.976 | [5 empty] | 0 | 1.012 | 24 | 2.1384 | 1.9575 | 1.3721 | 1.2245 | 0.73298 | 34.2767
2005-10-31 | 5:09 | 0 | 21.515 | 0 | 1 | 0 | 28.79 | 29.994 | 28.26 | 28.091 | 16.833 | 24.646 | 15.252 | 0 | 0 | 57.097 | 54.618 | 48.083 | 22.263 | 0 | 0 | 52.784 | 34.873 | [5 empty] | 0 | 0.699 | 25 | 2.155 | 1.9732 | 1.3728 | 1.2245 | 0.74876 | 34.7448
2005-10-31 | 5:10 | 0 | 21.515 | 0 | 2 | 0 | 28.67 | 29.418 | 28.26 | 28.165 | 16.536 | 24.646 | 15.229 | 0 | 0 | 57.119 | 54.618 | 48.039 | 22.287 | 0 | 0 | 52.784 | 34.921 | [5 empty] | 0 | 0.505 | 26 | 2.1617 | 1.9796 | 1.3731 | 1.2245 | 0.75512 | 34.9317
2005-10-31 | 5:11 | 0 | 21.571 | 0 | 2 | 0 | 28.606 | 29.256 | 28.221 | 28.099 | 16.496 | 24.678 | 15.262 | 1 | 0 | 57.126 | 54.649 | 48.093 | 22.319 | 0 | 0 | 52.814 | 34.976 | [5 empty] | 0 | 0.507 | 27 | 2.1521 | 1.9705 | 1.3727 | 1.2245 | 0.74599 | 34.6632
2005-10-31 | 5:12 | 0 | 21.515 | 0 | 2 | 0 | 28.501 | 29.055 | 28.165 | 28.067 | 16.388 | 24.646 | 15.277 | 0 | 0 | 57.074 | 54.595 | 48.016 | 22.287 | 0 | 0 | 52.74 | 34.897 | [5 empty] | 0 | 0.434 | 28 | 2.1477 | 1.9663 | 1.3725 | 1.2245 | 0.74184 | 34.5404
2005-10-31 | 5:13 | 0 | 21.539 | 1 | 2 | 0 | 28.43 | 28.935 | 28.116 | 28.02 | 16.413 | 24.624 | 15.252 | 0 | 0 | 57.074 | 54.618 | 47.992 | 22.287 | 0 | 0 | 52.74 | 34.873 | [5 empty] | 0 | 0.41 | 29 | 2.155 | 1.9732 | 1.3728 | 1.2245 | 0.74876 | 34.7448
2005-10-31 | 5:14 | 0 | 21.547 | 0 | 3 | 0 | 28.388 | 28.895 | 28.099 | 27.954 | 16.619 | 24.607 | 15.284 | 0 | 0 | 57.081 | 54.625 | 48.069 | 22.319 | 0 | 0 | 52.77 | 34.88 | [5 empty] | 0 | 0.434 | 30 | 2.1457 | 1.9644 | 1.3724 | 1.2245 | 0.7399 | 34.4829
2005-10-31 | 5:15 | 0 | 21.515 | 0 | 2 | 0 | 38.234 | 28.741 | 28.045 | 27.947 | 22.962 | 24.551 | 15.252 | 0 | 0 | 57.074 | 54.572 | 47.992 | 22.263 | 0 | 0 | 52.761 | 34.828 | [5 empty] | 0 | 10.287 | 31 | 2.155 | 1.9732 | 1.3728 | 1.2245 | 0.74876 | 34.7448
2005-10-31 | 5:16 | 0 | 21.571 | 0 | 2 | 0 | 46.188 | 30.001 | 28.003 | 27.978 | 23.982 | 24.607 | 15.211 | 0 | 0 | 57.037 | 54.581 | 48.069 | 22.295 | 0 | 0 | 52.77 | 34.904 | [5 empty] | 0 | 18.21 | 32 | 2.167 | 1.9846 | 1.3733 | 1.2245 | 0.76011 | 35.0771
2005-10-31 | 5:17 | 0 | 21.493 | 0 | 2 | 0 | 46.41 | 43.238 | 27.971 | 27.947 | 23.876 | 24.575 | 15.204 | 2 | 0 | 57.028 | 54.527 | 47.969 | 22.287 | 0 | 0 | 52.716 | 34.849 | [5 empty] | 0 | 18.463 | 33 | 2.169 | 1.9865 | 1.3734 | 1.2245 | 0.76204 | 35.1335
2005-10-31 | 5:18 | 0 | 21.515 | 0 | 2 | 0 | 46.043 | 46.067 | 27.947 | 27.996 | 23.732 | 24.575 | 15.179 | 1 | 0 | 57.008 | 54.504 | 47.969 | 22.287 | 0 | 0 | 52.74 | 34.828 | [5 empty] | 0 | 18.047 | 34 | 2.1763 | 1.9935 | 1.3737 | 1.2245 | 0.76896 | 35.3339
2005-10-31 | 5:19 | 1 | 21.547 | 0 | 2 | 0 | 45.913 | 46.12 | 28.099 | 27.907 | 23.933 | 24.703 | 15.211 | 1 | 0 | 57.058 | 54.581 | 48.023 | 22.319 | 0 | 0 | 52.77 | 34.859 | [5 empty] | 21.547 | 18.006 | 35 | 2.167 | 1.9846 | 1.3733 | 1.2245 | 0.76011 | 35.0771
2005-10-31 | 5:20 | 0 | 21.571 | 0 | 2 | 0 | 45.936 | 46.006 | 28.221 | 27.907 | 24.102 | 24.656 | 15.237 | 2 | 0 | 57.058 | 54.558 | 47.999 | 22.319 | 0 | 0 | 52.747 | 34.835 | [5 empty] | 0 | 18.029 | 36 | 2.1594 | 1.9774 | 1.373 | 1.2245 | 0.75291 | 34.8668
2005-10-31 | 5:21 | 0 | 21.539 | 0 | 2 | 0 | 45.997 | 46.043 | 28.211 | 27.9 | 24.19 | 24.72 | 15.204 | 1 | 0 | 57.008 | 54.527 | 47.945 | 22.287 | 0 | 0 | 52.693 | 34.849 | [5 empty] | 0 | 18.097 | 37 | 2.169 | 1.9865 | 1.3734 | 1.2245 | 0.76204 | 35.1335
2005-10-31 | 5:22 | 0 | 21.515 | 0 | 2 | 0 | 46.09 | 46.204 | 28.309 | 28.091 | 24.455 | 24.769 | 15.229 | 1 | 0 | 57.028 | 54.551 | 48.039 | 22.312 | 0 | 0 | 52.716 | 34.849 | [5 empty] | 0 | 17.999 | 38 | 2.1617 | 1.9796 | 1.3731 | 1.2245 | 0.75512 | 34.9317
2005-10-31 | 5:23 | 0 | 21.547 | 1 | 2 | 0 | 46.211 | 46.302 | 28.363 | 28.148 | 24.896 | 24.776 | 15.262 | 1 | 0 | 57.081 | 54.558 | 48.093 | 22.319 | 0 | 0 | 52.747 | 34.88 | [5 empty] | 0 | 18.063 | 39 | 2.1521 | 1.9705 | 1.3727 | 1.2245 | 0.74599 | 34.6632
2005-10-31 | 5:24 | 0 | 21.539 | 0 | 2 | 0 | 46.662 | 46.342 | 28.476 | 28.091 | 25.249 | 24.864 | 15.128 | 1 | 0 | 57.074 | 54.572 | 48.107 | 22.263 | 0 | 0 | 52.693 | 34.945 | [5 empty] | 0 | 18.571 | 40 | 2.1911 | 2.0076 | 1.3743 | 1.2245 | 0.78308 | 35.7387
2005-10-31 | 5:25 | 1 | 21.515 | 0 | 2 | 0 | 46.984 | 46.662 | 28.525 | 28.309 | 25.369 | 24.864 | 15.179 | 2 | 0 | 57.097 | 54.527 | 48.083 | 22.287 | 0 | 0 | 52.693 | 34.873 | [5 empty] | 21.515 | 18.675 | 41 | 2.1763 | 1.9935 | 1.3737 | 1.2245 | 0.76896 | 35.3339
2005-10-31 | 5:26 | 0 | 21.522 | 0 | 2 | 0 | 46.853 | 47.105 | 28.628 | 28.243 | 25.617 | 24.896 | 15.186 | 1 | 0 | 57.103 | 54.555 | 48.114 | 22.27 | 0 | 0 | 52.677 | 34.856 | [5 empty] | 0 | 18.61 | 42 | 2.1742 | 1.9915 | 1.3736 | 1.2245 | 0.76703 | 35.2779
2005-10-31 | 5:27 | 0 | 21.498 | 0 | 2 | 0 | 46.853 | 47.22 | 28.724 | 28.388 | 25.666 | 25.038 | 15.111 | 1 | 0 | 57.17 | 54.534 | 47.976 | 22.27 | 0 | 0 | 52.677 | 34.88 | [5 empty] | 0 | 18.465 | 43 | 2.1961 | 2.0123 | 1.3745 | 1.2245 | 0.78779 | 35.8724
2005-10-31 | 5:28 | 0 | 21.522 | 0 | 2 | 0 | 47.012 | 47.22 | 28.822 | 28.459 | 26.1 | 25.016 | 15.136 | 1 | 0 | 57.126 | 54.555 | 47.976 | 22.295 | 0 | 0 | 52.677 | 34.904 | [5 empty] | 0 | 18.553 | 44 | 2.1888 | 2.0054 | 1.3742 | 1.2245 | 0.78087 | 35.6756
2005-10-31 | 5:29 | 0 | 21.498 | 0 | 2 | 0 | 47.747 | 47.311 | 28.846 | 28.557 | 26.267 | 25.063 | 15.111 | 2 | 0 | 57.147 | 54.555 | 48.09 | 22.27 | 0 | 0 | 52.677 | 34.833 | [5 empty] | 0 | 19.19 | 45 | 2.1961 | 2.0123 | 1.3745 | 1.2245 | 0.78779 | 35.8724
2005-10-31 | 5:30 | 0 | 21.444 | 0 | 2 | 0 | 47.761 | 47.693 | 28.959 | 28.572 | 26.284 | 25.031 | 15.078 | 1 | 0 | 57.14 | 54.504 | 48.06 | 22.263 | 0 | 0 | 52.646 | 34.756 | [5 empty] | 0 | 19.189 | 46 | 2.2057 | 2.0214 | 1.3749 | 1.2245 | 0.79692 | 36.1302
2005-10-31 | 5:31 | 1 | 21.522 | 0 | 2 | 0 | 47.7 | 48.137 | 29.278 | 28.846 | 26.34 | 25.087 | 15.063 | 1 | 0 | 57.147 | 54.511 | 48.023 | 22.295 | 0 | 0 | 52.677 | 34.811 | [5 empty] | 21.522 | 18.854 | 47 | 2.2101 | 2.0256 | 1.375 | 1.2245 | 0.80107 | 36.2467
2005-10-31 | 5:32 | 0 | 21.466 | 1 | 2 | 1 | 47.556 | 48.06 | 29.68 | 28.91 | 26.38 | 25.151 | 15.078 | 1 | 0 | 57.186 | 54.525 | 47.922 | 22.238 | 0 | 0 | 52.623 | 34.756 | [5 empty] | 0 | 18.646 | 48 | 2.2057 | 2.0214 | 1.3749 | 1.2245 | 0.79692 | 36.1302
2005-10-31 | 5:33 | 0 | 21.498 | 0 | 2 | 0 | 48.023 | 47.952 | 30.195 | 29.302 | 26.654 | 25.232 | 15.063 | 1 | 0 | 57.238 | 54.534 | 47.976 | 22.27 | 0 | 0 | 52.677 | 34.763 | [5 empty] | 0 | 18.721 | 0 | 2.2101 | 2.0256 | 1.375 | 1.2245 | 0.80107 | 36.2467
2005-10-31 | 5:34 | 0 | 21.498 | 0 | 2 | 0 | 48.342 | 48.09 | 30.604 | 29.687 | 26.799 | 25.137 | 15.013 | 2 | 0 | 57.238 | 54.555 | 47.976 | 22.295 | 0 | 0 | 52.653 | 34.787 | [5 empty] | 0 | 18.655 | 1 | 2.2246 | 2.0394 | 1.0467 | 0.89552 | 1.1439 | 51.4192
2005-10-31 | 5:35 | 0 | 21.466 | 0 | 2 | 0 | 48.678 | 48.426 | 31.102 | 30.163 | 27.007 | 25.151 | 14.98 | 1 | 0 | 57.208 | 54.548 | 48.037 | 22.238 | 0 | 0 | 52.599 | 34.756 | [5 empty] | 0 | 18.515 | 2 | 2.2342 | 2.0485 | 1.0471 | 0.89552 | 1.153 | 51.6069
2005-10-31 | 5:36 | 0 | 21.466 | 0 | 2 | 0 | 49.047 | 48.816 | 31.583 | 30.764 | 27.152 | 25.274 | 14.98 | 1 | 0 | 57.229 | 54.525 | 47.945 | 22.263 | 0 | 0 | 52.623 | 34.732 | [5 empty] | 0 | 18.283 | 3 | 2.2342 | 2.0485 | 1.0471 | 0.89552 | 1.153 | 51.6069
2005-10-31 | 5:37 | 1 | 21.466 | 0 | 2 | 0 | 49.642 | 49.115 | 31.946 | 31.247 | 27.513 | 25.345 | 14.98 | 1 | 0 | 57.252 | 54.548 | 47.992 | 22.263 | 0 | 0 | 52.623 | 34.801 | [5 empty] | 21.466 | 18.395 | 4 | 2.2342 | 2.0485 | 1.0471 | 0.89552 | 1.153 | 51.6069
2005-10-31 | 5:38 | 0 | 21.466 | 0 | 1 | 0 | 45.308 | 49.551 | 32.331 | 31.632 | 24.067 | 25.249 | 15.053 | 1 | 0 | 57.208 | 54.548 | 48.107 | 22.238 | 0 | 0 | 52.576 | 34.801 | [5 empty] | 0 | 13.676 | 5 | 2.213 | 2.0283 | 1.0462 | 0.89552 | 1.1328 | 51.1895
2005-10-31 | 5:39 | 0 | 21.49 | 0 | 2 | 0 | 36.988 | 49.894 | 32.57 | 32.017 | 21.973 | 25.345 | 14.955 | 1 | 0 | 57.208 | 54.548 | 47.992 | 22.263 | 0 | 0 | 52.576 | 34.825 | [5 empty] | 0 | 4.971 | 6 | 2.2415 | 2.0555 | 1.0474 | 0.89552 | 1.1599 | 51.748
2005-10-31 | 5:40 | 0 | 21.522 | 0 | 2 | 0 | 34.646 | 42.752 | 32.835 | 32.289 | 20.61 | 25.306 | 15.063 | 0 | 0 | 57.259 | 54.555 | 48.181 | 22.27 | 0 | 0 | 52.585 | 34.88 | [5 empty] | 0 | 2.357 | 7 | 2.2101 | 2.0256 | 1.0461 | 0.89552 | 1.13 | 51.1317
2005-10-31 | 5:41 | 0 | 21.466 | 0 | 2 | 0 | 34.003 | 37.129 | 32.9 | 32.618 | 19.797 | 25.274 | 15.005 | 0 | 0 | 57.229 | 54.504 | 48.06 | 22.263 | 0 | 0 | 52.599 | 34.849 | [5 empty] | 0 | 1.385 | 8 | 2.2269 | 2.0416 | 1.0468 | 0.89552 | 1.1461 | 51.4649
2005-10-31 | 5:42 | 0 | 21.466 | 0 | 2 | 0 | 33.768 | 35.225 | 33.041 | 32.735 | 19.45 | 25.249 | 15.03 | 0 | 0 | 57.229 | 54.548 | 48.151 | 22.263 | 0 | 0 | 52.599 | 34.801 | [5 empty] | 0 | 1.033 | 9 | 2.2197 | 2.0347 | 1.0465 | 0.89552 | 1.1392 | 51.3219
2005-10-31 | 5:43 | 0 | 21.522 | 1 | 1 | 0 | 33.706 | 34.622 | 33.189 | 32.859 | 19.038 | 25.328 | 15.063 | 0 | 0 | 57.281 | 54.555 | 48.067 | 22.27 | 0 | 0 | 52.653 | 34.833 | [5 empty] | 0 | 0.847 | 10 | 2.2101 | 2.0256 | 1.0461 | 0.89552 | 1.13 | 51.1317
2005-10-31 | 5:44 | 0 | 21.522 | 0 | 2 | 0 | 33.658 | 34.364 | 33.165 | 32.952 | 18.94 | 25.306 | 15.038 | 0 | 0 | 57.259 | 54.555 | 48.067 | 22.295 | 0 | 0 | 52.653 | 34.833 | [5 empty] | 0 | 0.706 | 11 | 2.2173 | 2.0325 | 1.0464 | 0.89552 | 1.137 | 51.2759
2005-10-31 | 5:45 | 0 | 21.515 | 0 | 2 | 0 | 33.603 | 34.144 | 33.11 | 33.086 | 18.61 | 25.394 | 15.03 | 0 | 0 | 57.252 | 54.504 | 48.016 | 22.263 | 0 | 0 | 52.646 | 34.825 | [5 empty] | 0 | 0.517 | 12 | 2.2197 | 2.0347 | 1.0465 | 0.89552 | 1.1392 | 51.3219
2005-10-31 | 5:46 | 0 | 21.439 | 0 | 2 | 0 | 33.601 | 34.024 | 32.778 | 33.153 | 18.286 | 25.173 | 14.978 | 1 | 0 | 57.158 | 54.453 | 48.034 | 22.236 | 0 | 0 | 52.574 | 34.823 | [5 empty] | 0 | 0.448 | 13 | 2.2348 | 2.0491 | 1.0471 | 0.89552 | 1.1536 | 51.6182
2005-10-31 | 5:47 | 0 | 21.463 | 0 | 2 | 0 | 33.553 | 33.928 | 32.685 | 32.895 | 18.213 | 25.318 | 15.003 | 0 | 0 | 57.181 | 54.453 | 48.011 | 22.211 | 0 | 0 | 52.574 | 34.847 | [5 empty] | 0 | 0.658 | 14 | 2.2275 | 2.0422 | 1.0468 | 0.89552 | 1.1466 | 51.4763
2005-10-31 | 5:48 | 0 | 21.463 | 0 | 2 | 0 | 42.154 | 33.907 | 32.448 | 32.802 | 25.654 | 25.222 | 14.978 | 0 | 0 | 57.092 | 54.453 | 48.034 | 22.236 | 0 | 0 | 52.55 | 34.847 | [5 empty] | 0 | 9.352 | 15 | 2.2348 | 2.0491 | 1.0471 | 0.89552 | 1.1536 | 51.6182
2005-10-31 | 5:49 | 0 | 21.439 | 0 | 1 | 0 | 45.649 | 34.165 | 32.11 | 32.613 | 22.378 | 25.198 | 14.978 | 0 | 0 | 57.113 | 54.429 | 48.055 | 22.236 | 0 | 0 | 52.527 | 34.823 | [5 empty] | 0 | 13.036 | 16 | 2.2348 | 2.0491 | 1.0471 | 0.89552 | 1.1536 | 51.6182
2005-10-31 | 5:50 | 0 | 21.439 | 0 | 2 | 0 | 37.079 | 44.617 | 31.796 | 32.35 | 20.262 | 25.149 | 14.978 | 1 | 0 | 57.069 | 54.429 | 48.055 | 22.236 | 0 | 0 | 52.504 | 34.823 | [5 empty] | 0 | 4.729 | 17 | 2.2348 | 2.0491 | 1.0471 | 0.89552 | 1.1536 | 51.6182
2005-10-31 | 5:51 | 0 | 21.463 | 0 | 2 | 0 | 34.447 | 42.693 | 31.58 | 32.184 | 19.126 | 25.173 | 15.003 | 0 | 0 | 57.024 | 54.406 | 47.988 | 22.236 | 0 | 0 | 52.504 | 34.823 | [5 empty] | 0 | 2.263 | 18 | 2.2275 | 2.0422 | 1.0468 | 0.89552 | 1.1466 | 51.4763
2005-10-31 | 5:52 | 0 | 21.493 | 0 | 2 | 0 | 33.44 | 36.918 | 31.394 | 31.804 | 18.859 | 25.203 | 15.106 | 0 | 0 | 57.097 | 54.457 | 48.083 | 22.287 | 0 | 0 | 52.532 | 34.852 | [5 empty] | 0 | 1.636 | 19 | 2.1975 | 2.0137 | 1.0456 | 0.89552 | 1.1181 | 50.8815
2005-10-31 | 5:53 | 0 | 21.517 | 0 | 1 | 0 | 32.878 | 34.804 | 31.176 | 31.49 | 18.54 | 25.132 | 15.106 | 0 | 0 | 57.074 | 54.434 | 47.992 | 22.287 | 0 | 0 | 52.508 | 34.804 | [5 empty] | 0 | 1.388 | 20 | 2.1975 | 2.0137 | 1.0456 | 0.89552 | 1.1181 | 50.8815
2005-10-31 | 5:54 | 0 | 21.439 | 0 | 2 | 0 | 32.495 | 33.766 | 31.026 | 31.22 | 18.188 | 25.198 | 15.05 | 0 | 0 | 57.024 | 54.385 | 47.941 | 22.211 | 0 | 0 | 52.48 | 34.751 | [5 empty] | 0 | 1.275 | 21 | 2.2138 | 2.0292 | 1.0462 | 0.89552 | 1.1336 | 51.2068
2005-10-31 | 5:55 | 0 | 21.463 | 1 | 2 | 0 | 32.159 | 33.271 | 30.81 | 31.002 | 17.989 | 25.198 | 15.076 | 0 | 0 | 57.024 | 54.385 | 47.964 | 22.236 | 0 | 0 | 52.48 | 34.775 | [5 empty] | 0 | 1.157 | 22 | 2.2063 | 2.022 | 1.0459 | 0.89552 | 1.1264 | 51.0564
2005-10-31 | 5:56 | 0 | 21.463 | 0 | 1 | 0 | 31.821 | 32.895 | 30.592 | 30.761 | 17.942 | 25.053 | 15.076 | 0 | 0 | 57.001 | 54.362 | 47.941 | 22.236 | 0 | 0 | 52.504 | 34.799 | [5 empty] | 0 | 1.06 | 23 | 2.2063 | 2.022 | 1.0459 | 0.89552 | 1.1264 | 51.0564
2005-10-31 | 5:57 | 0 | 21.439 | 0 | 2 | 0 | 31.58 | 32.52 | 30.423 | 30.761 | 17.645 | 25.029 | 15.076 | 0 | 0 | 56.98 | 54.362 | 47.964 | 22.258 | 0 | 0 | 52.48 | 34.823 | [5 empty] | 0 | 0.819 | 24 | 2.2063 | 2.022 | 1.0459 | 0.89552 | 1.1264 | 51.0564
2005-10-31 | 5:58 | 0 | 21.429 | 0 | 2 | 0 | 31.257 | 32.196 | 30.318 | 30.462 | 17.288 | 24.945 | 15.066 | 0 | 0 | 56.948 | 54.329 | 47.931 | 22.201 | 0 | 0 | 52.403 | 34.766 | [5 empty] | 0 | 0.795 | 25 | 2.2092 | 2.0247 | 1.046 | 0.89552 | 1.1292 | 51.1144
2005-10-31 | 5:59 | 0 | 21.429 | 0 | 1 | 0 | 35.234 | 31.835 | 30.293 | 30.389 | 24.85 | 24.994 | 15.04 | 0 | 0 | 56.88 | 54.306 | 47.864 | 22.177 | 0 | 0 | 52.403 | 34.766 | [5 empty] | 0 | 4.845 | 26 | 2.2168 | 2.0319 | 1.0464 | 0.89552 | 1.1364 | 51.2644
2005-10-31 | 6:00 | 0 | 21.463 | 0 | 2 | 0 | 46.176 | 31.651 | 30.063 | 30.256 | 21.512 | 25.004 | 15.076 | 1 | 0 | 56.912 | 54.315 | 47.92 | 22.236 | 0 | 0 | 52.366 | 34.799 | [5 empty] | 0 | 15.92 | 27 | 2.2063 | 2.022 | 1.0459 | 0.89552 | 1.1264 | 51.0564
2005-10-31 | 6:01 | 0 | 21.429 | 0 | 2 | 0 | 35.871 | 40.545 | 29.933 | 30.148 | 19.189 | 25.09 | 15.015 | 0 | 0 | 56.925 | 54.282 | 47.77 | 22.177 | 0 | 0 | 52.357 | 34.766 | [5 empty] | 0 | 5.723 | 28 | 2.224 | 2.0388 | 1.0466 | 0.89552 | 1.1433 | 51.4078
2005-10-31 | 6:02 | 0 | 21.429 | 0 | 2 | 0 | 32.39 | 42.26 | 29.643 | 29.933 | 18.203 | 24.899 | 15.066 | 0 | 0 | 56.857 | 54.306 | 47.817 | 22.224 | 0 | 0 | 52.403 | 34.79 | [5 empty] | 0 | 2.457 | 29 | 2.2092 | 2.0247 | 1.046 | 0.89552 | 1.1292 | 51.1144
2005-10-31 | 6:03 | 0 | 21.463 | 0 | 1 | 0 | 31.291 | 35.385 | 29.582 | 29.773 | 17.595 | 24.933 | 15.076 | 1 | 0 | 56.846 | 54.292 | 47.826 | 22.236 | 0 | 0 | 52.389 | 34.775 | [5 empty] | 0 | 1.518 | 30 | 2.2063 | 2.022 | 1.0459 | 0.89552 | 1.1264 | 51.0564
2005-10-31 | 6:04 | 0 | 21.488 | 0 | 2 | 0 | 30.81 | 32.708 | 29.533 | 29.629 | 17.077 | 24.98 | 15.028 | 0 | 0 | 56.846 | 54.315 | 47.826 | 22.236 | 0 | 0 | 52.413 | 34.799 | [5 empty] | 0 | 1.181 | 31 | 2.2202 | 2.0352 | 1.0465 | 0.89552 | 1.1397 | 51.3334
2005-10-31 | 6:05 | 0 | 21.429 | 0 | 2 | 0 | 30.413 | 31.666 | 29.283 | 29.403 | 16.818 | 24.899 | 15.015 | 0 | 0 | 56.834 | 54.282 | 47.887 | 22.201 | 0 | 0 | 52.357 | 34.766 | [5 empty] | 0 | 1.01 | 32 | 2.224 | 2.0388 | 1.0466 | 0.89552 | 1.1433 | 51.4078
2005-10-31 | 6:06 | 0 | 21.49 | 1 | 2 | 0 | 30.259 | 31.198 | 29.271 | 29.464 | 16.732 | 24.886 | 15.03 | 0 | 0 | 56.848 | 54.296 | 47.831 | 22.263 | 0 | 0 | 52.394 | 34.849 | [5 empty] | 0 | 0.795 | 33 | 2.2197 | 2.0347 | 1.0465 | 0.89552 | 1.1392 | 51.3219
2005-10-31 | 6:07 | 0 | 21.49 | 0 | 1 | 0 | 29.994 | 30.837 | 29.246 | 29.271 | 16.659 | 24.911 | 15.078 | 0 | 0 | 56.848 | 54.32 | 47.854 | 22.263 | 0 | 0 | 52.371 | 34.801 | [5 empty] | 0 | 0.723 | 34 | 2.2057 | 2.0214 | 1.0459 | 0.89552 | 1.1259 | 51.0448
2005-10-31 | 6:08 | 0 | 21.461 | 0 | 2 | 0 | 29.82 | 30.543 | 29.146 | 29.217 | 16.727 | 24.835 | 15.023 | 0 | 0 | 56.82 | 54.245 | 47.78 | 22.233 | 0 | 0 | 52.389 | 34.751 | [5 empty] | 0 | 0.603 | 35 | 2.2217 | 2.0366 | 1.0466 | 0.89552 | 1.1411 | 51.362
2005-10-31 | 6:09 | 0 | 21.461 | 0 | 2 | 0 | 29.651 | 30.3 | 29.072 | 29.121 | 16.431 | 24.906 | 15 | 0 | 0 | 56.777 | 54.245 | 47.733 | 22.209 | 0 | 0 | 52.366 | 34.703 | [5 empty] | 0 | 0.53 | 36 | 2.2284 | 2.043 | 1.0468 | 0.89552 | 1.1475 | 51.4933
2005-10-31 | 6:10 | 0 | 21.461 | 0 | 2 | 0 | 30.999 | 30.158 | 28.976 | 29.001 | 25.291 | 24.81 | 15.048 | 0 | 0 | 56.8 | 54.245 | 47.689 | 22.233 | 0 | 0 | 52.366 | 34.727 | [5 empty] | 0 | 1.998 | 37 | 2.2144 | 2.0297 | 1.0463 | 0.89552 | 1.1342 | 51.2184
2005-10-31 | 6:11 | 0 | 21.461 | 0 | 1 | 0 | 46.083 | 29.94 | 28.807 | 28.976 | 21.39 | 24.761 | 15 | 0 | 0 | 56.754 | 54.224 | 47.733 | 22.209 | 0 | 0 | 52.343 | 34.727 | [5 empty] | 0 | 17.107 | 38 | 2.2284 | 2.043 | 1.0468 | 0.89552 | 1.1475 | 51.4933
2005-10-31 | 6:12 | 0 | 21.49 | 0 | 2 | 0 | 35.249 | 38.234 | 28.815 | 28.886 | 19.153 | 24.84 | 15.005 | 1 | 0 | 56.804 | 54.273 | 47.693 | 22.263 | 0 | 0 | 52.394 | 34.732 | [5 empty] | 0 | 6.363 | 39 | 2.2269 | 2.0416 | 1.0468 | 0.89552 | 1.1461 | 51.4649
2005-10-31 | 6:13 | 0 | 21.461 | 0 | 2 | 0 | 31.264 | 41.446 | 28.785 | 28.807 | 17.889 | 24.931 | 14.975 | 0 | 0 | 56.754 | 54.224 | 47.665 | 22.209 | 0 | 0 | 52.319 | 34.703 | [5 empty] | 0 | 2.457 | 40 | 2.2357 | 2.0499 | 1.0471 | 0.89552 | 1.1544 | 51.6352
2005-10-31 | 6:14 | 0 | 21.461 | 0 | 2 | 0 | 30.085 | 34.261 | 28.716 | 28.692 | 17.301 | 24.766 | 14.93 | 0 | 0 | 56.759 | 54.229 | 47.693 | 22.238 | 0 | 0 | 52.303 | 34.756 | [5 empty] | 0 | 1.393 | 41 | 2.2488 | 2.0624 | 1.0476 | 0.89552 | 1.1669 | 51.8882
2005-10-31 | 6:15 | 0 | 21.461 | 0 | 2 | 0 | 29.555 | 31.409 | 28.567 | 28.496 | 16.926 | 24.737 | 14.925 | 0 | 0 | 56.731 | 54.201 | 47.756 | 22.209 | 0 | 0 | 52.275 | 34.727 | [5 empty] | 0 | 1.059 | 42 | 2.2502 | 2.0638 | 1.0477 | 0.89552 | 1.1682 | 51.9161
2005-10-31 | 6:16 | 0 | 21.515 | 0 | 2 | 0 | 29.32 | 30.475 | 28.572 | 28.476 | 16.536 | 24.791 | 14.955 | 1 | 0 | 56.736 | 54.229 | 47.693 | 22.263 | 0 | 0 | 52.347 | 34.756 | [5 empty] | 0 | 0.844 | 43 | 2.2415 | 2.0555 | 1.0474 | 0.89552 | 1.1599 | 51.748
2005-10-31 | 6:17 | 0 | 21.49 | 0 | 1 | 0 | 29.15 | 29.969 | 28.621 | 28.476 | 16.265 | 24.815 | 14.93 | 0 | 0 | 56.782 | 54.205 | 47.67 | 22.214 | 0 | 0 | 52.347 | 34.756 | [5 empty] | 0 | 0.674 | 44 | 2.2488 | 2.0624 | 1.0476 | 0.89552 | 1.1669 | 51.8882
2005-10-31 | 6:18 | 0 | 21.461 | 1 | 2 | 0 | 28.952 | 29.675 | 28.376 | 28.376 | 16.282 | 24.737 | 14.975 | 0 | 0 | 56.709 | 54.201 | 47.712 | 22.233 | 0 | 0 | 52.252 | 34.727 | [5 empty] | 0 | 0.576 | 45 | 2.2357 | 2.0499 | 1.0471 | 0.89552 | 1.1544 | 51.6352
2005-10-31 | 6:19 | 0 | 21.466 | 0 | 2 | 0 | 28.861 | 29.511 | 28.381 | 28.405 | 16.24 | 24.742 | 14.955 | 0 | 0 | 56.715 | 54.205 | 47.761 | 22.238 | 0 | 0 | 52.28 | 34.756 | [5 empty] | 0 | 0.456 | 46 | 2.2415 | 2.0555 | 1.0474 | 0.89552 | 1.1599 | 51.748
2005-10-31 | 6:20 | 0 | 21.461 | 0 | 2 | 0 | 28.761 | 29.315 | 28.376 | 28.302 | 16.184 | 24.69 | 14.925 | 0 | 0 | 56.688 | 54.154 | 47.665 | 22.209 | 0 | 0 | 52.275 | 34.679 | [5 empty] | 0 | 0.459 | 47 | 2.2502 | 2.0638 | 1.0477 | 0.89552 | 1.1682 | 51.9161
2005-10-31 | 6:21 | 1 | 21.461 | 0 | 2 | 0 | 28.856 | 29.146 | 28.302 | 28.398 | 25.171 | 24.617 | 14.875 | 0 | 0 | 56.665 | 54.131 | 47.574 | 22.209 | 0 | 0 | 52.275 | 34.679 | [5 empty] | 21.461 | 0.458 | 48 | 2.2648 | 2.0776 | 1.0483 | 0.89552 | 1.1821 | 52.1935
2005-10-31 | 6:22 | 0 | 21.461 | 0 | 2 | 0 | 45.511 | 29.025 | 28.278 | 28.302 | 20.62 | 24.641 | 14.875 | 0 | 0 | 56.642 | 54.131 | 47.574 | 22.233 | 0 | 0 | 52.252 | 34.632 | [5 empty] | 0 | 17.209 | 49 | 2.2648 | 2.0776 | 1.0483 | 0.89552 | 1.1821 | 52.1935
2005-10-31 | 6:23 | 0 | 21.461 | 0 | 2 | 0 | 35.151 | 36.395 | 28.206 | 28.206 | 18.062 | 24.666 | 14.875 | 1 | 0 | 56.642 | 54.131 | 47.642 | 22.233 | 0 | 0 | 52.228 | 34.61 | [5 empty] | 0 | 6.945 | 50 | 2.2648 | 2.0776 | 1.0483 | 0.89552 | 1.1821 | 52.1935
2005-10-31 | 6:24 | 0 | 21.486 | 0 | 2 | 0 | 30.639 | 40.671 | 28.278 | 28.157 | 17.147 | 24.737 | 14.875 | 0 | 0 | 56.642 | 54.086 | 47.504 | 22.209 | 0 | 0 | 52.275 | 34.632 | [5 empty] | 0 | 2.482 | 51 | 2.2648 | 2.0776 | 1.0483 | 0.89552 | 1.1821 | 52.1935
2005-10-31 | 6:25 | 0 | 21.461 | 0 | 2 | 0 | 29.361 | 33.292 | 28.231 | 28.086 | 16.629 | 24.69 | 14.875 | 0 | 0 | 56.597 | 54.086 | 47.619 | 22.209 | 0 | 0 | 52.275 | 34.632 | [5 empty] | 0 | 1.275 | 52 | 2.2648 | 2.0776 | 1.0483 | 0.89552 | 1.1821 | 52.1935
2005-10-31 | 6:26 | 0 | 21.463 | 0 | 2 | 0 | 29.003 | 30.57 | 28.305 | 28.209 | 16.287 | 24.644 | 14.902 | 0 | 0 | 56.599 | 54.112 | 47.621 | 22.211 | 0 | 0 | 52.277 | 34.634 | [5 empty] | 0 | 0.794 | 53 | 2.2569 | 2.0701 | 1.048 | 0.89552 | 1.1746 | 52.0442
2005-10-31 | 6:27 | 0 | 21.463 | 0 | 2 | 0 | 28.667 | 29.607 | 28.184 | 28.064 | 15.89 | 24.595 | 14.804 | 0 | 0 | 56.576 | 54.089 | 47.577 | 22.187 | 0 | 0 | 52.254 | 34.613 | [5 empty] | 0 | 0.603 | 54 | 2.2855 | 2.0973 | 1.0491 | 0.89552 | 1.2017 | 52.5812
2005-10-31 | 6:28 | 0 | 21.517 | 0 | 2 | 0 | 28.574 | 29.226 | 28.263 | 28.069 | 15.873 | 24.698 | 14.859 | 0 | 0 | 56.672 | 54.093 | 47.514 | 22.216 | 0 | 0 | 52.305 | 34.641 | [5 empty] | 0 | 0.505 | 55 | 2.2695 | 2.082 | 1.0485 | 0.89552 | 1.1865 | 52.2815
2005-10-31 | 6:29 | 0 | 21.463 | 0 | 2 | 0 | 28.449 | 29.003 | 28.16 | 28.015 | 15.619 | 24.668 | 14.854 | 1 | 0 | 56.622 | 54.065 | 47.486 | 22.187 | 0 | 0 | 52.254 | 34.589 | [5 empty] | 0 | 0.434 | 56 | 2.2709 | 2.0834 | 1.0485 | 0.89552 | 1.1879 | 52.3089
2005-10-31 | 6:30 | 0 | 21.493 | 1 | 2 | 0 | 28.454 | 28.864 | 28.045 | 28.094 | 15.649 | 24.602 | 14.834 | 0 | 0 | 56.604 | 54.093 | 47.558 | 22.216 | 0 | 0 | 52.259 | 34.617 | [5 empty] | 0 | 0.36 | 57 | 2.2767 | 2.0889 | 1.0488 | 0.89552 | 1.1934 | 52.4182
2005-10-31 | 6:31 | 0 | 21.463 | 0 | 2 | 0 | 28.305 | 28.788 | 28.015 | 27.92 | 15.669 | 24.595 | 14.854 | 0 | 0 | 56.556 | 54.042 | 47.486 | 22.187 | 0 | 0 | 52.207 | 34.565 | [5 empty] | 0 | 0.385 | 58 | 2.2709 | 2.0834 | 1.0485 | 0.89552 | 1.1879 | 52.3089
2005-10-31 | 6:32 | 0 | 21.463 | 0 | 2 | 0 | 28.233 | 28.618 | 27.944 | 27.871 | 22.501 | 24.499 | 14.804 | 0 | 0 | 56.533 | 54.019 | 47.486 | 22.211 | 0 | 0 | 52.207 | 34.589 | [5 empty] | 0 | 0.362 | 59 | 2.2855 | 2.0973 | 1.0491 | 0.89552 | 1.2017 | 52.5812
2005-10-31 | 6:33 | 0 | 21.488 | 0 | 2 | 0 | 43.987 | 28.545 | 28.015 | 27.848 | 23.391 | 24.619 | 14.854 | 0 | 0 | 56.576 | 54.042 | 47.462 | 22.187 | 0 | 0 | 52.207 | 34.565 | [5 empty] | 0 | 16.139 | 60 | 2.2709 | 2.0834 | 1.0485 | 0.89552 | 1.1879 | 52.3089
2005-10-31 | 6:34 | 0 | 21.488 | 0 | 2 | 0 | 46.613 | 35.598 | 27.871 | 27.848 | 24.04 | 24.595 | 14.854 | 1 | 0 | 56.51 | 53.995 | 47.462 | 22.211 | 0 | 0 | 52.184 | 34.517 | [5 empty] | 0 | 18.765 | 61 | 2.2709 | 2.0834 | 1.0485 | 0.89552 | 1.1879 | 52.3089
2005-10-31 | 6:35 | 0 | 21.463 | 0 | 2 | 0 | 46.659 | 45.215 | 27.92 | 27.775 | 23.849 | 24.548 | 14.829 | 1 | 0 | 56.533 | 53.995 | 47.416 | 22.187 | 0 | 0 | 52.207 | 34.541 | [5 empty] | 0 | 18.884 | 62 | 2.2782 | 2.0903 | 1.0488 | 0.89552 | 1.1948 | 52.4455
2005-10-31 | 6:36 | 1 | 21.463 | 0 | 2 | 0 | 46.498 | 46.568 | 27.895 | 27.775 | 23.415 | 24.573 | 14.731 | 2 | 0 | 56.533 | 53.995 | 47.53 | 22.187 | 0 | 0 | 52.207 | 34.541 | [5 empty] | 21.463 | 18.723 | 63 | 2.3067 | 2.1175 | 1.05 | 0.89552 | 1.2219 | 52.9726
2005-10-31 | 6:37 | 0 | 21.463 | 0 | 2 | 0 | 46.2 | 46.498 | 28.064 | 27.799 | 23.56 | 24.619 | 14.829 | 1 | 0 | 56.533 | 53.974 | 47.439 | 22.187 | 0 | 0 | 52.207 | 34.471 | [5 empty] | 0 | 18.401 | 64 | 2.2782 | 2.0903 | 1.0488 | 0.89552 | 1.1948 | 52.4455
2005-10-31 | 6:38 | 0 | 21.488 | 0 | 2 | 0 | 46.179 | 46.246 | 28.113 | 27.824 | 23.825 | 24.693 | 14.804 | 1 | 0 | 56.556 | 53.995 | 47.462 | 22.162 | 0 | 0 | 52.207 | 34.495 | [5 empty] | 0 | 18.355 | 65 | 2.2855 | 2.0973 | 1.0491 | 0.89552 | 1.2017 | 52.5812
2005-10-31 | 6:39 | 0 | 21.463 | 0 | 2 | 1 | 46.041 | 46.431 | 28.113 | 27.871 | 24.018 | 24.573 | 14.779 | 1 | 0 | 56.556 | 53.974 | 47.553 | 22.211 | 0 | 0 | 52.163 | 34.541 | [5 empty] | 0 | 18.17 | 66 | 2.2928 | 2.1042 | 1.0494 | 0.89552 | 1.2087 | 52.7161
2005-10-31 | 6:40 | 0 | 21.439 | 1 | 2 | 0 | 46.062 | 46.361 | 28.184 | 27.871 | 24.21 | 24.668 | 14.706 | 1 | 0 | 56.556 | 53.974 | 47.553 | 22.187 | 0 | 0 | 52.14 | 34.541 | [5 empty] | 0 | 18.191 | 0 | 2.314 | 2.1244 | 1.0503 | 0.89552 | 1.2289 | 53.105
2005-10-31 | 6:41 | 0 | 21.463 | 0 | 2 | 0 | 46.041 | 46.293 | 28.28 | 28.015 | 24.499 | 24.693 | 14.779 | 2 | 0 | 56.556 | 53.951 | 47.439 | 22.187 | 0 | 0 | 52.14 | 34.541 | [5 empty] | 0 | 18.026 | 1 | 2.2928 | 2.1042 | 1.6173 | 1.4634 | 0.64076 | 27.9471
2005-10-31 | 6:42 | 1 | 21.463 | 0 | 2 | 0 | 46.223 | 46.361 | 28.425 | 28.184 | 24.884 | 24.715 | 14.804 | 1 | 0 | 56.576 | 53.951 | 47.462 | 22.187 | 0 | 0 | 52.14 | 34.541 | [5 empty] | 21.463 | 18.039 | 2 | 2.2855 | 2.0973 | 1.617 | 1.4634 | 0.63384 | 27.7333
2005-10-31 | 6:43 | 0 | 21.488 | 0 | 2 | 0 | 46.979 | 46.293 | 28.449 | 28.209 | 25.149 | 24.788 | 14.779 | 1 | 0 | 56.599 | 53.974 | 47.462 | 22.187 | 0 | 0 | 52.093 | 34.565 | [5 empty] | 0 | 18.77 | 3 | 2.2928 | 2.1042 | 1.6173 | 1.4634 | 0.64076 | 27.9471
2005-10-31 | 6:44 | 0 | 21.463 | 0 | 2 | 0 | 46.958 | 46.774 | 28.594 | 28.305 | 25.318 | 24.933 | 14.804 | 2 | 0 | 56.668 | 53.995 | 47.439 | 22.236 | 0 | 0 | 52.116 | 34.565 | [5 empty] | 0 | 18.653 | 4 | 2.2855 | 2.0973 | 1.617 | 1.4634 | 0.63384 | 27.7333
2005-10-31 | 6:45 | 0 | 21.488 | 0 | 3 | 0 | 46.888 | 47.301 | 28.618 | 28.449 | 25.558 | 24.837 | 14.804 | 1 | 0 | 56.645 | 53.974 | 47.486 | 22.211 | 0 | 0 | 52.116 | 34.565 | [5 empty] | 0 | 18.439 | 5 | 2.2855 | 2.0973 | 1.617 | 1.4634 | 0.63384 | 27.7333
2005-10-31 | 6:46 | 0 | 21.471 | 0 | 2 | 0 | 46.849 | 47.192 | 28.817 | 28.383 | 25.566 | 24.987 | 14.787 | 1 | 0 | 56.672 | 53.956 | 47.467 | 22.194 | 0 | 0 | 52.098 | 34.5 | [5 empty] | 0 | 18.466 | 6 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 6:47 | 1 | 21.471 | 0 | 2 | 0 | 47.306 | 47.215 | 28.913 | 28.503 | 25.902 | 24.94 | 14.736 | 1 | 0 | 56.626 | 53.979 | 47.467 | 22.194 | 0 | 0 | 52.144 | 34.524 | [5 empty] | 21.471 | 18.803 | 7 | 2.3053 | 2.1161 | 1.6178 | 1.4634 | 0.65266 | 28.3116
2005-10-31 | 6:48 | 0 | 21.495 | 0 | 2 | 0 | 47.787 | 47.329 | 29.106 | 28.577 | 26.12 | 24.987 | 14.812 | 2 | 0 | 56.695 | 54 | 47.42 | 22.194 | 0 | 0 | 52.144 | 34.548 | [5 empty] | 0 | 19.21 | 8 | 2.2831 | 2.095 | 1.6169 | 1.4634 | 0.63162 | 27.6646
2005-10-31 | 6:49 | 0 | 21.471 | 1 | 2 | 0 | 47.81 | 47.903 | 29.322 | 28.697 | 26.191 | 25.011 | 14.761 | 1 | 0 | 56.695 | 53.979 | 47.558 | 22.17 | 0 | 0 | 52.121 | 34.524 | [5 empty] | 0 | 19.113 | 9 | 2.298 | 2.1092 | 1.6175 | 1.4634 | 0.64574 | 28.1002
2005-10-31 | 6:50 | 0 | 21.495 | 0 | 2 | 0 | 47.742 | 48.062 | 29.83 | 29.057 | 26.36 | 25.085 | 14.787 | 1 | 0 | 56.695 | 53.956 | 47.42 | 22.194 | 0 | 0 | 52.098 | 34.548 | [5 empty] | 0 | 18.685 | 10 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 6:51 | 0 | 21.446 | 0 | 1 | 0 | 48.156 | 48.109 | 30.19 | 29.467 | 26.456 | 25.061 | 14.787 | 1 | 0 | 56.695 | 53.956 | 47.49 | 22.194 | 0 | 0 | 52.144 | 34.548 | [5 empty] | 0 | 18.689 | 11 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 6:52 | 0 | 21.414 | 0 | 2 | 0 | 48.354 | 48.193 | 30.737 | 29.749 | 26.713 | 25.1 | 14.829 | 2 | 0 | 56.665 | 53.949 | 47.413 | 22.138 | 0 | 0 | 52.091 | 34.517 | [5 empty] | 0 | 18.605 | 12 | 2.2782 | 2.0903 | 1.6167 | 1.4634 | 0.62692 | 27.5182
2005-10-31 | 6:53 | 1 | 21.471 | 0 | 2 | 0 | 48.774 | 48.522 | 31.443 | 30.43 | 26.865 | 25.276 | 14.837 | 1 | 0 | 56.715 | 54 | 47.444 | 22.194 | 0 | 0 | 52.144 | 34.569 | [5 empty] | 21.471 | 18.344 | 13 | 2.2759 | 2.0881 | 1.6166 | 1.4634 | 0.6247 | 27.4491
2005-10-31 | 6:54 | 0 | 21.471 | 0 | 2 | 0 | 49.325 | 48.797 | 31.708 | 30.985 | 27.179 | 25.107 | 14.862 | 1 | 0 | 56.665 | 53.925 | 47.46 | 22.162 | 0 | 0 | 52.067 | 34.517 | [5 empty] | 0 | 18.34 | 14 | 2.2686 | 2.0812 | 1.6163 | 1.4634 | 0.61778 | 27.2321
2005-10-31 | 6:55 | 0 | 21.422 | 0 | 2 | 0 | 49.897 | 49.208 | 32.166 | 31.394 | 26.77 | 25.156 | 14.787 | 1 | 0 | 56.715 | 53.956 | 47.514 | 22.17 | 0 | 0 | 52.053 | 34.548 | [5 empty] | 0 | 18.503 | 15 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 6:56 | 0 | 21.471 | 0 | 2 | 0 | 40.75 | 49.829 | 32.527 | 31.899 | 23.857 | 25.205 | 14.787 | 1 | 0 | 56.715 | 53.979 | 47.49 | 22.194 | 0 | 0 | 52.074 | 34.569 | [5 empty] | 0 | 8.851 | 16 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 6:57 | 0 | 21.471 | 0 | 2 | 0 | 35.675 | 47.787 | 32.785 | 32.166 | 21.809 | 25.35 | 14.837 | 0 | 0 | 56.738 | 53.979 | 47.535 | 22.17 | 0 | 0 | 52.074 | 34.593 | [5 empty] | 0 | 3.509 | 17 | 2.2759 | 2.0881 | 1.6166 | 1.4634 | 0.6247 | 27.4491
2005-10-31 | 6:58 | 0 | 21.471 | 0 | 2 | 0 | 34.311 | 39.621 | 32.854 | 32.551 | 20.774 | 25.47 | 14.812 | 1 | 0 | 56.83 | 54.047 | 47.605 | 22.194 | 0 | 0 | 52.053 | 34.569 | [5 empty] | 0 | 1.76 | 18 | 2.2831 | 2.095 | 1.6169 | 1.4634 | 0.63162 | 27.6646
2005-10-31 | 6:59 | 0 | 21.446 | 0 | 2 | 0 | 33.912 | 36.05 | 32.95 | 32.737 | 19.973 | 25.276 | 14.787 | 0 | 0 | 56.761 | 53.979 | 47.535 | 22.194 | 0 | 0 | 52.098 | 34.569 | [5 empty] | 0 | 1.175 | 19 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 7:00 | 0 | 21.471 | 1 | 1 | 0 | 33.725 | 34.852 | 33.043 | 32.833 | 19.307 | 25.301 | 14.812 | 0 | 0 | 56.761 | 53.979 | 47.581 | 22.17 | 0 | 0 | 52.098 | 34.569 | [5 empty] | 0 | 0.892 | 20 | 2.2831 | 2.095 | 1.6169 | 1.4634 | 0.63162 | 27.6646
2005-10-31 | 7:01 | 0 | 21.446 | 0 | 2 | 0 | 33.653 | 34.5 | 33.137 | 32.996 | 19.108 | 25.325 | 14.787 | 0 | 0 | 56.761 | 53.979 | 47.581 | 22.194 | 0 | 0 | 52.074 | 34.548 | [5 empty] | 0 | 0.657 | 21 | 2.2904 | 2.102 | 1.6172 | 1.4634 | 0.63854 | 27.8788
2005-10-31 | 7:02 | 0 | 21.471 | 0 | 2 | 0 | 33.653 | 34.194 | 33.019 | 33.067 | 18.565 | 25.252 | 14.812 | 0 | 0 | 56.761 | 53.956 | 47.535 | 22.219 | 0 | 0 | 52.03 | 34.548 | [5 empty] | 0 | 0.586 | 22 | 2.2831 | 2.095 | 1.6169 | 1.4634 | 0.63162 | 27.6646
2005-10-31 | 7:03 | 0 | 21.471 | 0 | 2 | 0 | 33.632 | 34.077 | 32.878 | 33.091 | 18.366 | 25.252 | 14.837 | 0 | 0 | 56.715 | 53.979 | 47.558 | 22.17 | 0 | 0 | 52.007 | 34.548 | [5 empty] | 0 | 0.541 | 23 | 2.2759 | 2.0881 | 1.6166 | 1.4634 | 0.6247 | 27.4491
2005-10-31 | 7:04 | 0 | 21.471 | 0 | 2 | 0 | 33.56 | 33.983 | 32.692 | 32.996 | 18.17 | 25.421 | 14.812 | 0 | 0 | 56.738 | 53.956 | 47.514 | 22.194 | 0 | 0 | 51.983 | 34.5 | [5 empty] | 0 | 0.564 | 24 | 2.2831 | 2.095 | 1.6169 | 1.4634 | 0.63162 | 27.6646
2005-10-31 | 7:05 | 0 | 21.446 | 0 | 1 | 0 | 33.56 | 33.912 | 32.527 | 32.809 | 28.528 | 25.276 | 14.885 | 0 | 0 | 56.672 | 53.956 | 47.649 | 22.17 | 0 | 0 | 51.983 | 34.524 | [5 empty] | 0 | 0.751 | 25 | 2.2619 | 2.0748 | 1.6161 | 1.4634 | 0.61142 | 27.0313
2005-10-31 | 7:06 | 0 | 21.486 | 0 | 2 | 0 | 48.811 | 33.974 | 32.372 | 32.775 | 23.606 | 25.316 | 15 | 1 | 0 | 56.665 | 53.972 | 47.481 | 22.184 | 0 | 0 | 52.023 | 34.538 | [5 empty] | 0 | 16.036 | 26 | 2.2284 | 2.043 | 1.6147 | 1.4634 | 0.57959 | 26.009
2005-10-31 | 7:07 | 0 | 21.486 | 0 | 2 | 0 | 41.002 | 37.007 | 31.987 | 32.613 | 20.573 | 25.22 | 14.925 | 0 | 0 | 56.642 | 53.925 | 47.551 | 22.209 | 0 | 0 | 52.023 | 34.538 | [5 empty] | 0 | 8.389 | 27 | 2.2502 | 2.0638 | 1.6156 | 1.4634 | 0.60035 | 26.6792
2005-10-31 | 7:08 | 0 | 21.461 | 0 | 2 | 0 | 35.572 | 46.473 | 31.698 | 32.326 | 19.395 | 25.171 | 14.875 | 0 | 0 | 56.62 | 53.902 | 47.528 | 22.184 | 0 | 0 | 52.023 | 34.514 | [5 empty] | 0 | 3.246 | 28 | 2.2648 | 2.0776 | 1.6162 | 1.4634 | 0.61419 | 27.1187
2005-10-31 | 7:09 | 0 | 21.486 | 0 | 1 | 0 | 33.952 | 39.825 | 31.482 | 32.108 | 18.507 | 25.146 | 14.9 | 1 | 0 | 56.597 | 53.902 | 47.551 | 22.209 | 0 | 0 | 52.023 | 34.538 | [5 empty] | 0 | 1.844 | 29 | 2.2575 | 2.0707 | 1.6159 | 1.4634 | 0.60727 | 26.8997
2005-10-31 | 7:10 | 0 | 21.429 | 0 | 2 | 0 | 33.122 | 35.73 | 31.21 | 31.691 | 18.153 | 25.259 | 14.842 | 0 | 0 | 56.59 | 53.872 | 47.574 | 22.209 | 0 | 0 | 52 | 34.514 | [5 empty] | 0 | 1.431 | 30 | 2.2744 | 2.0867 | 1.6166 | 1.4634 | 0.62332 | 27.4058
2005-10-31 | 7:11 | 0 | 21.429 | 0 | 2 | 0 | 32.723 | 34.273 | 30.992 | 31.426 | 17.733 | 25.068 | 14.942 | 0 | 0 | 56.544 | 53.895 | 47.43 | 22.152 | 0 | 0 | 51.923 | 34.483 | [5 empty] | 0 | 1.297 | 31 | 2.2453 | 2.0591 | 1.6154 | 1.4634 | 0.59564 | 26.5284
2005-10-31 | 7:12 | 0 | 21.486 | 1 | 1 | 0 | 32.326 | 33.598 | 30.808 | 31.144 | 17.642 | 25.122 | 14.95 | 0 | 0 | 56.553 | 53.879 | 47.551 | 22.16 | 0 | 0 | 51.93 | 34.491 | [5 empty] | 0 | 1.182 | 32 | 2.243 | 2.0568 | 1.6153 | 1.4634 | 0.59343 | 26.4572
2005-10-31 | 7:13 | 0 | 21.486 | 0 | 2 | 0 | 32.036 | 33.106 | 30.568 | 30.928 | 17.295 | 25.075 | 14.95 | 0 | 0 | 56.531 | 53.925 | 47.481 | 22.209 | 0 | 0 | 51.953 | 34.491 | [5 empty] | 0 | 1.108 | 33 | 2.243 | 2.0568 | 1.6153 | 1.4634 | 0.59343 | 26.4572
2005-10-31 | 7:14 | 0 | 21.486 | 0 | 2 | 0 | 31.723 | 32.754 | 30.519 | 30.734 | 17.099 | 25.1 | 15 | 0 | 0 | 56.62 | 53.925 | 47.481 | 22.209 | 0 | 0 | 51.953 | 34.491 | [5 empty] | 0 | 0.989 | 34 | 2.2284 | 2.043 | 1.6147 | 1.4634 | 0.57959 | 26.009
2005-10-31 | 7:15 | 0 | 21.486 | 0 | 1 | 0 | 31.482 | 32.326 | 30.399 | 30.639 | 16.851 | 25.075 | 14.925 | 0 | 0 | 56.531 | 53.902 | 47.481 | 22.209 | 0 | 0 | 51.953 | 34.514 | [5 empty] | 0 | 0.843 | 35 | 2.2502 | 2.0638 | 1.6156 | 1.4634 | 0.60035 | 26.6792
2005-10-31 | 7:16 | 0 | 21.461 | 0 | 2 | 0 | 31.193 | 32.083 | 30.205 | 30.47 | 23.462 | 25.075 | 14.95 | 0 | 0 | 56.531 | 53.879 | 47.481 | 22.209 | 0 | 0 | 51.885 | 34.514 | [5 empty] | 0 | 0.723 | 36 | 2.243 | 2.0568 | 1.6153 | 1.4634 | 0.59343 | 26.4572
2005-10-31 | 7:17 | 0 | 21.429 | 0 | 2 | 0 | 45.962 | 31.74 | 30.126 | 30.367 | 23.285 | 25.019 | 14.942 | 0 | 0 | 56.567 | 53.895 | 47.474 | 22.297 | 0 | 0 | 51.899 | 34.459 | [5 empty] | 0 | 15.595 | 37 | 2.2453 | 2.0591 | 1.6154 | 1.4634 | 0.59564 | 26.5284
2005-10-31 | 7:18 | 0 | 21.486 | 0 | 2 | 0 | 40.836 | 33.058 | 29.915 | 30.254 | 20.161 | 25.146 | 14.95 | 1 | 0 | 56.531 | 53.855 | 47.413 | 22.184 | 0 | 0 | 51.976 | 34.514 | [5 empty] | 0 | 10.582 | 38 | 2.243 | 2.0568 | 1.6153 | 1.4634 | 0.59343 | 26.4572
2005-10-31 | 7:19 | 0 | 21.478 | 0 | 2 | 0 | 33.873 | 44.746 | 29.717 | 30.126 | 18.869 | 24.923 | 14.917 | 0 | 0 | 56.432 | 53.825 | 47.406 | 22.201 | 0 | 0 | 51.899 | 34.438 | [5 empty] | 0 | 3.747 | 39 | 2.2526 | 2.066 | 1.6157 | 1.4634 | 0.60256 | 26.7499
2005-10-31 | 7:20 | 0 | 21.486 | 0 | 1 | 1 | 31.818 | 38.698 | 29.604 | 29.965 | 17.939 | 24.955 | 14.95 | 0 | 0 | 56.439 | 53.811 | 47.413 | 22.209 | 0 | 0 | 51.885 | 34.469 | [5 empty] | 0 | 1.853 | 40 | 2.243 | 2.0568 | 1.6153 | 1.4634 | 0.59343 | 26.4572
2005-10-31 | 7:21 | 0 | 21.461 | 0 | 2 | 0 | 30.977 | 33.904 | 29.506 | 29.7 | 17.542 | 24.955 | 14.95 | 0 | 0 | 56.419 | 53.834 | 47.322 | 22.184 | 0 | 0 | 51.885 | 34.491 | [5 empty] | 0 | 1.277 | 0 | 2.243 | 2.0568 | 1.6153 | 1.4634 | 0.59343 | 26.4572
2005-10-31 | 7:22 | 0 | 21.478 | 0 | 2 | 0 | 30.631 | 32.1 | 29.307 | 29.594 | 17.19 | 24.874 | 14.942 | 0 | 0 | 56.478 | 53.895 | 47.406 | 22.201 | 0 | 0 | 51.832 | 34.579 | [5 empty] | 0 | 1.037 | 1 | 2.2453 | 2.0591 | 1.4286 | 1.2766 | 0.78246 | 34.8489
2005-10-31 | 7:23 | 0 | 21.454 | 0 | 1 | 0 | 30.269 | 31.377 | 29.185 | 29.45 | 17.016 | 24.85 | 14.867 | 0 | 0 | 56.343 | 53.757 | 47.313 | 22.152 | 0 | 0 | 51.855 | 34.459 | [5 empty] | 0 | 0.819 | 2 | 2.2671 | 2.0798 | 1.4295 | 1.2766 | 0.80322 | 35.4289
2005-10-31 | 7:24 | 0 | 21.461 | 1 | 2 | 0 | 30.036 | 30.953 | 29.195 | 29.241 | 16.851 | 24.977 | 14.827 | 0 | 0 | 56.439 | 53.764 | 47.276 | 22.16 | 0 | 0 | 51.862 | 34.445 | [5 empty] | 0 | 0.795 | 3 | 2.2788 | 2.0909 | 1.4299 | 1.2766 | 0.81429 | 35.7337
2005-10-31 | 7:25 | 0 | 21.429 | 0 | 2 | 0 | 29.837 | 30.656 | 29.138 | 29.114 | 16.597 | 24.85 | 14.917 | 0 | 0 | 56.366 | 53.757 | 47.36 | 22.152 | 0 | 0 | 51.808 | 34.483 | [5 empty] | 0 | 0.723 | 4 | 2.2526 | 2.066 | 1.4289 | 1.2766 | 0.78938 | 35.0435
2005-10-31 | 7:26 | 0 | 21.454 | 0 | 2 | 0 | 29.692 | 30.391 | 29.018 | 29.065 | 16.448 | 24.85 | 14.917 | 0 | 0 | 56.343 | 53.771 | 47.374 | 22.167 | 0 | 0 | 51.822 | 34.498 | [5 empty] | 0 | 0.627 | 5 | 2.2526 | 2.066 | 1.4289 | 1.2766 | 0.78938 | 35.0435
2005-10-31 | 7:27 | 0 | 21.436 | 0 | 1 | 0 | 29.555 | 30.131 | 29.001 | 29.047 | 18.877 | 24.882 | 14.9 | 1 | 0 | 56.35 | 53.717 | 47.182 | 22.111 | 0 | 0 | 51.815 | 34.421 | [5 empty] | 0 | 0.508 | 6 | 2.2575 | 2.0707 | 1.4291 | 1.2766 | 0.79408 | 35.1751
2005-10-31 | 7:28 | 1 | 21.468 | 0 | 2 | 0 | 42.111 | 30.018 | 28.79 | 28.935 | 22.841 | 24.818 | 14.882 | 0 | 0 | 56.312 | 53.748 | 47.327 | 22.143 | 0 | 0 | 51.799 | 34.474 | [5 empty] | 21.468 | 13.176 | 7 | 2.2628 | 2.0757 | 1.4293 | 1.2766 | 0.79907 | 35.3138
2005-10-31 | 7:29 | 0 | 21.436 | 0 | 2 | 0 | 41.516 | 30.614 | 28.736 | 28.976 | 20.209 | 24.761 | 14.9 | 0 | 0 | 56.282 | 53.671 | 47.229 | 22.16 | 0 | 0 | 51.792 | 34.443 | [5 empty] | 0 | 12.54 | 8 | 2.2575 | 2.0707 | 1.4291 | 1.2766 | 0.79408 | 35.1751
2005-10-31 | 7:30 | 0 | 21.461 | 0 | 2 | 0 | 33.058 | 43.303 | 28.638 | 28.783 | 18.877 | 24.737 | 14.925 | 1 | 0 | 56.282 | 53.694 | 47.367 | 22.135 | 0 | 0 | 51.769 | 34.491 | [5 empty] | 0 | 4.275 | 9 | 2.2502 | 2.0638 | 1.4288 | 1.2766 | 0.78716 | 34.9813
2005-10-31 | 7:31 | 0 | 21.436 | 0 | 2 | 0 | 30.639 | 38.275 | 28.542 | 28.758 | 18.037 | 24.712 | 14.95 | 0 | 0 | 56.261 | 53.65 | 47.276 | 22.135 | 0 | 0 | 51.815 | 34.467 | [5 empty] | 0 | 1.881 | 10 | 2.243 | 2.0568 | 1.4285 | 1.2766 | 0.78024 | 34.7864
2005-10-31 | 7:32 | 0 | 21.436 | 0 | 2 | 0 | 29.82 | 32.752 | 28.471 | 28.542 | 17.517 | 24.663 | 14.95 | 0 | 0 | 56.216 | 53.65 | 47.182 | 22.135 | 0 | 0 | 51.815 | 34.421 | [5 empty] | 0 | 1.278 | 11 | 2.243 | 2.0568 | 1.4285 | 1.2766 | 0.78024 | 34.7864
2005-10-31 | 7:33 | 0 | 21.493 | 0 | 1 | 0 | 29.442 | 30.886 | 28.503 | 28.479 | 17.082 | 24.84 | 14.983 | 0 | 0 | 56.312 | 53.68 | 47.168 | 22.167 | 0 | 0 | 51.89 | 34.404 | [5 empty] | 0 | 0.963 | 12 | 2.2334 | 2.0477 | 1.4281 | 1.2766 | 0.77111 | 34.527
2005-10-31 | 7:34 | 0 | 21.468 | 0 | 2 | 0 | 29.177 | 30.163 | 28.503 | 28.43 | 16.883 | 24.818 | 15.005 | 0 | 0 | 56.245 | 53.724 | 47.283 | 22.192 | 0 | 0 | 51.869 | 34.428 | [5 empty] | 0 | 0.747 | 13 | 2.2269 | 2.0416 | 1.4278 | 1.2766 | 0.76502 | 34.3529
2005-10-31 | 7:35 | 0 | 21.468 | 1 | 2 | 0 | 29.055 | 29.803 | 28.405 | 28.479 | 16.71 | 24.695 | 15.005 | 0 | 0 | 56.268 | 53.68 | 47.236 | 22.167 | 0 | 0 | 51.869 | 34.452 | [5 empty] | 0 | 0.576 | 14 | 2.2269 | 2.0416 | 1.4278 | 1.2766 | 0.76502 | 34.3529
2005-10-31 | 7:36 | 0 | 21.468 | 0 | 2 | 0 | 28.935 | 29.562 | 28.405 | 28.381 | 16.637 | 24.72 | 14.983 | 0 | 0 | 56.268 | 53.68 | 47.236 | 22.192 | 0 | 0 | 51.799 | 34.452 | [5 empty] | 0 | 0.554 | 15 | 2.2334 | 2.0477 | 1.4281 | 1.2766 | 0.77111 | 34.527
2005-10-31 | 7:37 | 0 | 21.461 | 0 | 2 | 0 | 28.758 | 29.29 | 28.327 | 28.302 | 16.456 | 24.617 | 14.973 | 0 | 0 | 56.216 | 53.603 | 47.091 | 22.135 | 0 | 0 | 51.745 | 34.397 | [5 empty] | 0 | 0.456 | 16 | 2.2363 | 2.0505 | 1.4282 | 1.2766 | 0.77388 | 34.6059
2005-10-31 | 7:38 | 0 | 21.412 | 0 | 2 | 0 | 28.736 | 29.146 | 28.204 | 28.398 | 16.159 | 24.568 | 14.973 | 0 | 0 | 56.17 | 53.626 | 47.182 | 22.231 | 0 | 0 | 51.815 | 34.514 | [5 empty] | 0 | 0.338 | 17 | 2.2363 | 2.0505 | 1.4282 | 1.2766 | 0.77388 | 34.6059
2005-10-31 | 7:39 | 0 | 21.493 | 0 | 2 | 0 | 37.576 | 29.079 | 28.309 | 28.26 | 22.77 | 24.695 | 15.005 | 0 | 0 | 56.2 | 53.633 | 47.098 | 22.167 | 0 | 0 | 51.708 | 34.452 | [5 empty] | 0 | 9.316 | 18 | 2.2269 | 2.0416 | 1.4278 | 1.2766 | 0.76502 | 34.3529
2005-10-31 | 7:40 | 0 | 21.461 | 0 | 2 | 0 | 41.116 | 29.626 | 28.302 | 28.204 | 19.764 | 24.688 | 14.973 | 1 | 0 | 56.193 | 53.58 | 47.045 | 22.135 | 0 | 0 | 51.722 | 34.443 | [5 empty] | 0 | 12.912 | 19 | 2.2363 | 2.0505 | 1.4282 | 1.2766 | 0.77388 | 34.6059
2005-10-31 | 7:41 | 0 | 21.486 | 0 | 2 | 0 | 32.301 | 42.456 | 28.133 | 28.108 | 18.135 | 24.761 | 15.073 | 0 | 0 | 56.17 | 53.603 | 47.045 | 22.111 | 0 | 0 | 51.745 | 34.443 | [5 empty] | 0 | 4.193 | 20 | 2.2071 | 2.0228 | 1.427 | 1.2766 | 0.7462 | 33.8083
2005-10-31 | 7:42 | 0 | 21.468 | 0 | 2 | 0 | 29.827 | 36.519 | 28.165 | 28.094 | 17.328 | 24.673 | 15.005 | 1 | 0 | 56.177 | 53.587 | 47.098 | 22.167 | 0 | 0 | 51.752 | 34.452 | [5 empty] | 0 | 1.733 | 21 | 2.2269 | 2.0416 | 1.4278 | 1.2766 | 0.76502 | 34.3529
2005-10-31 | 7:43 | 0 | 21.468 | 0 | 2 | 0 | 29.055 | 31.512 | 28.236 | 28.02 | 16.883 | 24.624 | 15.005 | 0 | 0 | 56.2 | 53.587 | 47.031 | 22.143 | 0 | 0 | 51.752 | 34.38 | [5 empty] | 0 | 1.035 | 22 | 2.2269 | 2.0416 | 1.4278 | 1.2766 | 0.76502 | 34.3529
2005-10-31 | 7:44 | 0 | 21.436 | 0 | 1 | 0 | 28.758 | 29.891 | 28.062 | 27.988 | 16.504 | 24.519 | 14.973 | 0 | 0 | 56.103 | 53.535 | 47.024 | 22.135 | 0 | 0 | 51.701 | 34.325 | [5 empty] | 0 | 0.77 | 23 | 2.2363 | 2.0505 | 1.4282 | 1.2766 | 0.77388 | 34.6059
2005-10-31 | 7:45 | 0 | 21.468 | 0 | 2 | 0 | 28.623 | 29.393 | 28.069 | 28.045 | 16.192 | 24.649 | 15.005 | 0 | 0 | 56.133 | 53.566 | 47.075 | 22.143 | 0 | 0 | 51.752 | 34.38 | [5 empty] | 0 | 0.578 | 24 | 2.2269 | 2.0416 | 1.4278 | 1.2766 | 0.76502 | 34.3529
2005-10-31 | 7:46 | 0 | 21.461 | 0 | 2 | 0 | 28.41 | 29.038 | 28.05 | 27.905 | 16.071 | 24.531 | 14.985 | 0 | 0 | 56.114 | 53.594 | 46.989 | 22.123 | 0 | 0 | 51.689 | 34.34 | [5 empty] | 0 | 0.505 | 25 | 2.2328 | 2.0472 | 1.4281 | 1.2766 | 0.77056 | 34.5113
2005-10-31 | 7:47 | 0 | 21.471 | 1 | 3 | 0 | 28.385 | 28.891 | 28.047 | 27.951 | 15.948 | 24.627 | 15.033 | 0 | 0 | 56.181 | 53.545 | 47.033 | 22.145 | 0 | 0 | 51.734 | 34.337 | [5 empty] | 0 | 0.434 | 26 | 2.2188 | 2.0339 | 1.4275 | 1.2766 | 0.75727 | 34.1299
2005-10-31 | 7:48 | 0 | 21.495 | 0 | 2 | 0 | 28.361 | 28.795 | 27.976 | 28.047 | 15.973 | 24.627 | 15.008 | 0 | 0 | 56.159 | 53.568 | 47.15 | 22.17 | 0 | 0 | 51.713 | 34.361 | [5 empty] | 0 | 0.314 | 27 | 2.2261 | 2.0408 | 1.4278 | 1.2766 | 0.76419 | 34.3291
2005-10-31 | 7:49 | 0 | 21.471 | 0 | 2 | 0 | 28.265 | 28.65 | 28.072 | 27.902 | 15.847 | 24.747 | 15.058 | 0 | 0 | 56.159 | 53.591 | 47.056 | 22.265 | 0 | 0 | 51.713 | 34.385 | [5 empty] | 0 | 0.363 | 28 | 2.2115 | 2.0269 | 1.4272 | 1.2766 | 0.75035 | 33.9293
2005-10-31 | 7:50 | 0 | 21.471 | 0 | 2 | 0 | 33.28 | 28.577 | 27.927 | 28.023 | 22.653 | 24.506 | 15.008 | 0 | 0 | 56.068 | 53.524 | 47.012 | 22.17 | 0 | 0 | 51.689 | 34.337 | [5 empty] | 0 | 5.257 | 29 | 2.2261 | 2.0408 | 1.4278 | 1.2766 | 0.76419 | 34.3291
2005-10-31 | 7:51 | 0 | 21.414 | 0 | 2 | 0 | 45.558 | 29.003 | 27.846 | 27.824 | 22.523 | 24.546 | 14.952 | 1 | 0 | 56.037 | 53.493 | 47.049 | 22.089 | 0 | 0 | 51.636 | 34.282 | [5 empty] | 0 | 17.734 | 30 | 2.2424 | 2.0563 | 1.4285 | 1.2766 | 0.77969 | 34.7707
2005-10-31 | 7:52 | 1 | 21.495 | 0 | 2 | 0 | 46.666 | 42.279 | 27.878 | 27.831 | 23.783 | 24.577 | 14.96 | 1 | 0 | 56.068 | 53.5 | 47.103 | 22.17 | 0 | 0 | 51.666 | 34.29 | [5 empty] | 21.495 | 18.835 | 31 | 2.24 | 2.0541 | 1.4284 | 1.2766 | 0.77748 | 34.708
2005-10-31 | 7:53 | 0 | 21.495 | 0 | 2 | 0 | 46.391 | 46.116 | 28.023 | 27.856 | 23.518 | 24.676 | 15.033 | 2 | 0 | 56.068 | 53.5 | 46.942 | 22.17 | 0 | 0 | 51.713 | 34.314 | [5 empty] | 0 | 18.535 | 32 | 2.2188 | 2.0339 | 1.4275 | 1.2766 | 0.75727 | 34.1299
2005-10-31 | 7:54 | 0 | 21.463 | 0 | 2 | 0 | 46.109 | 46.407 | 27.944 | 27.775 | 23.56 | 24.57 | 14.927 | 1 | 0 | 56.014 | 53.47 | 46.935 | 22.113 | 0 | 0 | 51.659 | 34.306 | [5 empty] | 0 | 18.334 | 33 | 2.2497 | 2.0632 | 1.4288 | 1.2766 | 0.78661 | 34.9658
2005-10-31 | 7:55 | 0 | 21.463 | 0 | 2 | 0 | 46.223 | 46.246 | 28.015 | 27.775 | 23.582 | 24.524 | 14.952 | 1 | 0 | 56.084 | 53.447 | 46.888 | 22.113 | 0 | 0 | 51.659 | 34.306 | [5 empty] | 0 | 18.448 | 34 | 2.2424 | 2.0563 | 1.4285 | 1.2766 | 0.77969 | 34.7707
2005-10-31 | 7:56 | 0 | 21.488 | 0 | 3 | 0 | 46.018 | 46.407 | 28.184 | 27.799 | 23.849 | 24.546 | 14.975 | 1 | 0 | 56.107 | 53.47 | 46.912 | 22.138 | 0 | 0 | 51.659 | 34.306 | [5 empty] | 0 | 18.219 | 35 | 2.2357 | 2.0499 | 1.4282 | 1.2766 | 0.77332 | 34.5901
2005-10-31 | 7:57 | 0 | 21.495 | 1 | 2 | 0 | 45.978 | 46.277 | 28.265 | 27.902 | 24.266 | 24.676 | 15.008 | 2 | 0 | 56.138 | 53.568 | 46.942 | 22.145 | 0 | 0 | 51.689 | 34.337 | [5 empty] | 0 | 18.076 | 36 | 2.2261 | 2.0408 | 1.4278 | 1.2766 | 0.76419 | 34.3291
2005-10-31 | 7:58 | 1 | 21.471 | 0 | 2 | 0 | 46.209 | 46.347 | 28.192 | 27.976 | 24.457 | 24.555 | 14.985 | 1 | 0 | 56.091 | 53.454 | 47.012 | 22.145 | 0 | 0 | 51.666 | 34.337 | [5 empty] | 21.471 | 18.233 | 37 | 2.2328 | 2.0472 | 1.4281 | 1.2766 | 0.77056 | 34.5113
2005-10-31 | 7:59 | 0 | 21.471 | 0 | 2 | 0 | 46.162 | 46.438 | 28.312 | 28.072 | 24.651 | 24.577 | 14.985 | 1 | 0 | 56.138 | 53.454 | 47.012 | 22.145 | 0 | 0 | 51.643 | 34.361 | [5 empty] | 0 | 18.09 | 38 | 2.2328 | 2.0472 | 1.4281 | 1.2766 | 0.77056 | 34.5113
2005-10-31 | 8:00 | 0 | 21.446 | 0 | 2 | 0 | 46.552 | 46.391 | 28.481 | 28.072 | 25.085 | 24.651 | 15.008 | 1 | 0 | 56.138 | 53.477 | 47.033 | 22.121 | 0 | 0 | 51.575 | 34.337 | [5 empty] | 0 | 18.48 | 39 | 2.2261 | 2.0408 | 1.4278 | 1.2766 | 0.76419 | 34.3291
2005-10-31 | 8:01 | 0 | 21.463 | 0 | 2 | 0 | 46.958 | 46.498 | 28.498 | 28.305 | 25.269 | 24.668 | 15 | 1 | 0 | 56.128 | 53.493 | 46.935 | 22.113 | 0 | 0 | 51.566 | 34.306 | [5 empty] | 0 | 18.653 | 40 | 2.2284 | 2.043 | 1.4279 | 1.2766 | 0.7664 | 34.3926
2005-10-31 | 8:02 | 0 | 21.488 | 0 | 2 | 0 | 46.958 | 47.096 | 28.594 | 28.305 | 25.438 | 24.739 | 15 | 2 | 0 | 56.152 | 53.423 | 46.935 | 22.138 | 0 | 0 | 51.566 | 34.282 | [5 empty] | 0 | 18.653 | 41 | 2.2284 | 2.043 | 1.4279 | 1.2766 | 0.7664 | 34.3926
2005-10-31 | 8:03 | 0 | 21.463 | 0 | 2 | 0 | 47.003 | 47.234 | 28.665 | 28.305 | 25.774 | 24.788 | 15 | 1 | 0 | 56.175 | 53.47 | 47.049 | 22.113 | 0 | 0 | 51.545 | 34.282 | [5 empty] | 0 | 18.698 | 42 | 2.2284 | 2.043 | 1.4279 | 1.2766 | 0.7664 | 34.3926
2005-10-31 | 8:04 | 1 | 21.439 | 0 | 2 | 0 | 47.073 | 47.255 | 28.739 | 28.449 | 25.968 | 24.813 | 15 | 1 | 0 | 56.197 | 53.47 | 47.003 | 22.113 | 0 | 0 | 51.589 | 34.33 | [5 empty] | 21.439 | 18.624 | 43 | 2.2284 | 2.043 | 1.4279 | 1.2766 | 0.7664 | 34.3926
2005-10-31 | 8:05 | 0 | 21.463 | 0 | 2 | 0 | 47.875 | 47.371 | 29.003 | 28.498 | 26.184 | 24.933 | 15.05 | 1 | 0 | 56.243 | 53.493 | 47.119 | 22.209 | 0 | 0 | 51.636 | 34.376 | [5 empty] | 0 | 19.377 | 44 | 2.2138 | 2.0292 | 1.4273 | 1.2766 | 0.75256 | 33.9936
2005-10-31 | 8:06 | 0 | 21.463 | 1 | 2 | 0 | 47.691 | 47.7 | 29.16 | 28.677 | 26.414 | 24.992 | 15.088 | 2 | 0 | 56.229 | 53.479 | 47.038 | 22.125 | 0 | 0 | 51.645 | 34.34 | [5 empty] | 0 | 19.014 | 45 | 2.2028 | 2.0186 | 1.4269 | 1.2766 | 0.74205 | 33.6869
2005-10-31 | 8:07 | 0 | 21.461 | 0 | 2 | 1 | 47.572 | 48.123 | 29.531 | 28.976 | 26.399 | 24.928 | 15.121 | 1 | 0 | 56.238 | 53.465 | 46.93 | 22.135 | 0 | 0 | 51.678 | 34.304 | [5 empty] | 0 | 18.596 | 46 | 2.1932 | 2.0095 | 1.4265 | 1.2766 | 0.73291 | 33.418
2005-10-31 | 8:08 | 0 | 21.461 | 0 | 2 | 0 | 47.619 | 47.917 | 30.011 | 29.312 | 26.591 | 24.977 | 15.121 | 1 | 0 | 56.238 | 53.419 | 46.954 | 22.135 | 0 | 0 | 51.631 | 34.28 | [5 empty] | 0 | 18.307 | 0 | 2.1932 | 2.0095 | 1.4265 | 1.2766 | 0.73291 | 33.418
2005-10-31 | 8:09 | 1 | 21.436 | 0 | 2 | 0 | 47.871 | 47.894 | 30.494 | 29.7 | 26.689 | 25.026 | 15.146 | 1 | 0 | 56.238 | 53.442 | 47 | 22.135 | 0 | 0 | 51.608 | 34.304 | [5 empty] | 21.436 | 18.171 | 1 | 2.1859 | 2.0026 | 1.3741 | 1.2245 | 0.7781 | 35.5965
2005-10-31 | 8:10 | 0 | 21.461 | 0 | 2 | 0 | 48.331 | 48.055 | 31.144 | 30.156 | 26.855 | 25.217 | 15.171 | 1 | 0 | 56.261 | 53.442 | 46.93 | 22.111 | 0 | 0 | 51.608 | 34.256 | [5 empty] | 0 | 18.175 | 2 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:11 | 0 | 21.461 | 0 | 2 | 0 | 48.72 | 48.331 | 31.504 | 30.639 | 27.049 | 25.097 | 15.196 | 2 | 0 | 56.261 | 53.465 | 46.977 | 22.111 | 0 | 0 | 51.631 | 34.28 | [5 empty] | 0 | 18.081 | 3 | 2.1713 | 1.9887 | 1.3735 | 1.2245 | 0.76426 | 35.1977
2005-10-31 | 8:12 | 0 | 21.436 | 0 | 2 | 0 | 49.339 | 48.741 | 31.914 | 31.168 | 27.218 | 25.122 | 15.171 | 1 | 0 | 56.261 | 53.442 | 46.954 | 22.135 | 0 | 0 | 51.631 | 34.28 | [5 empty] | 0 | 18.171 | 4 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:13 | 0 | 21.461 | 0 | 2 | 0 | 49.178 | 49.225 | 32.372 | 31.649 | 25.411 | 25.316 | 15.171 | 1 | 0 | 56.261 | 53.465 | 47.024 | 22.16 | 0 | 0 | 51.631 | 34.373 | [5 empty] | 0 | 17.529 | 5 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:14 | 0 | 21.461 | 0 | 1 | 0 | 39.026 | 49.82 | 32.517 | 32.034 | 23.17 | 25.195 | 15.171 | 0 | 0 | 56.282 | 53.465 | 47.024 | 22.135 | 0 | 0 | 51.608 | 34.325 | [5 empty] | 0 | 6.992 | 6 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:15 | 0 | 21.493 | 0 | 2 | 0 | 35.273 | 45.815 | 32.689 | 32.429 | 21.758 | 25.249 | 15.179 | 1 | 0 | 56.312 | 53.472 | 47.075 | 22.167 | 0 | 0 | 51.638 | 34.357 | [5 empty] | 0 | 2.844 | 7 | 2.1763 | 1.9935 | 1.3737 | 1.2245 | 0.76896 | 35.3339
2005-10-31 | 8:16 | 0 | 21.493 | 1 | 2 | 0 | 34.263 | 38.468 | 32.854 | 32.524 | 20.291 | 25.274 | 15.204 | 0 | 0 | 56.312 | 53.496 | 47.168 | 22.143 | 0 | 0 | 51.615 | 34.335 | [5 empty] | 0 | 1.739 | 8 | 2.169 | 1.9865 | 1.3734 | 1.2245 | 0.76204 | 35.1335
2005-10-31 | 8:17 | 0 | 21.493 | 0 | 2 | 0 | 33.912 | 35.72 | 33.041 | 32.737 | 19.453 | 25.274 | 15.179 | 0 | 0 | 56.334 | 53.519 | 47.145 | 22.167 | 0 | 0 | 51.615 | 34.357 | [5 empty] | 0 | 1.175 | 9 | 2.1763 | 1.9935 | 1.3737 | 1.2245 | 0.76896 | 35.3339
2005-10-31 | 8:18 | 0 | 21.461 | 0 | 2 | 0 | 33.763 | 34.797 | 32.986 | 32.845 | 18.877 | 25.291 | 15.121 | 0 | 0 | 56.282 | 53.419 | 47.068 | 22.111 | 0 | 0 | 51.608 | 34.304 | [5 empty] | 0 | 0.918 | 10 | 2.1932 | 2.0095 | 1.3744 | 1.2245 | 0.78502 | 35.7938
2005-10-31 | 8:19 | 0 | 21.461 | 0 | 2 | 0 | 33.716 | 34.421 | 33.058 | 33.034 | 18.432 | 25.217 | 15.121 | 0 | 0 | 56.261 | 53.442 | 47.068 | 22.135 | 0 | 0 | 51.563 | 34.304 | [5 empty] | 0 | 0.682 | 11 | 2.1932 | 2.0095 | 1.3744 | 1.2245 | 0.78502 | 35.7938
2005-10-31 | 8:20 | 0 | 21.436 | 0 | 1 | 0 | 33.574 | 34.184 | 32.964 | 32.964 | 18.309 | 25.316 | 15.146 | 0 | 0 | 56.261 | 53.442 | 47.091 | 22.086 | 0 | 0 | 51.493 | 34.28 | [5 empty] | 0 | 0.61 | 12 | 2.1859 | 2.0026 | 1.3741 | 1.2245 | 0.7781 | 35.5965
2005-10-31 | 8:21 | 0 | 21.461 | 0 | 2 | 0 | 33.574 | 34.067 | 32.775 | 33.034 | 18.012 | 25.217 | 15.146 | 0 | 0 | 56.261 | 53.419 | 47.068 | 22.111 | 0 | 0 | 51.563 | 34.304 | [5 empty] | 0 | 0.54 | 13 | 2.1859 | 2.0026 | 1.3741 | 1.2245 | 0.7781 | 35.5965
2005-10-31 | 8:22 | 0 | 21.461 | 0 | 2 | 0 | 33.55 | 33.95 | 32.752 | 32.94 | 17.962 | 25.338 | 15.171 | 1 | 0 | 56.238 | 53.419 | 47.068 | 22.111 | 0 | 0 | 51.608 | 34.28 | [5 empty] | 0 | 0.61 | 14 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:23 | 0 | 21.436 | 0 | 2 | 0 | 34.349 | 33.926 | 32.397 | 32.893 | 26.88 | 25.266 | 15.171 | 0 | 0 | 56.193 | 53.398 | 47.068 | 22.111 | 0 | 0 | 51.584 | 34.28 | [5 empty] | 0 | 1.456 | 15 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:24 | 0 | 21.436 | 0 | 2 | 0 | 48.811 | 33.881 | 32.108 | 32.586 | 22.594 | 25.362 | 15.269 | 0 | 0 | 56.238 | 53.398 | 47 | 22.135 | 0 | 0 | 51.584 | 34.325 | [5 empty] | 0 | 16.225 | 16 | 2.1501 | 1.9685 | 1.3726 | 1.2245 | 0.74405 | 34.6059
2005-10-31 | 8:25 | 0 | 21.461 | 0 | 1 | 0 | 39.098 | 40.083 | 31.747 | 32.397 | 20.475 | 25.195 | 15.294 | 0 | 0 | 56.147 | 53.374 | 47.091 | 22.135 | 0 | 0 | 51.54 | 34.325 | [5 empty] | 0 | 6.701 | 17 | 2.1428 | 1.9616 | 1.3723 | 1.2245 | 0.73713 | 34.4006
2005-10-31 | 8:26 | 0 | 21.461 | 0 | 2 | 0 | 34.914 | 45.231 | 31.48 | 32.034 | 19.344 | 25.217 | 15.37 | 0 | 0 | 56.121 | 53.37 | 47.089 | 22.111 | 0 | 0 | 51.514 | 34.302 | [5 empty] | 0 | 2.88 | 18 | 2.1207 | 1.9406 | 1.3714 | 1.2245 | 0.71609 | 33.7676
2005-10-31 | 8:27 | 0 | 21.402 | 0 | 2 | 0 | 33.562 | 38.263 | 31.325 | 31.808 | 18.57 | 25.183 | 15.407 | 1 | 0 | 56.089 | 53.339 | 47.033 | 22.101 | 0 | 0 | 51.549 | 34.244 | [5 empty] | 0 | 1.754 | 19 | 2.1099 | 1.9303 | 1.371 | 1.2245 | 0.70585 | 33.4546
2005-10-31 | 8:28 | 0 | 21.427 | 1 | 2 | 0 | 32.952 | 35.115 | 31.156 | 31.566 | 18.273 | 25.112 | 15.458 | 0 | 0 | 56.089 | 53.316 | 46.965 | 22.076 | 0 | 0 | 51.573 | 34.223 | [5 empty] | 0 | 1.386 | 20 | 2.095 | 1.9162 | 1.3704 | 1.2245 | 0.69174 | 33.0179
2005-10-31 | 8:29 | 0 | 21.402 | 0 | 1 | 0 | 32.483 | 33.94 | 30.869 | 31.23 | 18.05 | 25.161 | 15.483 | 0 | 0 | 56.044 | 53.316 | 46.942 | 22.101 | 0 | 0 | 51.505 | 34.244 | [5 empty] | 0 | 1.253 | 21 | 2.0878 | 1.9093 | 1.3701 | 1.2245 | 0.68482 | 32.8016
2005-10-31 | 8:30 | 0 | 21.427 | 0 | 2 | 0 | 32.144 | 33.259 | 30.725 | 30.965 | 17.977 | 25.183 | 15.533 | 0 | 0 | 56.089 | 53.339 | 46.895 | 22.101 | 0 | 0 | 51.505 | 34.223 | [5 empty] | 0 | 1.179 | 22 | 2.0732 | 1.8955 | 1.3695 | 1.2245 | 0.67098 | 32.3644
2005-10-31 | 8:31 | 0 | 21.432 | 0 | 2 | 0 | 31.838 | 32.912 | 30.465 | 30.899 | 17.66 | 25.117 | 15.513 | 0 | 0 | 56.072 | 53.321 | 47.017 | 22.106 | 0 | 0 | 51.533 | 34.227 | [5 empty] | 0 | 0.939 | 23 | 2.079 | 1.901 | 1.3697 | 1.2245 | 0.67651 | 32.54
2005-10-31 | 8:32 | 0 | 21.427 | 0 | 1 | 0 | 31.495 | 32.483 | 30.435 | 30.602 | 17.358 | 25.038 | 15.483 | 0 | 0 | 55.998 | 53.316 | 46.942 | 22.125 | 0 | 0 | 51.505 | 34.223 | [5 empty] | 0 | 0.893 | 24 | 2.0878 | 1.9093 | 1.3701 | 1.2245 | 0.68482 | 32.8016
2005-10-31 | 8:33 | 0 | 21.427 | 0 | 2 | 0 | 31.23 | 32.193 | 30.266 | 30.411 | 17.162 | 25.016 | 15.533 | 0 | 0 | 56.021 | 53.316 | 46.851 | 22.15 | 0 | 0 | 51.458 | 34.223 | [5 empty] | 0 | 0.819 | 25 | 2.0732 | 1.8955 | 1.3695 | 1.2245 | 0.67098 | 32.3644
2005-10-31 | 8:34 | 0 | 21.427 | 0 | 2 | 0 | 31.061 | 31.808 | 30.072 | 30.46 | 27.159 | 24.967 | 15.458 | 0 | 0 | 55.974 | 53.269 | 46.851 | 22.125 | 0 | 0 | 51.411 | 34.199 | [5 empty] | 0 | 0.601 | 26 | 2.095 | 1.9162 | 1.3704 | 1.2245 | 0.69174 | 33.0179
2005-10-31 | 8:35 | 1 | 21.427 | 0 | 2 | 0 | 47.423 | 31.544 | 30.001 | 30.362 | 22.606 | 24.943 | 15.508 | 0 | 0 | 55.951 | 53.269 | 46.895 | 22.125 | 0 | 0 | 51.411 | 34.199 | [5 empty] | 21.427 | 17.061 | 27 | 2.0805 | 1.9024 | 1.3698 | 1.2245 | 0.6779 | 32.5838
2005-10-31 | 8:36 | 0 | 21.427 | 0 | 2 | 0 | 38.169 | 35.514 | 29.808 | 30.05 | 20.321 | 24.967 | 15.483 | 1 | 0 | 55.974 | 53.293 | 46.804 | 22.125 | 0 | 0 | 51.39 | 34.199 | [5 empty] | 0 | 8.119 | 28 | 2.0878 | 1.9093 | 1.3701 | 1.2245 | 0.68482 | 32.8016
2005-10-31 | 8:37 | 0 | 21.427 | 0 | 1 | 0 | 33 | 44.066 | 29.663 | 29.928 | 18.816 | 24.943 | 15.508 | 0 | 0 | 55.93 | 53.246 | 46.828 | 22.125 | 0 | 0 | 51.39 | 34.175 | [5 empty] | 0 | 3.072 | 29 | 2.0805 | 1.9024 | 1.3698 | 1.2245 | 0.6779 | 32.5838
2005-10-31 | 8:38 | 0 | 21.402 | 0 | 2 | 0 | 31.374 | 36.899 | 29.447 | 29.736 | 18.248 | 24.992 | 15.483 | 0 | 0 | 55.883 | 53.223 | 46.828 | 22.076 | 0 | 0 | 51.435 | 34.127 | [5 empty] | 0 | 1.638 | 30 | 2.0878 | 1.9093 | 1.3701 | 1.2245 | 0.68482 | 32.8016
2005-10-31 | 8:39 | 0 | 21.427 | 0 | 2 | 0 | 30.771 | 33.024 | 29.447 | 29.518 | 17.854 | 24.943 | 15.458 | 0 | 0 | 55.907 | 53.223 | 46.781 | 22.101 | 0 | 0 | 51.39 | 34.175 | [5 empty] | 0 | 1.253 | 31 | 2.095 | 1.9162 | 1.3704 | 1.2245 | 0.69174 | 33.0179
2005-10-31 | 8:40 | 0 | 21.451 | 1 | 2 | 0 | 30.386 | 31.784 | 29.352 | 29.352 | 17.607 | 25.016 | 15.458 | 0 | 0 | 55.951 | 53.223 | 46.757 | 22.101 | 0 | 0 | 51.39 | 34.175 | [5 empty] | 0 | 1.034 | 32 | 2.095 | 1.9162 | 1.3704 | 1.2245 | 0.69174 | 33.0179
2005-10-31 | 8:41 | 0 | 21.451 | 0 | 1 | 0 | 30.17 | 31.134 | 29.207 | 29.231 | 17.336 | 24.943 | 15.385 | 1 | 0 | 55.86 | 53.223 | 46.804 | 22.101 | 0 | 0 | 51.367 | 34.175 | [5 empty] | 0 | 0.939 | 33 | 2.1163 | 1.9364 | 1.3712 | 1.2245 | 0.71194 | 33.6411
2005-10-31 | 8:42 | 0 | 21.451 | 0 | 2 | 0 | 29.906 | 30.796 | 29.087 | 29.133 | 17.235 | 24.847 | 15.407 | 0 | 0 | 55.883 | 53.223 | 46.781 | 22.101 | 0 | 0 | 51.32 | 34.127 | [5 empty] | 0 | 0.773 | 34 | 2.1099 | 1.9303 | 1.371 | 1.2245 | 0.70585 | 33.4546
2005-10-31 | 8:43 | 0 | 21.427 | 0 | 2 | 0 | 29.712 | 30.482 | 28.989 | 29.109 | 16.939 | 24.967 | 15.433 | 0 | 0 | 55.907 | 53.202 | 46.69 | 22.101 | 0 | 0 | 51.367 | 34.103 | [5 empty] | 0 | 0.603 | 35 | 2.1023 | 1.9231 | 1.3707 | 1.2245 | 0.69866 | 33.2328
2005-10-31 | 8:44 | 0 | 21.427 | 0 | 2 | 0 | 29.641 | 30.217 | 28.893 | 29.109 | 16.939 | 24.752 | 15.385 | 0 | 0 | 55.86 | 53.223 | 46.757 | 22.101 | 0 | 0 | 51.344 | 34.175 | [5 empty] | 0 | 0.532 | 36 | 2.1163 | 1.9364 | 1.3712 | 1.2245 | 0.71194 | 33.6411
2005-10-31 | 8:45 | 0 | 21.402 | 0 | 2 | 0 | 29.496 | 30.05 | 28.893 | 28.942 | 23.763 | 24.798 | 15.284 | 0 | 0 | 55.837 | 53.178 | 46.69 | 22.101 | 0 | 0 | 51.367 | 34.199 | [5 empty] | 0 | 0.554 | 37 | 2.1457 | 1.9644 | 1.3724 | 1.2245 | 0.7399 | 34.4829
2005-10-31 | 8:46 | 0 | 21.451 | 0 | 2 | 0 | 44.3 | 29.881 | 28.942 | 28.991 | 23.908 | 24.703 | 15.284 | 0 | 0 | 55.841 | 53.181 | 46.806 | 22.101 | 0 | 0 | 51.346 | 34.199 | [5 empty] | 0 | 15.309 | 38 | 2.1457 | 1.9644 | 1.3724 | 1.2245 | 0.7399 | 34.4829
2005-10-31 | 8:47 | 0 | 21.461 | 0 | 2 | 0 | 46.449 | 36.839 | 28.881 | 28.927 | 24.183 | 24.737 | 15.269 | 1 | 0 | 55.804 | 53.167 | 46.725 | 22.086 | 0 | 0 | 51.379 | 34.208 | [5 empty] | 0 | 17.522 | 39 | 2.1501 | 1.9685 | 1.3726 | 1.2245 | 0.74405 | 34.6059
2005-10-31 | 8:48 | 0 | 21.436 | 0 | 2 | 0 | 46.426 | 45.647 | 28.856 | 28.952 | 23.7 | 24.808 | 15.221 | 1 | 0 | 55.827 | 53.146 | 46.655 | 22.086 | 0 | 0 | 51.355 | 34.163 | [5 empty] | 0 | 17.474 | 40 | 2.164 | 1.9818 | 1.3732 | 1.2245 | 0.75734 | 34.9964
2005-10-31 | 8:49 | 0 | 21.436 | 0 | 2 | 0 | 46.06 | 46.517 | 28.736 | 28.832 | 23.893 | 24.786 | 15.171 | 1 | 0 | 55.781 | 53.146 | 46.748 | 22.086 | 0 | 0 | 51.332 | 34.163 | [5 empty] | 0 | 17.228 | 41 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:50 | 1 | 21.436 | 1 | 2 | 0 | 45.945 | 46.221 | 28.881 | 28.712 | 23.989 | 24.882 | 15.269 | 2 | 0 | 55.804 | 53.146 | 46.634 | 22.111 | 0 | 0 | 53.808 | 31.529 | [5 empty] | 21.436 | 17.233 | 42 | 2.1501 | 1.9685 | 1.3726 | 1.2245 | 0.74405 | 34.6059
2005-10-31 | 8:51 | 0 | 21.436 | 0 | 2 | 0 | 46.265 | 46.083 | 28.903 | 28.736 | 24.158 | 24.808 | 15.244 | 1 | 0 | 55.757 | 53.052 | 46.587 | 22.111 | 2 | 0 | 57.247 | 23.148 | [5 empty] | 0 | 17.529 | 43 | 2.1573 | 1.9755 | 1.3729 | 1.2245 | 0.75097 | 34.8099
2005-10-31 | 8:52 | 0 | 21.436 | 0 | 2 | 0 | 46.93 | 46.244 | 28.856 | 28.736 | 24.278 | 24.928 | 15.221 | 1 | 0 | 55.804 | 52.961 | 45.922 | 22.086 | 0 | 0 | 57.717 | 22.086 | [5 empty] | 0 | 18.194 | 44 | 2.164 | 1.9818 | 1.3732 | 1.2245 | 0.75734 | 34.9964
2005-10-31 | 8:53 | 0 | 21.461 | 0 | 2 | 0 | 47.252 | 46.816 | 28.952 | 28.856 | 24.543 | 24.857 | 15.171 | 1 | 0 | 55.757 | 52.915 | 45.28 | 22.111 | 0 | 0 | 57.74 | 22.184 | [5 empty] | 0 | 18.396 | 45 | 2.1786 | 1.9957 | 1.3738 | 1.2245 | 0.77118 | 35.3978
2005-10-31 | 8:54 | 0 | 21.436 | 0 | 2 | 0 | 47.458 | 47.229 | 29.097 | 28.783 | 24.712 | 24.977 | 15.244 | 1 | 0 | 55.827 | 52.915 | 44.662 | 22.086 | 0 | 0 | 57.628 | 22.496 | [5 empty] | 0 | 18.675 | 46 | 2.1573 | 1.9755 | 1.3729 | 1.2245 | 0.75097 | 34.8099
2005-10-31 | 8:55 | 1 | 21.468 | 0 | 2 | 0 | 47.901 | 47.558 | 29.199 | 28.864 | 25.034 | 24.913 | 15.302 | 2 | 0 | 55.858 | 52.922 | 44.391 | 22.143 | 0 | 0 | 57.523 | 22.937 | [5 empty] | 21.468 | 19.037 | 47 | 2.1405 | 1.9594 | 1.3722 | 1.2245 | 0.73492 | 34.3346
2005-10-31 | 8:56 | 0 | 21.493 | 0 | 2 | 1 | 48.244 | 47.833 | 29.464 | 29.033 | 25.227 | 25.009 | 15.254 | 1 | 0 | 55.881 | 52.922 | 43.992 | 22.143 | 0 | 0 | 57.455 | 23.322 | [5 empty] | 0 | 19.211 | 48 | 2.1544 | 1.9727 | 1.3728 | 1.2245 | 0.7482 | 34.7285
2005-10-31 | 8:57 | 0 | 21.436 | 0 | 2 | 0 | 48.697 | 48.214 | 29.432 | 29.192 | 25.507 | 24.882 | 15.319 | 1 | 0 | 55.827 | 52.891 | 43.819 | 22.135 | 0 | 0 | 57.313 | 23.604 | [5 empty] | 0 | 19.505 | 0 | 2.1355 | 1.9547 | 1.372 | 1.2245 | 0.73021 | 34.1938
2005-10-31 | 8:58 | 0 | 21.486 | 0 | 2 | 0 | 49.087 | 48.559 | 29.675 | 29.168 | 25.627 | 25.026 | 15.418 | 2 | 0 | 55.895 | 52.891 | 43.561 | 22.086 | 0 | 0 | 57.247 | 23.918 | [5 empty] | 0 | 19.919 | 1 | 2.1067 | 1.9273 | 4.1464 | 4 | -2.0727 | -98.3872
2005-10-31 | 8:59 | 0 | 21.412 | 0 | 2 | 0 | 49.155 | 49.11 | 29.675 | 29.241 | 25.965 | 24.906 | 15.443 | 1 | 0 | 55.874 | 52.915 | 43.492 | 22.135 | 0 | 0 | 57.179 | 24.183 | [5 empty] | 0 | 19.914 | 2 | 2.0994 | 1.9204 | 4.1461 | 4 | -2.0796 | -99.058
2005-10-31 | 9:00 | 0 | 21.436 | 1 | 1 | 0 | 49.246 | 49.362 | 29.722 | 29.386 | 26.279 | 25.051 | 15.468 | 1 | 0 | 55.918 | 52.891 | 43.396 | 22.111 | 0 | 0 | 57.156 | 24.398 | [5 empty] | 0 | 19.86 | 3 | 2.0921 | 1.9135 | 4.1458 | 4 | -2.0865 | -99.7335
2005-10-31 | 9:01 | 1 | 21.468 | 0 | 2 | 0 | 49.666 | 49.46 | 30.018 | 29.587 | 26.743 | 25.083 | 15.475 | 1 | 0 | 55.925 | 52.901 | 43.358 | 22.167 | 0 | 0 | 57.097 | 24.744 | [5 empty] | 21.468 | 20.079 | 4 | 2.0901 | 1.9115 | 4.1457 | 4 | -2.0885 | -99.9234
2005-10-31 | 9:02 | 0 | 21.436 | 0 | 2 | 0 | 49.981 | 49.591 | 30.085 | 29.602 | 26.904 | 25.097 | 15.418 | 2 | 0 | 55.874 | 52.87 | 43.303 | 22.135 | 0 | 0 | 56.978 | 24.977 | [5 empty] | 0 | 20.379 | 5 | 2.1067 | 1.9273 | 4.1464 | 4 | -2.0727 | -98.3872
2005-10-31 | 9:03 | 0 | 21.436 | 0 | 2 | 0 | 50.072 | 49.957 | 30.325 | 29.746 | 27.025 | 25.097 | 15.392 | 1 | 0 | 55.895 | 52.891 | 43.303 | 22.135 | 0 | 0 | 56.866 | 25.266 | [5 empty] | 0 | 20.326 | 6 | 2.1142 | 1.9345 | 4.1467 | 4 | -2.0655 | -97.6945
2005-10-31 | 9:04 | 0 | 21.461 | 0 | 2 | 0 | 50.004 | 50.233 | 30.639 | 30.011 | 25.916 | 25.217 | 15.37 | 1 | 0 | 55.942 | 52.87 | 43.327 | 22.111 | 0 | 0 | 56.798 | 25.482 | [5 empty] | 0 | 19.993 | 7 | 2.1207 | 1.9406 | 4.1469 | 4 | -2.0594 | -97.1122
2005-10-31 | 9:05 | 0 | 21.436 | 0 | 1 | 0 | 39.614 | 50.3 | 30.95 | 30.374 | 23.17 | 25.266 | 15.345 | 0 | 0 | 55.918 | 52.847 | 43.327 | 22.111 | 0 | 0 | 56.754 | 25.7 | [5 empty] | 0 | 9.24 | 8 | 2.1279 | 1.9475 | 4.1472 | 4 | -2.0525 | -96.4548
2005-10-31 | 9:06 | 0 | 21.493 | 0 | 6 | 0 | 34.945 | 48.13 | 31.343 | 33.44 | 30.043 | 25.443 | 15.352 | 1 | 0 | 47.808 | 52.919 | 47.005 | 22.167 | 0 | 0 | 56.736 | 25.948 | [5 empty] | 0 | 1.505 | 9 | 2.1259 | 1.9456 | 4.1471 | 4 | -2.0544 | -96.6384
2005-10-31 | 9:07 | 1 | 21.476 | 0 | 15 | 0 | 53.706 | 44.764 | 33.916 | 45.773 | 48.044 | 25.521 | 15.262 | 1 | 0 | 55.013 | 52.56 | 48.296 | 22.125 | 0 | 0 | 56.652 | 25.183 | [5 empty] | 21.476 | 7.933 | 10 | 2.1521 | 1.9705 | 4.1482 | 4 | -2.0295 | -94.304
2005-10-31 | 9:08 | 1 | 21.451 | 1 | 15 | 0 | 63.555 | 43.879 | 37.347 | 54.439 | 55.678 | 25.448 | 15.262 | 2 | 0 | 62.188 | 52.147 | 55.104 | 22.101 | 0 | 0 | 56.583 | 25.811 | [5 empty] | 21.451 | 9.116 | 11 | 2.1521 | 1.9705 | 4.1482 | 4 | -2.0295 | -94.304
2005-10-31 | 9:09 | 0 | 21.451 | 0 | 15 | 0 | 68.007 | 43.48 | 40.777 | 59.454 | 56.382 | 25.448 | 15.262 | 1 | 0 | 66.514 | 52.147 | 59.497 | 22.15 | 0 | 0 | 56.494 | 30.845 | [5 empty] | 0 | 8.553 | 12 | 2.1521 | 1.9705 | 4.1482 | 4 | -2.0295 | -94.304
2005-10-31 | 9:10 | 1 | 21.476 | 0 | 15 | 0 | 69.588 | 43.339 | 43.362 | 61.74 | 56.27 | 25.571 | 15.262 | 1 | 0 | 68.577 | 52.49 | 61.606 | 22.15 | 0 | 0 | 56.494 | 34.974 | [5 empty] | 21.476 | 7.848 | 13 | 2.1521 | 1.9705 | 4.1482 | 4 | -2.0295 | -94.304
2005-10-31 | 9:11 | 1 | 21.451 | 0 | 15 | 1 | 70.006 | 43.243 | 45.336 | 63.039 | 56.225 | 25.426 | 15.284 | 0 | 1 | 69.127 | 53.087 | 62.861 | 22.15 | 0 | 0 | 56.405 | 37.935 | [5 empty] | 21.451 | 6.967 | 14 | 2.1457 | 1.9644 | 4.1479 | 4 | -2.0356 | -94.8694
2005-10-31 | 9:12 | 0 | 21.476 | 0 | 15 | 0 | 70.05 | 43.126 | 46.919 | 63.623 | 56.112 | 25.472 | 15.262 | 0 | 0 | 69.368 | 53.82 | 63.6 | 22.125 | 0 | 0 | 56.471 | 40.071 | [5 empty] | 0 | 6.427 | 0 | 2.1521 | 1.9705 | 4.1482 | 4 | -2.0295 | -94.304
2005-10-31 | 9:13 | 1 | 21.451 | 1 | 14 | 0 | 70.093 | 43.126 | 47.997 | 64.159 | 56.068 | 25.426 | 15.284 | 0 | 0 | 69.456 | 54.371 | 64.07 | 22.125 | 0 | 0 | 56.652 | 41.741 | [5 empty] | 21.451 | 5.934 | 1 | 2.1457 | 1.9644 | 1.2591 | 1.1111 | 0.85328 | 39.7669
2005-10-31 | 9:14 | 0 | 21.476 | 0 | 15 | 0 | 70.05 | 43.102 | 49.096 | 64.563 | 55.907 | 25.593 | 15.309 | 0 | 0 | 69.523 | 54.943 | 64.54 | 22.125 | 0 | 0 | 56.921 | 43.056 | [5 empty] | 0 | 5.487 | 2 | 2.1384 | 1.9575 | 1.2588 | 1.1111 | 0.84636 | 39.5787
2005-10-31 | 9:15 | 1 | 21.476 | 0 | 15 | 0 | 69.983 | 43.102 | 49.876 | 64.944 | 55.837 | 25.521 | 15.36 | 1 | 0 | 69.5 | 55.494 | 64.922 | 22.125 | 0 | 0 | 57.167 | 44.09 | [5 empty] | 21.476 | 5.039 | 3 | 2.1236 | 1.9434 | 1.2582 | 1.1111 | 0.83224 | 39.1907
2005-10-31 | 9:16 | 0 | 21.476 | 0 | 11 | 0 | 69.565 | 49.785 | 46.781 | 65.214 | 47.012 | 25.617 | 15.284 | 0 | 0 | 69.433 | 55.93 | 65.147 | 22.125 | 0 | 0 | 57.391 | 44.925 | [5 empty] | 0 | 4.351 | 4 | 2.1457 | 1.9644 | 1.2591 | 1.1111 | 0.85328 | 39.7669
2005-10-31 | 9:17 | 0 | 21.451 | 0 | 2 | 0 | 67.477 | 66.311 | 36.337 | 64.833 | 33.845 | 25.737 | 15.284 | 0 | 0 | 68.49 | 56.382 | 64.07 | 22.15 | 0 | 0 | 57.66 | 44.741 | [5 empty] | 0 | 2.644 | 5 | 2.1457 | 1.9644 | 1.2591 | 1.1111 | 0.85328 | 39.7669
2005-10-31 | 9:18 | 0 | 21.402 | 0 | 1 | 0 | 65.976 | 68.203 | 33.4 | 53.155 | 27.785 | 25.666 | 15.262 | 0 | 0 | 67.007 | 56.629 | 61.448 | 22.101 | 0 | 0 | 57.884 | 44.324 | [5 empty] | 0 | 12.821 | 6 | 2.1521 | 1.9705 | 1.2593 | 1.1111 | 0.85937 | 39.9315
2005-10-31 | 9:19 | 0 | 21.456 | 0 | 0 | 0 | 64.883 | 67.568 | 32.24 | 44.536 | 25.521 | 25.786 | 15.262 | 0 | 0 | 65.864 | 56.875 | 58.714 | 22.125 | 0 | 0 | 58.087 | 43.807 | [5 empty] | 0 | 20.347 | 7 | 2.1521 | 1.9705 | 1.2593 | 1.1111 | 0.85937 | 39.9315
2005-10-31 | 9:20 | 0 | 21.451 | 0 | 0 | 0 | 64.159 | 67.277 | 31.929 | 43.08 | 24.028 | 25.835 | 15.284 | 0 | 0 | 65.102 | 57.055 | 56.563 | 22.101 | 0 | 0 | 58.311 | 43.339 | [5 empty] | 0 | 21.079 | 8 | 2.1457 | 1.9644 | 1.2591 | 1.1111 | 0.85328 | 39.7669
2005-10-31 | 9:21 | 0 | 21.456 | 0 | 0 | 0 | 63.605 | 66.968 | 31.693 | 42.779 | 22.756 | 25.816 | 15.292 | 0 | 0 | 64.456 | 57.217 | 55.062 | 22.13 | 0 | 0 | 58.381 | 42.92 | [5 empty] | 0 | 20.826 | 9 | 2.1434 | 1.9622 | 1.259 | 1.1111 | 0.85106 | 39.7068
2005-10-31 | 9:22 | 0 | 21.451 | 0 | 0 | 0 | 63.018 | 66.626 | 31.71 | 42.609 | 21.667 | 25.762 | 15.262 | 0 | 0 | 63.959 | 57.256 | 53.797 | 22.101 | 0 | 0 | 58.489 | 42.468 | [5 empty] | 0 | 20.409 | 10 | 2.1521 | 1.9705 | 1.2593 | 1.1111 | 0.85937 | 39.9315
2005-10-31 | 9:23 | 0 | 21.456 | 0 | 0 | 0 | 62.462 | 66.295 | 31.838 | 42.473 | 21.191 | 25.816 | 15.314 | 0 | 0 | 63.628 | 57.373 | 52.726 | 22.155 | 0 | 0 | 58.607 | 42.121 | [5 empty] | 0 | 19.989 | 11 | 2.137 | 1.9561 | 1.2587 | 1.1111 | 0.84497 | 39.5409
2005-10-31 | 9:24 | 0 | 21.481 | 0 | 0 | 0 | 61.923 | 65.869 | 32.029 | 42.334 | 20.591 | 25.84 | 15.34 | 0 | 0 | 63.313 | 57.441 | 51.899 | 22.155 | 0 | 0 | 58.651 | 41.745 | [5 empty] | 0 | 19.589 | 12 | 2.1294 | 1.9489 | 1.2584 | 1.1111 | 0.83778 | 39.3435
2005-10-31 | 9:25 | 0 | 21.451 | 0 | 0 | 0 | 61.336 | 65.483 | 32.049 | 42.092 | 20.149 | 25.857 | 15.309 | 0 | 0 | 63.018 | 57.437 | 51.253 | 22.125 | 0 | 0 | 58.758 | 41.341 | [5 empty] | 0 | 19.244 | 13 | 2.1384 | 1.9575 | 1.2588 | 1.1111 | 0.84636 | 39.5787
2005-10-31 | 9:26 | 0 | 21.456 | 0 | 0 | 0 | 60.802 | 65.063 | 32.078 | 41.899 | 20.192 | 25.899 | 15.327 | 1 | 0 | 62.811 | 57.521 | 50.788 | 22.143 | 0 | 0 | 58.799 | 41.076 | [5 empty] | 0 | 18.903 | 14 | 2.1332 | 1.9525 | 1.2586 | 1.1111 | 0.84138 | 39.4423
2005-10-31 | 9:27 | 0 | 21.409 | 0 | 0 | 0 | 60.223 | 64.595 | 32.201 | 41.7 | 20.279 | 25.698 | 15.267 | 0 | 0 | 62.555 | 57.489 | 50.436 | 22.108 | 0 | 0 | 58.813 | 40.738 | [5 empty] | 0 | 18.523 | 15 | 2.1506 | 1.9691 | 1.2593 | 1.1111 | 0.85798 | 39.8941
2005-10-31 | 9:28 | 0 | 21.409 | 0 | 0 | 0 | 59.664 | 64.168 | 32.225 | 41.561 | 20.833 | 25.624 | 15.292 | 0 | 0 | 62.354 | 57.512 | 50.184 | 22.108 | 0 | 0 | 58.902 | 40.432 | [5 empty] | 0 | 18.103 | 16 | 2.1434 | 1.9622 | 1.259 | 1.1111 | 0.85106 | 39.7068
2005-10-31 | 9:29 | 0 | 21.434 | 0 | 0 | 0 | 59.059 | 63.721 | 32.417 | 41.279 | 22.422 | 25.698 | 15.367 | 0 | 0 | 62.197 | 57.555 | 49.976 | 22.108 | 0 | 0 | 58.856 | 40.243 | [5 empty] | 0 | 17.78 | 17 | 2.1215 | 1.9414 | 1.2581 | 1.1111 | 0.8303 | 39.137
2005-10-31 | 9:30 | 0 | 21.466 | 0 | 0 | 0 | 58.527 | 63.301 | 32.402 | 41.004 | 21.611 | 25.681 | 15.325 | 0 | 0 | 62.115 | 57.608 | 49.915 | 22.14 | 0 | 0 | 58.863 | 40.016 | [5 empty] | 0 | 17.523 | 18 | 2.1338 | 1.953 | 1.2586 | 1.1111 | 0.84193 | 39.4575
2005-10-31 | 9:31 | 0 | 21.466 | 0 | 0 | 0 | 58.169 | 62.854 | 32.546 | 40.887 | 21.321 | 25.777 | 15.35 | 0 | 0 | 62.003 | 57.653 | 49.778 | 22.165 | 0 | 0 | 58.886 | 39.829 | [5 empty] | 0 | 17.282 | 19 | 2.1265 | 1.9461 | 1.2583 | 1.1111 | 0.83501 | 39.2672
2005-10-31 | 9:32 | 0 | 21.434 | 0 | 0 | 0 | 57.489 | 62.331 | 32.56 | 40.621 | 20.738 | 25.769 | 15.194 | 0 | 0 | 61.905 | 57.601 | 49.633 | 22.084 | 0 | 0 | 58.879 | 39.564 | [5 empty] | 0 | 16.868 | 20 | 2.1719 | 1.9893 | 1.2601 | 1.1111 | 0.87819 | 40.434
2005-10-31 | 9:33 | 0 | 21.441 | 0 | 0 | 0 | 57.026 | 61.934 | 32.497 | 40.533 | 20.066 | 25.632 | 15.252 | 0 | 0 | 61.845 | 57.653 | 49.754 | 22.165 | 0 | 0 | 58.842 | 39.406 | [5 empty] | 0 | 16.493 | 21 | 2.155 | 1.9732 | 1.2594 | 1.1111 | 0.86214 | 40.006
2005-10-31 | 9:34 | 0 | 21.409 | 0 | 2 | 0 | 60.583 | 60.223 | 32.007 | 36.062 | 20.787 | 25.553 | 15.096 | 0 | 0 | 61.727 | 57.624 | 49.542 | 22.133 | 0 | 0 | 58.79 | 39.21 | [5 empty] | 0 | 24.521 | 22 | 2.2004 | 2.0164 | 1.2613 | 1.1111 | 0.90532 | 41.1424
2005-10-31 | 9:35 | 0 | 21.36 | 0 | 0 | 0 | 60.269 | 59.125 | 32.866 | 33.782 | 20.084 | 25.553 | 15.144 | 0 | 0 | 61.681 | 57.601 | 49.563 | 22.108 | 0 | 0 | 58.833 | 39.023 | [5 empty] | 0 | 26.487 | 23 | 2.1865 | 2.0031 | 1.2607 | 1.1111 | 0.89203 | 40.7978
2005-10-31 | 9:36 | 0 | 21.409 | 0 | 0 | 0 | 59.776 | 58.609 | 33.031 | 33.455 | 19.737 | 25.553 | 15.118 | 0 | 0 | 61.613 | 57.646 | 49.404 | 22.157 | 0 | 0 | 58.79 | 38.928 | [5 empty] | 0 | 26.321 | 24 | 2.194 | 2.0103 | 1.261 | 1.1111 | 0.89923 | 40.985
2005-10-31 | 9:37 | 0 | 21.441 | 0 | 0 | 0 | 59.223 | 58.327 | 33.015 | 33.414 | 19.722 | 25.536 | 15.176 | 0 | 0 | 61.576 | 57.653 | 49.388 | 22.165 | 0 | 0 | 58.819 | 38.748 | [5 empty] | 0 | 25.809 | 25 | 2.1771 | 1.9943 | 1.2603 | 1.1111 | 0.88317 | 40.5655
2005-10-31 | 9:38 | 0 | 21.466 | 0 | 0 | 0 | 58.662 | 58.034 | 32.921 | 33.39 | 19.87 | 25.512 | 15.226 | 0 | 0 | 61.53 | 57.653 | 49.341 | 22.189 | 0 | 0 | 58.797 | 38.631 | [5 empty] | 0 | 25.272 | 26 | 2.1626 | 1.9804 | 1.2597 | 1.1111 | 0.86933 | 40.1987
2005-10-31 | 9:39 | 0 | 21.434 | 0 | 0 | 0 | 58.005 | 57.713 | 32.936 | 33.125 | 19.91 | 25.48 | 15.219 | 0 | 0 | 61.546 | 57.646 | 49.243 | 22.133 | 0 | 0 | 58.721 | 38.435 | [5 empty] | 0 | 24.88 | 27 | 2.1646 | 1.9824 | 1.2598 | 1.1111 | 0.87127 | 40.2503
2005-10-31 | 9:40 | 0 | 21.409 | 0 | 0 | 0 | 57.466 | 57.4 | 32.773 | 33.125 | 19.588 | 25.335 | 15.219 | 0 | 0 | 61.435 | 57.646 | 49.358 | 22.133 | 0 | 0 | 58.744 | 38.294 | [5 empty] | 0 | 24.341 | 28 | 2.1646 | 1.9824 | 1.2598 | 1.1111 | 0.87127 | 40.2503
2005-10-31 | 9:41 | 0 | 21.409 | 0 | 0 | 0 | 56.928 | 57.131 | 32.795 | 33.031 | 19.121 | 25.335 | 15.194 | 0 | 0 | 61.366 | 57.624 | 49.267 | 22.133 | 0 | 0 | 58.813 | 38.177 | [5 empty] | 0 | 23.897 | 29 | 2.1719 | 1.9893 | 1.2601 | 1.1111 | 0.87819 | 40.434
2005-10-31 | 9:42 | 0 | 21.417 | 0 | 0 | 0 | 56.398 | 56.846 | 32.732 | 32.897 | 19.794 | 25.296 | 15.299 | 0 | 0 | 61.375 | 57.676 | 49.318 | 22.165 | 0 | 0 | 58.685 | 38.114 | [5 empty] | 0 | 23.501 | 30 | 2.1413 | 1.9602 | 1.2589 | 1.1111 | 0.84913 | 39.6541
2005-10-31 | 9:43 | 0 | 21.417 | 0 | 0 | 0 | 55.876 | 56.533 | 32.78 | 32.874 | 19.324 | 25.247 | 15.325 | 0 | 0 | 61.33 | 57.676 | 49.159 | 22.14 | 0 | 0 | 58.708 | 37.997 | [5 empty] | 0 | 23.002 | 31 | 2.1338 | 1.953 | 1.2586 | 1.1111 | 0.84193 | 39.4575
2005-10-31 | 9:44 | 0 | 21.466 | 0 | 0 | 0 | 55.372 | 56.218 | 32.756 | 32.804 | 19.498 | 25.342 | 15.35 | 0 | 0 | 61.241 | 57.676 | 49.136 | 22.165 | 0 | 0 | 58.708 | 37.878 | [5 empty] | 0 | 22.568 | 32 | 2.1265 | 1.9461 | 1.2583 | 1.1111 | 0.83501 | 39.2672
2005-10-31 | 9:45 | 0 | 21.434 | 0 | 0 | 0 | 54.861 | 55.893 | 32.584 | 32.819 | 19.219 | 25.144 | 14.922 | 0 | 0 | 61.143 | 57.624 | 49.197 | 22.133 | 0 | 0 | 58.566 | 37.753 | [5 empty] | 0 | 22.042 | 33 | 2.2511 | 2.0646 | 1.2633 | 1.1111 | 0.95348 | 42.3559
2005-10-31 | 9:46 | 0 | 21.466 | 0 | 0 | 0 | 54.364 | 55.601 | 32.687 | 32.663 | 19.375 | 25.247 | 15.053 | 0 | 0 | 61.108 | 57.656 | 49.136 | 22.14 | 0 | 0 | 58.687 | 37.646 | [5 empty] | 0 | 21.701 | 34 | 2.213 | 2.0283 | 1.2618 | 1.1111 | 0.91722 | 41.4475
2005-10-31 | 9:47 | 0 | 21.466 | 0 | 0 | 0 | 53.907 | 55.305 | 32.497 | 32.687 | 19.251 | 25.2 | 15.299 | 0 | 0 | 61.085 | 57.678 | 49.183 | 22.309 | 0 | 0 | 58.641 | 37.574 | [5 empty] | 0 | 21.22 | 35 | 2.1413 | 1.9602 | 1.2589 | 1.1111 | 0.84913 | 39.6541
2005-10-31 | 9:48 | 0 | 21.522 | 0 | 0 | 0 | 53.454 | 55.036 | 32.67 | 32.553 | 19.259 | 25.208 | 15.234 | 0 | 0 | 61.003 | 57.685 | 49.098 | 22.221 | 0 | 0 | 58.582 | 37.536 | [5 empty] | 0 | 20.901 | 36 | 2.1603 | 1.9782 | 1.2596 | 1.1111 | 0.86712 | 40.1395
2005-10-31 | 9:49 | 0 | 21.498 | 0 | 0 | 0 | 52.973 | 54.716 | 32.529 | 32.385 | 19.432 | 25.11 | 15.209 | 0 | 0 | 60.889 | 57.685 | 49.145 | 22.221 | 0 | 0 | 58.603 | 37.464 | [5 empty] | 0 | 20.588 | 37 | 2.1675 | 1.9851 | 1.2599 | 1.1111 | 0.87404 | 40.324
2005-10-31 | 9:50 | 0 | 21.473 | 0 | 2 | 0 | 47.516 | 52.996 | 33.376 | 31.639 | 18.987 | 25.159 | 15.332 | 0 | 0 | 60.846 | 57.662 | 49.075 | 22.221 | 0 | 0 | 58.648 | 37.347 | [5 empty] | 0 | 15.877 | 38 | 2.1317 | 1.9511 | 1.2585 | 1.1111 | 0.83999 | 39.4044
2005-10-31 | 9:51 | 0 | 21.417 | 0 | 2 | 0 | 46.501 | 52.508 | 32.687 | 31.919 | 24.308 | 25.007 | 15.407 | 0 | 0 | 60.734 | 57.64 | 49.122 | 22.221 | 0 | 0 | 58.582 | 37.277 | [5 empty] | 0 | 14.582 | 39 | 2.1099 | 1.9303 | 1.2576 | 1.1111 | 0.81923 | 38.8283
2005-10-31 | 9:52 | 0 | 21.449 | 1 | 1 | 0 | 45.063 | 46.622 | 30.555 | 32.883 | 22.582 | 25.087 | 15.48 | 0 | 0 | 60.688 | 57.662 | 49.19 | 22.197 | 0 | 0 | 58.582 | 37.158 | [5 empty] | 0 | 12.18 | 40 | 2.0886 | 1.9101 | 1.2567 | 1.1111 | 0.79902 | 38.256
2005-10-31 | 9:53 | 0 | 21.473 | 0 | 2 | 0 | 36.782 | 48.662 | 29.253 | 31.686 | 20.608 | 25.087 | 15.48 | 0 | 0 | 60.622 | 57.617 | 49.122 | 22.221 | 0 | 0 | 58.536 | 37.088 | [5 empty] | 0 | 5.096 | 41 | 2.0886 | 1.9101 | 1.2567 | 1.1111 | 0.79902 | 38.256
2005-10-31 | 9:54 | 0 | 21.449 | 0 | 2 | 0 | 34.433 | 42.705 | 28.53 | 29.881 | 19.679 | 25.063 | 15.455 | 0 | 0 | 60.531 | 57.573 | 49.122 | 22.197 | 0 | 0 | 58.559 | 36.995 | [5 empty] | 0 | 4.552 | 42 | 2.0959 | 1.9171 | 1.257 | 1.1111 | 0.80594 | 38.4533
2005-10-31 | 9:55 | 0 | 21.473 | 0 | 2 | 0 | 32.409 | 37.04 | 28.339 | 28.675 | 19.53 | 25.134 | 15.407 | 0 | 0 | 60.488 | 57.617 | 48.961 | 22.197 | 0 | 0 | 58.514 | 36.995 | [5 empty] | 0 | 3.734 | 43 | 2.1099 | 1.9303 | 1.2576 | 1.1111 | 0.81923 | 38.8283
2005-10-31 | 9:56 | 0 | 21.441 | 0 | 2 | 0 | 30.619 | 34.519 | 28.233 | 28.138 | 18.781 | 25.176 | 15.397 | 0 | 0 | 60.346 | 57.564 | 48.907 | 22.165 | 0 | 0 | 58.418 | 36.916 | [5 empty] | 0 | 2.481 | 44 | 2.1128 | 1.9331 | 1.2577 | 1.1111 | 0.822 | 38.9058
2005-10-31 | 9:57 | 0 | 21.473 | 0 | 2 | 0 | 29.592 | 32.553 | 28.025 | 28.099 | 18.246 | 25.11 | 15.455 | 0 | 0 | 60.353 | 57.573 | 48.961 | 22.197 | 0 | 0 | 58.491 | 36.878 | [5 empty] | 0 | 1.493 | 45 | 2.0959 | 1.9171 | 1.257 | 1.1111 | 0.80594 | 38.4533
2005-10-31 | 9:58 | 0 | 21.449 | 0 | 2 | 0 | 28.94 | 30.867 | 28.074 | 27.834 | 18.148 | 25.183 | 15.48 | 0 | 0 | 60.307 | 57.573 | 48.776 | 22.221 | 0 | 0 | 58.447 | 36.83 | [5 empty] | 0 | 1.106 | 46 | 2.0886 | 1.9101 | 1.2567 | 1.1111 | 0.79902 | 38.256
2005-10-31 | 9:59 | 0 | 21.473 | 0 | 2 | 0 | 28.675 | 29.881 | 28.074 | 27.929 | 17.728 | 25.11 | 15.531 | 0 | 0 | 60.218 | 57.551 | 48.732 | 22.221 | 0 | 0 | 58.379 | 36.758 | [5 empty] | 0 | 0.746 | 47 | 2.0738 | 1.896 | 1.2561 | 1.1111 | 0.78491 | 37.8493
2005-10-31 | 10:00 | 0 | 21.449 | 0 | 2 | 0 | 28.434 | 29.398 | 28.29 | 27.834 | 17.851 | 25.183 | 15.556 | 0 | 0 | 60.15 | 57.528 | 48.732 | 22.221 | 0 | 0 | 58.402 | 36.689 | [5 empty] | 0 | 0.6 | 48 | 2.0665 | 1.8891 | 1.2559 | 1.1111 | 0.77799 | 37.6478
2005-10-31 | 10:01 | 0 | 21.473 | 0 | 2 | 0 | 28.388 | 29.038 | 28.844 | 28 | 17.605 | 25.159 | 15.531 | 0 | 0 | 60.061 | 57.505 | 48.685 | 22.221 | 0 | 0 | 58.402 | 36.641 | [5 empty] | 0 | 0.388 | 49 | 2.0738 | 1.896 | 1.2561 | 1.1111 | 0.78491 | 37.8493
2005-10-31 | 10:02 | 0 | 21.498 | 0 | 2 | 0 | 39.485 | 28.844 | 29.158 | 28.508 | 23.594 | 25.232 | 15.556 | 0 | 0 | 60.015 | 57.482 | 48.618 | 22.197 | 0 | 0 | 58.402 | 36.572 | [5 empty] | 0 | 10.977 | 50 | 2.0665 | 1.8891 | 1.2559 | 1.1111 | 0.77799 | 37.6478
2005-10-31 | 10:03 | 0 | 21.473 | 1 | 3 | 0 | 45.752 | 31.421 | 29.038 | 28.94 | 24.678 | 25.183 | 15.654 | 0 | 0 | 59.949 | 57.505 | 48.662 | 22.292 | 0 | 0 | 58.402 | 36.524 | [5 empty] | 0 | 16.812 | 51 | 2.038 | 1.862 | 1.2547 | 1.1111 | 0.75086 | 36.8439
2005-10-31 | 10:04 | 1 | 21.498 | 0 | 2 | 0 | 46.438 | 44.09 | 28.748 | 29.038 | 24.34 | 25.087 | 15.629 | 0 | 0 | 59.903 | 57.439 | 48.571 | 22.197 | 0 | 0 | 58.379 | 36.5 | [5 empty] | 21.498 | 17.4 | 52 | 2.0452 | 1.8689 | 1.255 | 1.1111 | 0.75778 | 37.0511
2005-10-31 | 10:05 | 0 | 21.473 | 0 | 2 | 1 | 46.141 | 46.232 | 28.434 | 28.868 | 24.124 | 25.134 | 15.556 | 0 | 0 | 59.792 | 57.416 | 48.618 | 22.197 | 0 | 0 | 58.29 | 36.478 | [5 empty] | 0 | 17.273 | 53 | 2.0665 | 1.8891 | 1.2559 | 1.1111 | 0.77799 | 37.6478
2005-10-31 | 10:06 | 0 | 21.429 | 0 | 2 | 0 | 46.05 | 46.235 | 28.317 | 28.461 | 24.224 | 25.21 | 15.511 | 0 | 0 | 59.748 | 57.416 | 48.527 | 22.177 | 0 | 0 | 58.29 | 36.385 | [5 empty] | 0 | 17.589 | 0 | 2.0796 | 1.9016 | 1.2564 | 1.1111 | 0.79044 | 38.0095
2005-10-31 | 10:07 | 0 | 21.456 | 0 | 2 | 0 | 46.694 | 46.144 | 28.152 | 28.177 | 24.273 | 25.141 | 15.636 | 2 | 0 | 59.682 | 57.373 | 48.482 | 22.226 | 0 | 0 | 58.338 | 36.342 | [5 empty] | 0 | 18.517 | 1 | 2.0432 | 1.867 | 1.0393 | 0.89552 | 0.97143 | 47.5448
2005-10-31 | 10:08 | 0 | 21.427 | 0 | 2 | 0 | 46.575 | 46.666 | 28.17 | 27.929 | 24.244 | 25.087 | 15.631 | 1 | 0 | 59.677 | 57.345 | 48.524 | 22.15 | 0 | 0 | 58.288 | 36.313 | [5 empty] | 0 | 18.646 | 2 | 2.0447 | 1.8683 | 1.0394 | 0.89552 | 0.97282 | 47.5786
2005-10-31 | 10:09 | 1 | 21.481 | 0 | 2 | 0 | 46.902 | 46.879 | 28.393 | 27.983 | 24.298 | 25.092 | 15.538 | 1 | 0 | 59.659 | 57.373 | 48.552 | 22.204 | 0 | 0 | 58.338 | 36.27 | [5 empty] | 21.481 | 18.919 | 3 | 2.0717 | 1.8941 | 1.0405 | 0.89552 | 0.99856 | 48.1992
2005-10-31 | 10:10 | 0 | 21.456 | 0 | 2 | 0 | 47.04 | 47.061 | 28.851 | 28.054 | 24.273 | 25.141 | 15.611 | 1 | 0 | 59.636 | 57.395 | 48.506 | 22.179 | 0 | 0 | 58.45 | 36.246 | [5 empty] | 0 | 18.986 | 4 | 2.0505 | 1.8739 | 1.0396 | 0.89552 | 0.97835 | 47.7134
2005-10-31 | 10:11 | 0 | 21.481 | 0 | 2 | 0 | 47.175 | 47.292 | 29.332 | 28.368 | 24.227 | 25.213 | 15.759 | 1 | 0 | 59.636 | 57.395 | 48.506 | 22.204 | 0 | 0 | 58.516 | 36.201 | [5 empty] | 0 | 18.807 | 5 | 2.0074 | 1.8329 | 1.0379 | 0.89552 | 0.93739 | 46.697
2005-10-31 | 10:12 | 0 | 21.456 | 1 | 2 | 0 | 47.658 | 47.474 | 29.837 | 28.996 | 24.298 | 25.092 | 15.81 | 2 | 0 | 59.616 | 57.352 | 48.576 | 22.204 | 0 | 0 | 58.473 | 36.177 | [5 empty] | 0 | 18.662 | 6 | 1.9925 | 1.8188 | 1.0373 | 0.89552 | 0.92327 | 46.3366
2005-10-31 | 10:13 | 0 | 21.481 | 0 | 2 | 0 | 48.139 | 47.588 | 30.32 | 29.501 | 24.394 | 25.237 | 15.712 | 1 | 0 | 59.636 | 57.373 | 48.552 | 22.179 | 0 | 0 | 58.427 | 36.153 | [5 empty] | 0 | 18.638 | 7 | 2.0211 | 1.8459 | 1.0384 | 0.89552 | 0.9504 | 47.0245
2005-10-31 | 10:14 | 0 | 21.476 | 0 | 2 | 0 | 48.639 | 48.065 | 30.676 | 29.928 | 24.558 | 25.183 | 15.729 | 1 | 0 | 59.566 | 57.345 | 48.524 | 22.15 | 0 | 0 | 58.311 | 36.124 | [5 empty] | 0 | 18.711 | 8 | 2.0161 | 1.8412 | 1.0382 | 0.89552 | 0.94569 | 46.9066
2005-10-31 | 10:15 | 1 | 21.451 | 0 | 2 | 0 | 49.257 | 48.548 | 30.771 | 30.386 | 24.798 | 25.112 | 15.729 | 1 | 0 | 59.566 | 57.325 | 48.639 | 22.175 | 0 | 0 | 58.269 | 36.129 | [5 empty] | 21.451 | 18.871 | 9 | 2.0161 | 1.8412 | 1.0382 | 0.89552 | 0.94569 | 46.9066
2005-10-31 | 10:16 | 0 | 21.481 | 0 | 2 | 0 | 49.904 | 49.148 | 31.041 | 30.511 | 25.021 | 25.19 | 15.835 | 1 | 0 | 59.593 | 57.418 | 48.597 | 22.204 | 0 | 0 | 58.269 | 36.108 | [5 empty] | 0 | 19.393 | 10 | 1.9852 | 1.8119 | 1.037 | 0.89552 | 0.91635 | 46.1579
2005-10-31 | 10:17 | 0 | 21.505 | 0 | 2 | 0 | 44.608 | 49.698 | 31.235 | 30.776 | 22.949 | 25.213 | 15.712 | 1 | 0 | 59.593 | 57.373 | 48.597 | 22.179 | 0 | 0 | 58.226 | 36.06 | [5 empty] | 0 | 13.832 | 11 | 2.0211 | 1.8459 | 1.0384 | 0.89552 | 0.9504 | 47.0245
2005-10-31 | 10:18 | 0 | 21.456 | 0 | 2 | 0 | 36.318 | 49.95 | 31.499 | 30.994 | 21.432 | 25.311 | 15.687 | 1 | 0 | 59.616 | 57.373 | 48.597 | 22.179 | 0 | 0 | 58.226 | 36.036 | [5 empty] | 0 | 5.324 | 12 | 2.0283 | 1.8528 | 1.0387 | 0.89552 | 0.95732 | 47.1969
2005-10-31 | 10:19 | 0 | 21.481 | 0 | 2 | 0 | 33.873 | 42.193 | 31.669 | 31.379 | 20.735 | 25.262 | 15.661 | 0 | 0 | 59.636 | 57.373 | 48.643 | 22.204 | 0 | 0 | 58.226 | 36.036 | [5 empty] | 0 | 2.494 | 13 | 2.0359 | 1.86 | 1.039 | 0.89552 | 0.96451 | 47.3749
2005-10-31 | 10:20 | 0 | 21.456 | 0 | 1 | 0 | 33.098 | 36.459 | 32.005 | 31.428 | 20.031 | 25.311 | 15.712 | 0 | 0 | 59.57 | 57.373 | 48.69 | 22.204 | 0 | 0 | 58.203 | 36.06 | [5 empty] | 0 | 1.67 | 14 | 2.0211 | 1.8459 | 1.0384 | 0.89552 | 0.9504 | 47.0245
2005-10-31 | 10:21 | 0 | 21.456 | 0 | 2 | 0 | 32.84 | 34.51 | 31.958 | 31.62 | 19.465 | 25.333 | 15.734 | 0 | 0 | 59.57 | 57.352 | 48.804 | 22.204 | 0 | 0 | 58.203 | 36.012 | [5 empty] | 0 | 1.22 | 15 | 2.0147 | 1.8398 | 1.0382 | 0.89552 | 0.94431 | 46.8718
2005-10-31 | 10:22 | 0 | 21.481 | 0 | 2 | 0 | 32.723 | 33.732 | 32.078 | 31.933 | 19.093 | 25.357 | 15.835 | 0 | 0 | 59.593 | 57.329 | 48.69 | 22.204 | 0 | 0 | 58.203 | 36.012 | [5 empty] | 0 | 0.79 | 16 | 1.9852 | 1.8119 | 1.037 | 0.89552 | 0.91635 | 46.1579
2005-10-31 | 10:23 | 0 | 21.456 | 1 | 2 | 0 | 32.699 | 33.405 | 32.103 | 31.933 | 18.821 | 25.286 | 15.857 | 0 | 0 | 59.547 | 57.329 | 48.713 | 22.204 | 0 | 0 | 58.158 | 35.988 | [5 empty] | 0 | 0.766 | 17 | 1.9788 | 1.8058 | 1.0367 | 0.89552 | 0.91026 | 45.9996
2005-10-31 | 10:24 | 0 | 21.481 | 0 | 2 | 0 | 32.675 | 33.216 | 31.909 | 32.005 | 18.698 | 25.333 | 15.958 | 0 | 0 | 59.547 | 57.329 | 48.713 | 22.204 | 0 | 0 | 58.135 | 35.966 | [5 empty] | 0 | 0.67 | 18 | 1.9494 | 1.7778 | 1.0355 | 0.89552 | 0.8823 | 45.2595
2005-10-31 | 10:25 | 0 | 21.505 | 0 | 1 | 0 | 32.675 | 33.146 | 31.549 | 31.933 | 18.525 | 25.333 | 15.958 | 1 | 0 | 59.525 | 57.329 | 48.758 | 22.204 | 0 | 0 | 58.135 | 35.895 | [5 empty] | 0 | 0.742 | 19 | 1.9494 | 1.7778 | 1.0355 | 0.89552 | 0.8823 | 45.2595
2005-10-31 | 10:26 | 0 | 21.505 | 0 | 2 | 0 | 32.699 | 33.074 | 31.284 | 31.764 | 19.895 | 25.323 | 16.018 | 0 | 0 | 59.513 | 57.295 | 48.655 | 22.192 | 0 | 0 | 58.123 | 35.813 | [5 empty] | 0 | 0.935 | 20 | 1.932 | 1.7612 | 1.0348 | 0.89552 | 0.8657 | 44.8092
2005-10-31 | 10:27 | 0 | 21.483 | 0 | 2 | 0 | 43.415 | 33.031 | 30.852 | 31.622 | 24.3 | 25.313 | 16.033 | 0 | 0 | 59.484 | 57.286 | 48.716 | 22.327 | 0 | 0 | 58.16 | 35.921 | [5 empty] | 0 | 11.793 | 21 | 1.9276 | 1.7571 | 1.0346 | 0.89552 | 0.86154 | 44.6953
2005-10-31 | 10:28 | 0 | 21.454 | 0 | 2 | 0 | 44.398 | 33.354 | 30.244 | 31.137 | 21.839 | 25.33 | 16.003 | 0 | 0 | 59.41 | 57.259 | 48.688 | 22.177 | 0 | 0 | 58.133 | 35.751 | [5 empty] | 0 | 13.261 | 22 | 1.9363 | 1.7654 | 1.035 | 0.89552 | 0.86985 | 44.9226
2005-10-31 | 10:29 | 0 | 21.483 | 0 | 1 | 0 | 35.921 | 44.543 | 29.793 | 30.828 | 20.159 | 25.338 | 16.033 | 0 | 0 | 59.395 | 57.243 | 48.669 | 22.206 | 0 | 0 | 58.094 | 35.78 | [5 empty] | 0 | 5.093 | 23 | 1.9276 | 1.7571 | 1.0346 | 0.89552 | 0.86154 | 44.6953
2005-10-31 | 10:30 | 0 | 21.483 | 0 | 2 | 0 | 33.149 | 42.006 | 29.504 | 30.202 | 19.171 | 25.409 | 16.157 | 1 | 0 | 59.461 | 57.263 | 48.83 | 22.206 | 0 | 0 | 58.117 | 35.732 | [5 empty] | 0 | 2.947 | 24 | 1.8915 | 1.7227 | 1.0332 | 0.89552 | 0.82722 | 43.734
2005-10-31 | 10:31 | 0 | 21.483 | 0 | 2 | 0 | 32.007 | 35.99 | 29.214 | 29.673 | 18.676 | 25.36 | 16.008 | 0 | 0 | 59.395 | 57.263 | 48.669 | 22.206 | 0 | 0 | 58.117 | 35.732 | [5 empty] | 0 | 2.334 | 25 | 1.9349 | 1.764 | 1.0349 | 0.89552 | 0.86846 | 44.8848
2005-10-31 | 10:32 | 0 | 21.483 | 0 | 1 | 0 | 31.286 | 33.548 | 29.07 | 29.359 | 18.429 | 25.338 | 15.986 | 0 | 0 | 59.349 | 57.263 | 48.669 | 22.206 | 0 | 0 | 58.137 | 35.71 | [5 empty] | 0 | 1.927 | 26 | 1.9413 | 1.7701 | 1.0352 | 0.89552 | 0.87455 | 45.0504
2005-10-31 | 10:33 | 0 | 21.483 | 0 | 2 | 0 | 30.757 | 32.49 | 28.756 | 29.119 | 18.331 | 25.338 | 15.935 | 0 | 0 | 59.349 | 57.22 | 48.601 | 22.182 | 0 | 0 | 58.117 | 35.663 | [5 empty] | 0 | 1.638 | 27 | 1.9561 | 1.7842 | 1.0358 | 0.89552 | 0.88867 | 45.43
2005-10-31 | 10:34 | 0 | 21.508 | 0 | 2 | 0 | 30.298 | 31.816 | 28.611 | 28.829 | 18.233 | 25.24 | 15.986 | 0 | 0 | 59.326 | 57.197 | 48.669 | 22.206 | 0 | 0 | 58.094 | 35.687 | [5 empty] | 0 | 1.469 | 28 | 1.9413 | 1.7701 | 1.0352 | 0.89552 | 0.87455 | 45.0504
2005-10-31 | 10:35 | 0 | 21.483 | 1 | 1 | 0 | 30.033 | 31.213 | 28.589 | 28.829 | 18.108 | 25.193 | 15.986 | 0 | 0 | 59.303 | 57.197 | 48.716 | 22.228 | 0 | 0 | 58.094 | 35.78 | [5 empty] | 0 | 1.204 | 29 | 1.9413 | 1.7701 | 1.0352 | 0.89552 | 0.87455 | 45.0504
2005-10-31 | 10:36 | 0 | 21.508 | 0 | 2 | 0 | 29.648 | 30.732 | 28.54 | 28.611 | 18.108 | 25.144 | 15.961 | 0 | 0 | 59.26 | 57.174 | 48.601 | 22.206 | 0 | 0 | 58.025 | 35.639 | [5 empty] | 0 | 1.037 | 30 | 1.9486 | 1.777 | 1.0355 | 0.89552 | 0.88147 | 45.2372
2005-10-31 | 10:37 | 0 | 21.483 | 0 | 1 | 0 | 29.455 | 30.323 | 28.491 | 28.589 | 18.009 | 25.119 | 15.935 | 0 | 0 | 59.26 | 57.174 | 48.578 | 22.206 | 0 | 0 | 57.913 | 35.615 | [5 empty] | 0 | 0.866 | 31 | 1.9561 | 1.7842 | 1.0358 | 0.89552 | 0.88867 | 45.43
2005-10-31 | 10:38 | 0 | 21.483 | 0 | 2 | 0 | 35.873 | 30.082 | 28.469 | 28.54 | 23.435 | 25.215 | 15.885 | 0 | 0 | 59.26 | 57.174 | 48.669 | 22.182 | 0 | 0 | 57.87 | 35.569 | [5 empty] | 0 | 7.333 | 32 | 1.9707 | 1.798 | 1.0364 | 0.89552 | 0.90251 | 45.7967
2005-10-31 | 10:39 | 0 | 21.483 | 0 | 2 | 0 | 45.047 | 29.864 | 28.275 | 28.564 | 21.603 | 25.193 | 15.885 | 1 | 0 | 59.214 | 57.108 | 48.555 | 22.182 | 0 | 0 | 57.847 | 35.545 | [5 empty] | 0 | 16.483 | 33 | 1.9707 | 1.798 | 1.0364 | 0.89552 | 0.90251 | 45.7967
2005-10-31 | 10:40 | 0 | 21.429 | 0 | 2 | 0 | 34.27 | 39.652 | 28.27 | 28.341 | 20.006 | 25.164 | 15.855 | 0 | 0 | 59.164 | 57.081 | 48.503 | 22.152 | 0 | 0 | 57.843 | 35.469 | [5 empty] | 0 | 5.929 | 34 | 1.9794 | 1.8063 | 1.0367 | 0.89552 | 0.91081 | 46.0141
2005-10-31 | 10:41 | 0 | 21.483 | 0 | 1 | 0 | 30.803 | 41.301 | 28.324 | 28.251 | 18.925 | 25.215 | 15.935 | 0 | 0 | 59.191 | 57.128 | 48.531 | 22.206 | 0 | 0 | 57.913 | 35.474 | [5 empty] | 0 | 2.552 | 35 | 1.9561 | 1.7842 | 1.0358 | 0.89552 | 0.88867 | 45.43
2005-10-31 | 10:42 | 0 | 21.454 | 0 | 2 | 0 | 29.739 | 34.084 | 28.246 | 28.27 | 18.326 | 25.186 | 15.855 | 0 | 0 | 59.141 | 57.058 | 48.503 | 22.177 | 0 | 0 | 57.909 | 35.469 | [5 empty] | 0 | 1.469 | 36 | 1.9794 | 1.8063 | 1.0367 | 0.89552 | 0.91081 | 46.0141
2005-10-31 | 10:43 | 0 | 21.483 | 0 | 2 | 0 | 29.263 | 31.262 | 28.3 | 28.251 | 17.886 | 25.338 | 15.837 | 0 | 0 | 59.191 | 57.085 | 48.485 | 22.206 | 0 | 0 | 57.982 | 35.474 | [5 empty] | 0 | 1.012 | 37 | 1.9847 | 1.8113 | 1.0369 | 0.89552 | 0.9158 | 46.1436
2005-10-31 | 10:44 | 0 | 21.483 | 0 | 1 | 0 | 29.07 | 30.202 | 28.13 | 28.202 | 17.59 | 25.384 | 15.863 | 0 | 0 | 59.191 | 57.085 | 48.508 | 22.157 | 0 | 0 | 57.87 | 35.428 | [5 empty] | 0 | 0.868 | 38 | 1.9771 | 1.8041 | 1.0366 | 0.89552 | 0.9086 | 45.9563
2005-10-31 | 10:45 | 0 | 21.429 | 0 | 2 | 0 | 28.895 | 29.739 | 28.076 | 28.101 | 17.363 | 25.235 | 15.855 | 0 | 0 | 59.098 | 57.058 | 48.457 | 22.152 | 0 | 0 | 57.751 | 35.423 | [5 empty] | 0 | 0.794 | 39 | 1.9794 | 1.8063 | 1.0367 | 0.89552 | 0.91081 | 46.0141
2005-10-31 | 10:46 | 0 | 21.459 | 1 | 1 | 0 | 28.876 | 29.479 | 28.13 | 28.13 | 17.22 | 25.264 | 15.863 | 1 | 0 | 59.121 | 57.081 | 48.506 | 22.228 | 0 | 0 | 57.777 | 35.474 | [5 empty] | 0 | 0.746 | 40 | 1.9771 | 1.8041 | 1.0366 | 0.89552 | 0.9086 | 45.9563
2005-10-31 | 10:47 | 0 | 21.449 | 0 | 2 | 0 | 28.721 | 29.347 | 28.023 | 28.023 | 16.961 | 25.205 | 15.875 | 0 | 0 | 59.112 | 57.026 | 48.45 | 22.123 | 0 | 0 | 57.722 | 35.368 | [5 empty] | 0 | 0.698 | 41 | 1.9736 | 1.8008 | 1.0365 | 0.89552 | 0.90528 | 45.8694
2005-10-31 | 10:48 | 0 | 21.395 | 0 | 2 | 0 | 28.596 | 29.15 | 27.922 | 27.969 | 16.76 | 25.151 | 15.87 | 0 | 0 | 59.039 | 56.976 | 48.445 | 22.118 | 0 | 0 | 57.738 | 35.34 | [5 empty] | 0 | 0.627 | 42 | 1.9751 | 1.8022 | 1.0366 | 0.89552 | 0.90666 | 45.9056
2005-10-31 | 10:49 | 1 | 21.449 | 0 | 2 | 0 | 32.142 | 29.106 | 27.902 | 27.853 | 22.653 | 25.23 | 15.951 | 0 | 0 | 59.066 | 56.982 | 48.426 | 22.148 | 0 | 0 | 57.699 | 35.323 | [5 empty] | 21.449 | 4.289 | 43 | 1.9515 | 1.7798 | 1.0356 | 0.89552 | 0.88424 | 45.3116
2005-10-31 | 10:50 | 0 | 21.449 | 0 | 1 | 0 | 45.331 | 28.962 | 27.927 | 27.853 | 20.897 | 25.276 | 15.925 | 1 | 0 | 59.043 | 57.003 | 48.405 | 22.17 | 0 | 0 | 57.676 | 35.323 | [5 empty] | 0 | 17.478 | 44 | 1.959 | 1.787 | 1.0359 | 0.89552 | 0.89144 | 45.5038
2005-10-31 | 10:51 | 0 | 21.449 | 0 | 2 | 0 | 34.053 | 38.165 | 27.687 | 27.782 | 19.407 | 25.132 | 15.9 | 0 | 0 | 59 | 56.982 | 48.426 | 22.17 | 0 | 0 | 57.676 | 35.344 | [5 empty] | 0 | 6.271 | 45 | 1.9663 | 1.7939 | 1.0362 | 0.89552 | 0.89836 | 45.6873
2005-10-31 | 10:52 | 0 | 21.449 | 0 | 2 | 0 | 30.261 | 40.655 | 27.782 | 27.853 | 18.369 | 25.132 | 15.9 | 0 | 0 | 59 | 57.003 | 48.473 | 22.17 | 0 | 0 | 57.653 | 35.344 | [5 empty] | 0 | 2.408 | 46 | 1.9663 | 1.7939 | 1.0362 | 0.89552 | 0.89836 | 45.6873
2005-10-31 | 10:53 | 0 | 21.449 | 0 | 2 | 0 | 29.131 | 33.326 | 27.782 | 27.733 | 17.703 | 25.156 | 15.875 | 0 | 0 | 59 | 56.96 | 48.541 | 22.148 | 0 | 0 | 57.631 | 35.368 | [5 empty] | 0 | 1.398 | 47 | 1.9736 | 1.8008 | 1.0365 | 0.89552 | 0.90528 | 45.8694
2005-10-31 | 10:54 | 0 | 21.449 | 0 | 2 | 0 | 28.626 | 30.43 | 27.829 | 27.687 | 17.381 | 25.23 | 15.951 | 1 | 0 | 59 | 57.049 | 48.657 | 22.29 | 0 | 0 | 57.699 | 35.368 | [5 empty] | 0 | 0.939 | 48 | 1.9515 | 1.7798 | 1.0356 | 0.89552 | 0.88424 | 45.3116
2005-10-31 | 10:55 | 0 | 21.449 | 0 | 1 | 0 | 28.432 | 29.467 | 27.807 | 27.687 | 17.109 | 25.23 | 15.827 | 0 | 0 | 58.977 | 56.96 | 48.473 | 22.148 | 0 | 0 | 57.61 | 35.323 | [5 empty] | 0 | 0.745 | 49 | 1.9876 | 1.8141 | 1.0371 | 0.89552 | 0.91856 | 46.2153
2005-10-31 | 10:56 | 0 | 21.473 | 0 | 2 | 0 | 28.361 | 29.057 | 27.807 | 27.807 | 17.037 | 25.132 | 15.827 | 0 | 0 | 58.977 | 56.937 | 48.564 | 22.148 | 0 | 0 | 57.61 | 35.323 | [5 empty] | 0 | 0.554 | 50 | 1.9876 | 1.8141 | 1.0371 | 0.89552 | 0.91856 | 46.2153
2005-10-31 | 10:57 | 0 | 21.473 | 0 | 2 | 0 | 28.263 | 28.866 | 27.782 | 27.709 | 16.838 | 25.132 | 15.85 | 0 | 0 | 59.02 | 56.914 | 48.426 | 22.148 | 0 | 0 | 57.653 | 35.323 | [5 empty] | 0 | 0.554 | 51 | 1.9809 | 1.8077 | 1.0368 | 0.89552 | 0.9122 | 46.0501
2005-10-31 | 10:58 | 0 | 21.444 | 1 | 2 | 0 | 28.209 | 28.643 | 27.704 | 27.753 | 16.685 | 25.031 | 15.845 | 0 | 0 | 58.927 | 56.909 | 48.536 | 22.14 | 0 | 0 | 57.649 | 35.294 | [5 empty] | 0 | 0.456 | 52 | 1.9823 | 1.8091 | 1.0369 | 0.89552 | 0.91358 | 46.0861
2005-10-31 | 10:59 | 0 | 21.473 | 0 | 2 | 0 | 28.167 | 28.552 | 27.807 | 27.687 | 16.443 | 25.061 | 15.827 | 0 | 0 | 58.977 | 56.914 | 48.426 | 22.148 | 0 | 0 | 57.676 | 35.323 | [5 empty] | 0 | 0.48 | 53 | 1.9876 | 1.8141 | 1.0371 | 0.89552 | 0.91856 | 46.2153
2005-10-31 | 11:00 | 0 | 21.495 | 0 | 2 | 0 | 29.516 | 28.481 | 27.782 | 27.613 | 22.699 | 25.132 | 15.875 | 0 | 0 | 58.954 | 56.891 | 48.426 | 22.123 | 0 | 0 | 57.765 | 35.299 | [5 empty] | 0 | 1.903 | 54 | 1.9736 | 1.8008 | 1.0365 | 0.89552 | 0.90528 | 45.8694
2005-10-31 | 11:01 | 0 | 21.419 | 0 | 2 | 0 | 44.173 | 28.378 | 27.657 | 27.679 | 20.747 | 24.982 | 15.895 | 1 | 0 | 58.861 | 56.82 | 48.422 | 22.118 | 0 | 0 | 57.672 | 35.246 | [5 empty] | 0 | 16.494 | 55 | 1.9678 | 1.7953 | 1.0363 | 0.89552 | 0.89974 | 45.7238
2005-10-31 | 11:02 | 0 | 21.473 | 0 | 2 | 0 | 33.419 | 38.588 | 27.829 | 27.662 | 18.912 | 25.132 | 15.973 | 0 | 0 | 58.977 | 56.914 | 48.426 | 22.219 | 0 | 0 | 57.745 | 35.275 | [5 empty] | 0 | 5.757 | 56 | 1.9451 | 1.7737 | 1.0353 | 0.89552 | 0.87815 | 45.1477
2005-10-31 | 11:03 | 0 | 21.444 | 0 | 1 | 0 | 29.776 | 38.535 | 27.704 | 27.728 | 17.846 | 24.935 | 15.968 | 0 | 0 | 58.881 | 56.843 | 48.468 | 22.14 | 0 | 0 | 57.626 | 35.294 | [5 empty] | 0 | 2.048 | 57 | 1.9465 | 1.7751 | 1.0354 | 0.89552 | 0.87954 | 45.185
2005-10-31 | 11:04 | 0 | 21.473 | 0 | 2 | 0 | 28.792 | 32.019 | 27.758 | 27.638 | 17.233 | 25.011 | 15.973 | 0 | 0 | 58.888 | 56.871 | 48.426 | 22.148 | 0 | 0 | 57.722 | 35.299 | [5 empty] | 0 | 1.154 | 58 | 1.9451 | 1.7737 | 1.0353 | 0.89552 | 0.87815 | 45.1477
2005-10-31 | 11:05 | 0 | 21.473 | 0 | 2 | 0 | 28.407 | 29.756 | 27.829 | 27.638 | 16.939 | 24.916 | 15.998 | 1 | 0 | 58.865 | 56.848 | 48.426 | 22.148 | 0 | 0 | 57.676 | 35.251 | [5 empty] | 0 | 0.769 | 59 | 1.9378 | 1.7668 | 1.035 | 0.89552 | 0.87123 | 44.9602
2005-10-31 | 11:06 | 0 | 21.473 | 0 | 2 | 0 | 28.287 | 29.082 | 27.853 | 27.638 | 16.639 | 24.82 | 15.948 | 0 | 0 | 58.849 | 56.809 | 48.433 | 22.123 | 0 | 0 | 57.64 | 35.23 | [5 empty] | 0 | 0.649 | 60 | 1.9523 | 1.7806 | 1.0356 | 0.89552 | 0.88507 | 45.3338
2005-10-31 | 11:07 | 0 | 21.562 | 0 | 2 | 0 | 28.258 | 28.834 | 27.895 | 27.75 | 16.582 | 24.933 | 16.038 | 0 | 0 | 58.931 | 56.914 | 48.517 | 22.236 | 0 | 0 | 57.722 | 35.294 | [5 empty] | 0 | 0.508 | 61 | 1.9261 | 1.7557 | 1.0346 | 0.89552 | 0.86016 | 44.6573
2005-10-31 | 11:08 | 0 | 21.537 | 0 | 2 | 0 | 28.16 | 28.714 | 27.895 | 27.75 | 16.509 | 24.958 | 16.038 | 0 | 0 | 58.977 | 56.914 | 48.447 | 22.211 | 0 | 0 | 57.653 | 35.27 | [5 empty] | 0 | 0.41 | 62 | 1.9261 | 1.7557 | 1.0346 | 0.89552 | 0.86016 | 44.6573
2005-10-31 | 11:09 | 0 | 21.537 | 1 | 2 | 0 | 28.135 | 28.545 | 27.799 | 27.75 | 16.582 | 24.884 | 16.038 | 0 | 0 | 58.908 | 56.891 | 48.471 | 22.211 | 0 | 0 | 57.699 | 35.246 | [5 empty] | 0 | 0.385 | 63 | 1.9261 | 1.7557 | 1.0346 | 0.89552 | 0.86016 | 44.6573
2005-10-31 | 11:10 | 0 | 21.53 | 0 | 2 | 0 | 28.081 | 28.491 | 27.768 | 27.647 | 16.302 | 24.877 | 15.981 | 0 | 0 | 58.902 | 56.907 | 48.601 | 22.3 | 0 | 0 | 57.713 | 35.215 | [5 empty] | 0 | 0.434 | 64 | 1.9427 | 1.7715 | 1.0352 | 0.89552 | 0.87594 | 45.0879
2005-10-31 | 11:11 | 0 | 21.537 | 0 | 3 | 0 | 28.354 | 28.425 | 27.775 | 27.655 | 22.935 | 24.933 | 16.038 | 0 | 0 | 58.865 | 56.868 | 48.517 | 22.211 | 0 | 0 | 57.676 | 35.27 | [5 empty] | 0 | 0.699 | 65 | 1.9261 | 1.7557 | 1.0346 | 0.89552 | 0.86016 | 44.6573
2005-10-31 | 11:12 | 0 | 21.537 | 0 | 2 | 1 | 44.059 | 28.378 | 27.655 | 27.704 | 22.427 | 24.837 | 16.064 | 0 | 0 | 58.886 | 56.825 | 48.562 | 22.187 | 0 | 0 | 57.699 | 35.246 | [5 empty] | 0 | 16.355 | 66 | 1.9186 | 1.7485 | 1.0343 | 0.89552 | 0.85296 | 44.4584
2005-10-31 | 11:13 | 0 | 21.481 | 0 | 2 | 0 | 45.873 | 38.669 | 27.574 | 27.598 | 22.371 | 24.852 | 16.006 | 2 | 0 | 58.835 | 56.795 | 48.394 | 22.179 | 0 | 0 | 57.669 | 35.215 | [5 empty] | 0 | 18.275 | 0 | 1.9355 | 1.7645 | 1.035 | 0.89552 | 0.86902 | 44.8999
2005-10-31 | 11:14 | 1 | 21.53 | 0 | 2 | 0 | 45.85 | 45.184 | 27.718 | 27.552 | 22.805 | 24.926 | 16.056 | 1 | 0 | 58.856 | 56.795 | 48.394 | 22.204 | 0 | 0 | 57.669 | 35.191 | [5 empty] | 21.53 | 18.298 | 1 | 1.9209 | 1.7507 | 2.1388 | 2 | -0.2493 | -12.9784
2005-10-31 | 11:15 | 0 | 21.53 | 0 | 2 | 0 | 45.803 | 45.85 | 27.694 | 27.478 | 22.949 | 24.852 | 16.031 | 1 | 0 | 58.835 | 56.795 | 48.394 | 22.226 | 0 | 0 | 57.713 | 35.191 | [5 empty] | 0 | 18.325 | 2 | 1.9282 | 1.7576 | 2.1391 | 2 | -0.24238 | -12.5705
2005-10-31 | 11:16 | 0 | 21.537 | 0 | 2 | 0 | 45.833 | 45.88 | 27.969 | 27.606 | 22.957 | 24.958 | 16.114 | 1 | 0 | 58.886 | 56.802 | 48.424 | 22.211 | 0 | 0 | 57.722 | 35.175 | [5 empty] | 0 | 18.227 | 3 | 1.904 | 1.7346 | 2.1382 | 2 | -0.26536 | -13.9367
2005-10-31 | 11:17 | 0 | 21.537 | 0 | 2 | 0 | 46.018 | 45.857 | 28.015 | 27.606 | 23.077 | 24.884 | 16.139 | 2 | 0 | 58.865 | 56.802 | 48.471 | 22.211 | 0 | 0 | 57.722 | 35.199 | [5 empty] | 0 | 18.412 | 4 | 1.8967 | 1.7277 | 2.1379 | 2 | -0.27228 | -14.355
2005-10-31 | 11:18 | 0 | 21.505 | 0 | 2 | 0 | 46.148 | 46.032 | 27.961 | 27.743 | 23.214 | 24.828 | 16.129 | 1 | 0 | 58.813 | 56.75 | 48.487 | 22.204 | 0 | 0 | 57.669 | 35.191 | [5 empty] | 0 | 18.405 | 5 | 1.8996 | 1.7305 | 2.138 | 2 | -0.26951 | -14.1873
2005-10-31 | 11:19 | 0 | 21.537 | 1 | 2 | 0 | 46.109 | 46.314 | 28.089 | 27.824 | 23.415 | 24.859 | 16.187 | 1 | 0 | 58.908 | 56.802 | 48.494 | 22.236 | 0 | 0 | 57.722 | 35.246 | [5 empty] | 0 | 18.285 | 6 | 1.8827 | 1.7144 | 2.1373 | 2 | -0.28556 | -15.1673
2005-10-31 | 11:20 | 1 | 21.537 | 0 | 2 | 0 | 46.155 | 46.361 | 28.233 | 27.871 | 23.896 | 24.884 | 16.139 | 1 | 0 | 58.931 | 56.846 | 48.632 | 22.211 | 0 | 0 | 57.699 | 35.246 | [5 empty] | 21.537 | 18.284 | 7 | 1.8967 | 1.7277 | 2.1379 | 2 | -0.27228 | -14.355
2005-10-31 | 11:21 | 0 | 21.505 | 0 | 2 | 0 | 46.4 | 46.354 | 28.322 | 28.081 | 24.033 | 24.901 | 16.081 | 1 | 0 | 58.924 | 56.772 | 48.555 | 22.204 | 0 | 0 | 57.669 | 35.215 | [5 empty] | 0 | 18.319 | 8 | 1.9136 | 1.7438 | 2.1385 | 2 | -0.25622 | -13.3894
2005-10-31 | 11:22 | 0 | 21.505 | 0 | 2 | 0 | 46.72 | 46.445 | 28.393 | 28.177 | 24.227 | 24.901 | 16.031 | 2 | 0 | 58.879 | 56.772 | 48.508 | 22.204 | 0 | 0 | 57.624 | 35.167 | [5 empty] | 0 | 18.543 | 9 | 1.9282 | 1.7576 | 2.1391 | 2 | -0.24238 | -12.5705
2005-10-31 | 11:23 | 0 | 21.537 | 0 | 2 | 0 | 47.325 | 46.727 | 28.474 | 28.113 | 24.45 | 24.933 | 16.064 | 1 | 0 | 58.977 | 56.802 | 48.562 | 22.211 | 0 | 0 | 57.676 | 35.199 | [5 empty] | 0 | 19.212 | 10 | 1.9186 | 1.7485 | 2.1387 | 2 | -0.25152 | -13.1096
2005-10-31 | 11:24 | 0 | 21.537 | 0 | 2 | 0 | 47.486 | 47.255 | 28.569 | 28.16 | 24.573 | 24.958 | 16.038 | 1 | 0 | 58.977 | 56.846 | 48.585 | 22.236 | 0 | 0 | 57.653 | 35.175 | [5 empty] | 0 | 19.326 | 11 | 1.9261 | 1.7557 | 2.1391 | 2 | -0.24432 | -12.6844
2005-10-31 | 11:25 | 1 | 21.562 | 0 | 2 | 0 | 47.553 | 47.668 | 28.763 | 28.28 | 24.715 | 24.982 | 16.013 | 1 | 0 | 58.997 | 56.825 | 48.562 | 22.236 | 0 | 0 | 57.699 | 35.199 | [5 empty] | 21.562 | 19.273 | 12 | 1.9334 | 1.7626 | 2.1393 | 2 | -0.2374 | -12.2787
2005-10-31 | 11:26 | 0 | 21.481 | 0 | 2 | 0 | 47.591 | 47.752 | 29.067 | 28.442 | 24.852 | 25.117 | 16.129 | 1 | 0 | 58.968 | 56.795 | 48.464 | 22.204 | 0 | 0 | 57.669 | 35.191 | [5 empty] | 0 | 19.149 | 13 | 1.8996 | 1.7305 | 2.138 | 2 | -0.26951 | -14.1873
2005-10-31 | 11:27 | 0 | 21.547 | 0 | 2 | 0 | 48.296 | 47.815 | 29.616 | 28.868 | 25.087 | 24.989 | 16.023 | 2 | 0 | 58.984 | 56.788 | 48.524 | 22.197 | 0 | 0 | 57.662 | 35.184 | [5 empty] | 0 | 19.428 | 14 | 1.9305 | 1.7598 | 2.1392 | 2 | -0.24017 | -12.4406
2005-10-31 | 11:28 | 0 | 21.498 | 1 | 2 | 0 | 48.319 | 48.114 | 30.193 | 29.158 | 25.232 | 25.087 | 16.023 | 1 | 0 | 59.007 | 56.811 | 48.548 | 22.197 | 0 | 0 | 57.662 | 35.139 | [5 empty] | 0 | 19.161 | 15 | 1.9305 | 1.7598 | 2.1392 | 2 | -0.24017 | -12.4406
2005-10-31 | 11:29 | 0 | 21.522 | 0 | 2 | 0 | 48.641 | 48.548 | 30.676 | 29.616 | 25.423 | 25.159 | 16.049 | 1 | 0 | 59.029 | 56.811 | 48.618 | 22.221 | 0 | 0 | 57.617 | 35.139 | [5 empty] | 0 | 19.025 | 16 | 1.9229 | 1.7526 | 2.1389 | 2 | -0.24736 | -12.8639
2005-10-31 | 11:30 | 0 | 21.522 | 0 | 1 | 0 | 49.166 | 48.755 | 31.156 | 30.193 | 25.593 | 25.11 | 16.124 | 1 | 0 | 59.052 | 56.832 | 48.571 | 22.221 | 0 | 0 | 57.662 | 35.139 | [5 empty] | 0 | 18.973 | 17 | 1.9011 | 1.7319 | 2.138 | 2 | -0.26812 | -14.1036
2005-10-31 | 11:31 | 0 | 21.49 | 0 | 2 | 0 | 45.17 | 49 | 31.632 | 30.764 | 23.947 | 25.247 | 16.016 | 1 | 0 | 59.045 | 56.802 | 48.517 | 22.165 | 0 | 0 | 57.587 | 35.129 | [5 empty] | 0 | 14.406 | 18 | 1.9325 | 1.7618 | 2.1393 | 2 | -0.23823 | -12.3272
2005-10-31 | 11:32 | 0 | 21.466 | 0 | 2 | 0 | 36.423 | 49.435 | 31.799 | 31.198 | 22.334 | 25.247 | 16.016 | 1 | 0 | 59.068 | 56.782 | 48.541 | 22.165 | 0 | 0 | 57.564 | 35.108 | [5 empty] | 0 | 5.225 | 19 | 1.9325 | 1.7618 | 2.1393 | 2 | -0.23823 | -12.3272
2005-10-31 | 11:33 | 0 | 21.466 | 0 | 2 | 0 | 33.979 | 42.791 | 32.041 | 31.534 | 21.226 | 25.247 | 16.041 | 0 | 0 | 59.023 | 56.759 | 48.564 | 22.14 | 0 | 0 | 57.61 | 35.108 | [5 empty] | 0 | 2.445 | 20 | 1.9253 | 1.7549 | 2.139 | 2 | -0.24515 | -12.7333
2005-10-31 | 11:34 | 0 | 21.498 | 0 | 1 | 0 | 33.328 | 36.782 | 32.095 | 31.735 | 20.561 | 25.232 | 16.124 | 0 | 0 | 59.118 | 56.832 | 48.594 | 22.221 | 0 | 0 | 57.594 | 35.256 | [5 empty] | 0 | 1.593 | 21 | 1.9011 | 1.7319 | 2.138 | 2 | -0.26812 | -14.1036
2005-10-31 | 11:35 | 0 | 21.49 | 0 | 2 | 0 | 33.086 | 34.636 | 32.041 | 31.799 | 20.141 | 25.176 | 16.066 | 0 | 0 | 59.045 | 56.782 | 48.611 | 22.211 | 0 | 0 | 57.521 | 35.084 | [5 empty] | 0 | 1.287 | 22 | 1.918 | 1.7479 | 2.1387 | 2 | -0.25207 | -13.1424
2005-10-31 | 11:36 | 0 | 21.473 | 0 | 2 | 0 | 33 | 33.916 | 32.024 | 31.929 | 19.704 | 25.159 | 15.998 | 0 | 0 | 59.052 | 56.788 | 48.662 | 22.221 | 0 | 0 | 57.528 | 35.139 | [5 empty] | 0 | 1.071 | 23 | 1.9378 | 1.7668 | 2.1395 | 2 | -0.23325 | -12.0368
2005-10-31 | 11:37 | 0 | 21.473 | 0 | 2 | 0 | 32.929 | 33.682 | 31.904 | 31.929 | 19.136 | 25.208 | 15.951 | 0 | 0 | 59.052 | 56.788 | 48.732 | 22.197 | 0 | 0 | 57.505 | 35.16 | [5 empty] | 0 | 1 | 24 | 1.9515 | 1.7798 | 2.1401 | 2 | -0.22024 | -11.2857
2005-10-31 | 11:38 | 0 | 21.498 | 0 | 1 | 0 | 32.859 | 33.493 | 31.735 | 32.095 | 18.962 | 25.159 | 15.852 | 1 | 0 | 59.029 | 56.788 | 48.732 | 22.197 | 0 | 0 | 57.551 | 35.184 | [5 empty] | 0 | 0.764 | 25 | 1.9803 | 1.8072 | 2.1412 | 2 | -0.19283 | -9.7376
2005-10-31 | 11:39 | 0 | 21.466 | 1 | 2 | 0 | 32.663 | 33.321 | 31.414 | 31.774 | 18.585 | 25.176 | 15.82 | 0 | 0 | 59 | 56.759 | 48.611 | 22.189 | 0 | 0 | 57.521 | 35.129 | [5 empty] | 0 | 0.889 | 26 | 1.9896 | 1.816 | 2.1416 | 2 | -0.18398 | -9.2468
2005-10-31 | 11:40 | 0 | 21.498 | 0 | 2 | 0 | 32.601 | 33.187 | 31.181 | 31.639 | 18.296 | 25.328 | 15.802 | 0 | 0 | 59.029 | 56.766 | 48.641 | 22.197 | 0 | 0 | 57.482 | 35.139 | [5 empty] | 0 | 0.962 | 27 | 1.9949 | 1.821 | 2.1418 | 2 | -0.17899 | -8.9728
2005-10-31 | 11:41 | 1 | 21.441 | 0 | 2 | 0 | 40.559 | 33.039 | 30.788 | 31.487 | 24.837 | 25.2 | 15.82 | 0 | 0 | 58.934 | 56.713 | 48.632 | 22.189 | 0 | 0 | 57.475 | 35.084 | [5 empty] | 21.441 | 9.072 | 28 | 1.9896 | 1.816 | 2.1416 | 2 | -0.18398 | -9.2468
2005-10-31 | 11:42 | 0 | 21.466 | 0 | 1 | 1 | 45.49 | 33.062 | 30.546 | 31.124 | 22.309 | 25.176 | 15.795 | 0 | 0 | 58.954 | 56.736 | 48.587 | 22.189 | 0 | 0 | 57.453 | 35.108 | [5 empty] | 0 | 14.366 | 29 | 1.9969 | 1.8229 | 2.1419 | 2 | -0.17706 | -8.8666
2005-10-31 | 11:43 | 0 | 21.498 | 0 | 2 | 0 | 36.265 | 43.011 | 29.977 | 30.771 | 20.512 | 25.208 | 15.951 | 1 | 0 | 58.94 | 56.743 | 48.662 | 22.221 | 0 | 0 | 57.459 | 35.16 | [5 empty] | 0 | 5.494 | 0 | 1.9515 | 1.7798 | 2.1401 | 2 | -0.22024 | -11.2857
2005-10-31 | 11:44 | 0 | 21.498 | 0 | 2 | 0 | 33.259 | 42.611 | 29.687 | 30.362 | 19.382 | 25.328 | 15.9 | 0 | 0 | 58.895 | 56.743 | 48.641 | 22.221 | 0 | 0 | 57.416 | 35.184 | [5 empty] | 0 | 2.897 | 1 | 1.9663 | 1.7939 | 1.1752 | 1.0345 | 0.7594 | 38.6202
2005-10-31 | 11:45 | 0 | 21.441 | 0 | 2 | 0 | 31.992 | 36.186 | 29.366 | 29.849 | 18.98 | 25.2 | 15.868 | 0 | 0 | 58.934 | 56.69 | 48.564 | 22.165 | 0 | 0 | 57.341 | 35.153 | [5 empty] | 0 | 2.143 | 2 | 1.9756 | 1.8027 | 1.1755 | 1.0345 | 0.76825 | 38.8864
2005-10-31 | 11:46 | 0 | 21.441 | 0 | 1 | 0 | 31.343 | 33.603 | 29.077 | 29.486 | 18.759 | 25.176 | 15.868 | 0 | 0 | 58.865 | 56.668 | 48.564 | 22.211 | 0 | 0 | 57.386 | 35.153 | [5 empty] | 0 | 1.857 | 3 | 1.9756 | 1.8027 | 1.1755 | 1.0345 | 0.76825 | 38.8864
2005-10-31 | 11:47 | 0 | 21.449 | 0 | 2 | 0 | 30.771 | 32.48 | 28.964 | 29.229 | 18.492 | 25.205 | 15.85 | 1 | 0 | 58.826 | 56.652 | 48.524 | 22.148 | 0 | 0 | 57.393 | 35.091 | [5 empty] | 0 | 1.542 | 4 | 1.9809 | 1.8077 | 1.1758 | 1.0345 | 0.77324 | 39.035
2005-10-31 | 11:48 | 0 | 21.456 | 0 | 1 | 0 | 30.44 | 31.862 | 28.876 | 29.092 | 18.155 | 25.092 | 15.883 | 0 | 0 | 58.835 | 56.661 | 48.601 | 22.204 | 0 | 0 | 57.423 | 35.144 | [5 empty] | 0 | 1.348 | 5 | 1.9713 | 1.7986 | 1.1754 | 1.0345 | 0.7641 | 38.7619
2005-10-31 | 11:49 | 0 | 21.424 | 0 | 2 | 0 | 29.999 | 31.252 | 28.819 | 28.891 | 17.999 | 25.183 | 15.973 | 0 | 0 | 58.826 | 56.631 | 48.524 | 22.148 | 0 | 0 | 57.437 | 35.091 | [5 empty] | 0 | 1.108 | 6 | 1.9451 | 1.7737 | 1.1743 | 1.0345 | 0.73919 | 38.0035
2005-10-31 | 11:50 | 0 | 21.424 | 0 | 2 | 0 | 29.71 | 30.842 | 28.626 | 28.748 | 17.728 | 25.085 | 16.074 | 0 | 0 | 58.806 | 56.608 | 48.524 | 22.172 | 0 | 0 | 57.437 | 35.091 | [5 empty] | 0 | 0.962 | 7 | 1.9157 | 1.7457 | 1.1731 | 1.0345 | 0.71123 | 37.1275
2005-10-31 | 11:51 | 0 | 21.449 | 1 | 1 | 0 | 29.494 | 30.433 | 28.555 | 28.77 | 17.554 | 25.014 | 16.121 | 0 | 0 | 58.76 | 56.585 | 48.501 | 22.194 | 0 | 0 | 57.459 | 35.091 | [5 empty] | 0 | 0.724 | 8 | 1.902 | 1.7327 | 1.1726 | 1.0345 | 0.69822 | 36.7107
2005-10-31 | 11:52 | 0 | 21.449 | 0 | 2 | 0 | 33.328 | 30.097 | 28.53 | 28.579 | 24.17 | 25.061 | 16.197 | 0 | 0 | 58.737 | 56.608 | 48.571 | 22.194 | 0 | 0 | 57.414 | 35.091 | [5 empty] | 0 | 4.749 | 9 | 1.8798 | 1.7117 | 1.1717 | 1.0345 | 0.67719 | 36.0238
2005-10-31 | 11:53 | 0 | 21.449 | 0 | 2 | 0 | 45.773 | 29.903 | 28.41 | 28.459 | 22.148 | 25.014 | 16.245 | 0 | 0 | 58.737 | 56.608 | 48.478 | 22.172 | 0 | 0 | 57.482 | 35.067 | [5 empty] | 0 | 17.314 | 10 | 1.8659 | 1.6984 | 1.1711 | 1.0345 | 0.6639 | 35.5816
2005-10-31 | 11:54 | 0 | 21.449 | 0 | 1 | 0 | 34.785 | 38.239 | 28.361 | 28.434 | 20.416 | 25.014 | 16.222 | 1 | 0 | 58.692 | 56.563 | 48.548 | 22.172 | 0 | 0 | 57.393 | 35.067 | [5 empty] | 0 | 6.351 | 11 | 1.8726 | 1.7048 | 1.1714 | 1.0345 | 0.67027 | 35.7943
2005-10-31 | 11:55 | 0 | 21.449 | 0 | 2 | 0 | 30.987 | 41.765 | 28.339 | 28.339 | 19.407 | 24.989 | 16.121 | 0 | 0 | 58.692 | 56.585 | 48.571 | 22.194 | 0 | 0 | 57.414 | 35.067 | [5 empty] | 0 | 2.648 | 12 | 1.902 | 1.7327 | 1.1726 | 1.0345 | 0.69822 | 36.7107
2005-10-31 | 11:56 | 0 | 21.4 | 0 | 2 | 0 | 29.783 | 34.455 | 28.361 | 28.216 | 18.987 | 24.989 | 16.049 | 0 | 0 | 58.671 | 56.54 | 48.571 | 22.172 | 0 | 0 | 57.37 | 35.043 | [5 empty] | 0 | 1.567 | 13 | 1.9229 | 1.7526 | 1.1734 | 1.0345 | 0.71815 | 37.3468
2005-10-31 | 11:57 | 0 | 21.449 | 0 | 2 | 0 | 29.349 | 31.325 | 28.29 | 28.361 | 18.716 | 24.94 | 15.973 | 0 | 0 | 58.625 | 56.517 | 48.457 | 22.194 | 0 | 0 | 57.37 | 35.067 | [5 empty] | 0 | 0.988 | 14 | 1.9451 | 1.7737 | 1.1743 | 1.0345 | 0.73919 | 38.0035
2005-10-31 | 11:58 | 0 | 21.424 | 0 | 1 | 0 | 29.06 | 30.242 | 28.194 | 28.265 | 18.394 | 25.038 | 15.925 | 0 | 0 | 58.692 | 56.54 | 48.433 | 22.148 | 0 | 0 | 57.393 | 35.091 | [5 empty] | 0 | 0.795 | 15 | 1.959 | 1.787 | 1.1749 | 1.0345 | 0.75248 | 38.4105
2005-10-31 | 11:59 | 0 | 21.449 | 0 | 2 | 0 | 28.964 | 29.808 | 28.096 | 28.339 | 18.246 | 24.94 | 15.825 | 1 | 0 | 58.648 | 56.517 | 48.457 | 22.172 | 0 | 0 | 57.37 | 35.091 | [5 empty] | 0 | 0.625 | 16 | 1.9882 | 1.8146 | 1.176 | 1.0345 | 0.78016 | 39.2402
2005-10-31 | 12:00 | 0 | 21.449 | 0 | 1 | 0 | 28.891 | 29.567 | 28.096 | 28.17 | 18.047 | 25.014 | 15.825 | 0 | 0 | 58.671 | 56.517 | 48.478 | 22.194 | 0 | 0 | 57.348 | 35.091 | [5 empty] | 0 | 0.721 | 17 | 1.9882 | 1.8146 | 1.176 | 1.0345 | 0.78016 | 39.2402
2005-10-31 | 12:01 | 0 | 21.449 | 0 | 2 | 0 | 28.819 | 29.374 | 28.096 | 28.265 | 17.876 | 24.918 | 15.825 | 0 | 0 | 58.625 | 56.496 | 48.524 | 22.194 | 0 | 0 | 57.302 | 35.091 | [5 empty] | 0 | 0.554 | 18 | 1.9882 | 1.8146 | 1.176 | 1.0345 | 0.78016 | 39.2402
2005-10-31 | 12:02 | 0 | 21.449 | 1 | 2 | 0 | 28.675 | 29.204 | 27.976 | 28.05 | 17.728 | 24.94 | 15.825 | 0 | 0 | 58.625 | 56.496 | 48.478 | 22.219 | 0 | 0 | 57.236 | 35.043 | [5 empty] | 0 | 0.625 | 19 | 1.9882 | 1.8146 | 1.176 | 1.0345 | 0.78016 | 39.2402
2005-10-31 | 12:03 | 0 | 21.449 | 0 | 2 | 0 | 29.71 | 29.109 | 27.951 | 27.951 | 24.121 | 24.965 | 15.802 | 0 | 0 | 58.625 | 56.474 | 48.548 | 22.172 | 0 | 0 | 57.147 | 35.043 | [5 empty] | 0 | 1.759 | 20 | 1.9949 | 1.821 | 1.1763 | 1.0345 | 0.78652 | 39.4276
2005-10-31 | 12:04 | 0 | 21.417 | 0 | 1 | 0 | 46.431 | 28.981 | 27.799 | 27.944 | 22.067 | 24.908 | 15.792 | 0 | 0 | 58.55 | 56.421 | 48.403 | 22.162 | 0 | 0 | 57.206 | 34.988 | [5 empty] | 0 | 18.487 | 21 | 1.9978 | 1.8238 | 1.1764 | 1.0345 | 0.78929 | 39.5086
2005-10-31 | 12:05 | 0 | 21.449 | 0 | 2 | 0 | 35.16 | 35.77 | 27.785 | 27.88 | 20.392 | 24.965 | 15.9 | 1 | 0 | 58.557 | 56.496 | 48.363 | 22.194 | 0 | 0 | 57.236 | 34.995 | [5 empty] | 0 | 7.28 | 22 | 1.9663 | 1.7939 | 1.1752 | 1.0345 | 0.7594 | 38.6202
2005-10-31 | 12:06 | 0 | 21.473 | 0 | 2 | 0 | 30.553 | 41.903 | 27.831 | 27.76 | 19.48 | 25.085 | 15.85 | 0 | 0 | 58.568 | 56.462 | 48.398 | 22.16 | 0 | 0 | 57.27 | 35.055 | [5 empty] | 0 | 2.793 | 23 | 1.9809 | 1.8077 | 1.1758 | 1.0345 | 0.77324 | 39.035
2005-10-31 | 12:07 | 0 | 21.461 | 0 | 2 | 0 | 29.192 | 34.163 | 27.868 | 27.893 | 18.852 | 25.051 | 15.837 | 0 | 0 | 58.548 | 56.416 | 48.398 | 22.206 | 0 | 0 | 57.247 | 35.055 | [5 empty] | 0 | 1.299 | 24 | 1.9847 | 1.8113 | 1.1759 | 1.0345 | 0.77684 | 39.1419
2005-10-31 | 12:08 | 0 | 21.405 | 0 | 2 | 0 | 28.751 | 30.727 | 27.885 | 27.836 | 18.424 | 24.97 | 15.78 | 0 | 0 | 58.539 | 56.432 | 48.436 | 22.152 | 0 | 0 | 57.195 | 35 | [5 empty] | 0 | 0.915 | 25 | 2.0013 | 1.8271 | 1.1766 | 1.0345 | 0.79261 | 39.6056
2005-10-31 | 12:09 | 0 | 21.429 | 0 | 1 | 0 | 28.51 | 29.57 | 27.907 | 27.741 | 18.102 | 25.09 | 15.78 | 0 | 0 | 58.562 | 56.41 | 48.345 | 22.152 | 0 | 0 | 57.217 | 35 | [5 empty] | 0 | 0.769 | 26 | 2.0013 | 1.8271 | 1.1766 | 1.0345 | 0.79261 | 39.6056
2005-10-31 | 12:10 | 0 | 21.461 | 0 | 2 | 0 | 28.373 | 29.121 | 27.964 | 27.772 | 17.911 | 25.122 | 15.764 | 0 | 0 | 58.591 | 56.416 | 48.398 | 22.184 | 0 | 0 | 57.135 | 34.983 | [5 empty] | 0 | 0.601 | 27 | 2.0059 | 1.8315 | 1.1768 | 1.0345 | 0.79704 | 39.7344
2005-10-31 | 12:11 | 0 | 21.454 | 0 | 2 | 0 | 28.295 | 28.849 | 27.812 | 27.763 | 17.73 | 25.019 | 15.732 | 0 | 0 | 58.495 | 56.387 | 48.415 | 22.175 | 0 | 0 | 57.083 | 34.952 | [5 empty] | 0 | 0.532 | 28 | 2.0152 | 1.8404 | 1.1771 | 1.0345 | 0.8059 | 39.9902
2005-10-31 | 12:12 | 0 | 21.478 | 0 | 2 | 0 | 28.197 | 28.775 | 27.741 | 27.716 | 17.708 | 24.994 | 15.707 | 1 | 0 | 58.495 | 56.364 | 48.345 | 22.152 | 0 | 0 | 57.106 | 34.952 | [5 empty] | 0 | 0.481 | 29 | 2.0225 | 1.8473 | 1.1774 | 1.0345 | 0.81282 | 40.1884
2005-10-31 | 12:13 | 0 | 21.429 | 0 | 2 | 0 | 28.172 | 28.631 | 27.787 | 27.667 | 17.386 | 24.994 | 15.805 | 0 | 0 | 58.495 | 56.364 | 48.3 | 22.175 | 0 | 0 | 57.083 | 34.952 | [5 empty] | 0 | 0.505 | 30 | 1.994 | 1.8202 | 1.1763 | 1.0345 | 0.78569 | 39.4032
2005-10-31 | 12:14 | 0 | 21.461 | 1 | 1 | 0 | 28.204 | 28.567 | 27.748 | 27.603 | 23.604 | 24.977 | 15.837 | 0 | 0 | 58.525 | 56.373 | 48.331 | 22.16 | 0 | 0 | 57.067 | 34.962 | [5 empty] | 0 | 0.601 | 31 | 1.9847 | 1.8113 | 1.1759 | 1.0345 | 0.77684 | 39.1419
2005-10-31 | 12:15 | 0 | 21.405 | 0 | 2 | 0 | 45.135 | 28.415 | 27.692 | 27.667 | 22.054 | 24.921 | 15.78 | 0 | 0 | 58.45 | 56.298 | 48.345 | 22.152 | 0 | 0 | 57.037 | 34.931 | [5 empty] | 0 | 17.468 | 32 | 2.0013 | 1.8271 | 1.1766 | 1.0345 | 0.79261 | 39.6056
2005-10-31 | 12:16 | 0 | 21.461 | 0 | 2 | 0 | 34.725 | 35.337 | 27.844 | 27.652 | 20.426 | 25.122 | 15.863 | 0 | 0 | 58.502 | 56.35 | 48.352 | 22.231 | 0 | 0 | 57.113 | 34.962 | [5 empty] | 0 | 7.073 | 33 | 1.9771 | 1.8041 | 1.1756 | 1.0345 | 0.76964 | 38.9278
2005-10-31 | 12:17 | 0 | 21.429 | 0 | 2 | 0 | 30.077 | 40.31 | 27.741 | 27.571 | 19.337 | 24.97 | 15.83 | 1 | 0 | 58.45 | 56.321 | 48.3 | 22.128 | 0 | 0 | 57.106 | 34.883 | [5 empty] | 0 | 2.506 | 34 | 1.9867 | 1.8133 | 1.176 | 1.0345 | 0.77877 | 39.1993
2005-10-31 | 12:18 | 0 | 21.405 | 0 | 2 | 0 | 28.849 | 32.814 | 27.836 | 27.62 | 18.671 | 25.019 | 15.83 | 0 | 0 | 58.427 | 56.298 | 48.321 | 22.152 | 0 | 0 | 57.172 | 34.907 | [5 empty] | 0 | 1.229 | 35 | 1.9867 | 1.8133 | 1.176 | 1.0345 | 0.77877 | 39.1993
2005-10-31 | 12:19 | 0 | 21.405 | 0 | 2 | 0 | 28.415 | 29.979 | 27.763 | 27.62 | 18.201 | 24.921 | 15.805 | 0 | 0 | 58.404 | 56.275 | 48.345 | 22.152 | 0 | 0 | 57.195 | 34.931 | [5 empty] | 0 | 0.795 | 36 | 1.994 | 1.8202 | 1.1763 | 1.0345 | 0.78569 | 39.4032
2005-10-31 | 12:20 | 0 | 21.405 | 0 | 2 | 0 | 28.246 | 29.16 | 27.763 | 27.716 | 17.929 | 24.921 | 15.78 | 0 | 0 | 58.404 | 56.275 | 48.321 | 22.175 | 0 | 0 | 57.126 | 34.907 | [5 empty] | 0 | 0.53 | 37 | 2.0013 | 1.8271 | 1.1766 | 1.0345 | 0.79261 | 39.6056
2005-10-31 | 12:21 | 0 | 21.429 | 0 | 2 | 0 | 28.126 | 28.8 | 27.836 | 27.62 | 17.756 | 24.921 | 15.805 | 0 | 0 | 58.427 | 56.298 | 48.3 | 22.152 | 0 | 0 | 57.126 | 34.931 | [5 empty] | 0 | 0.506 | 38 | 1.994 | 1.8202 | 1.1763 | 1.0345 | 0.78569 | 39.4032
2005-10-31 | 12:22 | 0 | 21.405 | 0 | 2 | 0 | 28.126 | 28.582 | 27.741 | 27.787 | 17.683 | 24.825 | 15.805 | 0 | 0 | 58.384 | 56.252 | 48.321 | 22.152 | 0 | 0 | 57.037 | 34.952 | [5 empty] | 0 | 0.339 | 39 | 1.994 | 1.8202 | 1.1763 | 1.0345 | 0.78569 | 39.4032
2005-10-31 | 12:23 | 0 | 21.405 | 0 | 2 | 0 | 28.03 | 28.486 | 27.642 | 27.763 | 17.509 | 24.85 | 15.805 | 0 | 0 | 58.404 | 56.252 | 48.321 | 22.152 | 0 | 0 | 56.994 | 34.976 | [5 empty] | 0 | 0.267 | 40 | 1.994 | 1.8202 | 1.1763 | 1.0345 | 0.78569 | 39.4032
2005-10-31 | 12:24 | 0 | 21.405 | 0 | 2 | 0 | 28.005 | 28.439 | 27.642 | 27.62 | 17.459 | 24.825 | 15.805 | 0 | 0 | 58.384 | 56.252 | 48.277 | 22.152 | 0 | 0 | 56.994 | 34.976 | [5 empty] | 0 | 0.385 | 41 | 1.994 | 1.8202 | 1.1763 | 1.0345 | 0.78569 | 39.4032
2005-10-31 | 12:25 | 1 | 21.405 | 0 | 2 | 0 | 28.005 | 28.317 | 27.642 | 27.667 | 22.103 | 24.776 | 15.88 | 0 | 0 | 58.384 | 56.252 | 48.345 | 22.175 | 0 | 0 | 57.014 | 34.976 | [5 empty] | 21.405 | 0.338 | 42 | 1.9721 | 1.7994 | 1.1754 | 1.0345 | 0.76493 | 38.7869
2005-10-31 | 12:26 | 0 | 21.429 | 1 | 2 | 0 | 43.602 | 28.317 | 27.642 | 27.547 | 23.717 | 24.776 | 15.855 | 1 | 0 | 58.338 | 56.209 | 48.254 | 22.128 | 0 | 0 | 57.014 | 34.931 | [5 empty] | 0 | 16.055 | 43 | 1.9794 | 1.8063 | 1.1757 | 1.0345 | 0.77185 | 38.9938
2005-10-31 | 12:27 | 0 | 21.422 | 0 | 2 | 0 | 45.999 | 35.065 | 27.589 | 27.66 | 23.759 | 24.771 | 15.873 | 1 | 0 | 58.354 | 56.202 | 48.317 | 22.17 | 0 | 0 | 56.987 | 34.969 | [5 empty] | 0 | 18.339 | 44 | 1.9742 | 1.8014 | 1.1755 | 1.0345 | 0.76687 | 38.845
2005-10-31 | 12:28 | 0 | 21.517 | 0 | 2 | 0 | 45.931 | 44.762 | 27.564 | 27.613 | 23.685 | 24.771 | 15.923 | 1 | 0 | 58.377 | 56.202 | 48.408 | 22.192 | 0 | 0 | 57.01 | 34.969 | [5 empty] | 0 | 18.318 | 45 | 1.9596 | 1.7875 | 1.1749 | 1.0345 | 0.75303 | 38.4273
2005-10-31 | 12:29 | 0 | 21.422 | 0 | 2 | 0 | 45.908 | 45.84 | 27.589 | 27.539 | 23.614 | 24.771 | 15.923 | 1 | 0 | 58.354 | 56.202 | 48.293 | 22.192 | 0 | 0 | 57.03 | 34.947 | [5 empty] | 0 | 18.369 | 46 | 1.9596 | 1.7875 | 1.1749 | 1.0345 | 0.75303 | 38.4273
2005-10-31 | 12:30 | 1 | 21.446 | 0 | 3 | 0 | 45.817 | 45.908 | 27.758 | 27.493 | 23.398 | 24.891 | 15.923 | 2 | 0 | 58.377 | 56.248 | 48.247 | 22.192 | 0 | 0 | 56.987 | 34.947 | [5 empty] | 21.446 | 18.324 | 47 | 1.9596 | 1.7875 | 1.1749 | 1.0345 | 0.75303 | 38.4273
2005-10-31 | 12:31 | 0 | 21.422 | 0 | 1 | 0 | 45.84 | 45.84 | 27.924 | 27.564 | 23.374 | 24.962 | 15.898 | 1 | 0 | 58.443 | 56.202 | 48.247 | 22.192 | 0 | 0 | 57.01 | 34.947 | [5 empty] | 0 | 18.276 | 48 | 1.9669 | 1.7944 | 1.1752 | 1.0345 | 0.75995 | 38.6369
2005-10-31 | 12:32 | 0 | 21.39 | 0 | 2 | 0 | 46.291 | 45.901 | 27.917 | 27.557 | 23.678 | 24.859 | 15.865 | 1 | 0 | 58.347 | 56.172 | 48.263 | 22.16 | 0 | 0 | 56.957 | 34.916 | [5 empty] | 0 | 18.734 | 49 | 1.9765 | 1.8036 | 1.1756 | 1.0345 | 0.76909 | 38.9112
2005-10-31 | 12:33 | 0 | 21.397 | 0 | 2 | 0 | 46.412 | 46.207 | 27.973 | 27.733 | 23.952 | 24.793 | 15.797 | 1 | 0 | 58.4 | 56.202 | 48.338 | 22.216 | 0 | 0 | 57.03 | 34.969 | [5 empty] | 0 | 18.679 | 50 | 1.9963 | 1.8224 | 1.1764 | 1.0345 | 0.78791 | 39.4681
2005-10-31 | 12:34 | 0 | 21.397 | 0 | 2 | 0 | 46.298 | 46.596 | 28.094 | 27.709 | 24.072 | 24.818 | 15.797 | 1 | 0 | 58.443 | 56.202 | 48.293 | 22.192 | 0 | 0 | 57.03 | 34.993 | [5 empty] | 0 | 18.589 | 51 | 1.9963 | 1.8224 | 1.1764 | 1.0345 | 0.78791 | 39.4681
2005-10-31 | 12:35 | 0 | 21.365 | 1 | 2 | 0 | 46.566 | 46.519 | 28.206 | 27.797 | 24.232 | 24.81 | 15.742 | 1 | 0 | 58.413 | 56.195 | 48.286 | 22.138 | 0 | 0 | 57.001 | 34.938 | [5 empty] | 0 | 18.769 | 52 | 2.0123 | 1.8376 | 1.177 | 1.0345 | 0.80313 | 39.9105
2005-10-31 | 12:36 | 1 | 21.365 | 0 | 2 | 0 | 46.956 | 46.61 | 28.327 | 27.991 | 24.401 | 24.859 | 15.692 | 1 | 0 | 58.413 | 56.195 | 48.354 | 22.184 | 0 | 0 | 56.98 | 34.962 | [5 empty] | 21.365 | 18.965 | 53 | 2.0269 | 1.8515 | 1.1776 | 1.0345 | 0.81697 | 40.3067
2005-10-31 | 12:37 | 0 | 21.397 | 0 | 2 | 0 | 47.168 | 47.031 | 28.383 | 28.094 | 24.722 | 24.938 | 15.797 | 1 | 0 | 58.489 | 56.225 | 48.317 | 22.192 | 0 | 0 | 56.987 | 34.993 | [5 empty] | 0 | 19.074 | 54 | 1.9963 | 1.8224 | 1.1764 | 1.0345 | 0.78791 | 39.4681
2005-10-31 | 12:38 | 0 | 21.397 | 0 | 2 | 0 | 47.628 | 47.283 | 28.432 | 28.189 | 24.891 | 25.058 | 15.724 | 1 | 0 | 58.534 | 56.225 | 48.317 | 22.192 | 0 | 0 | 56.941 | 34.969 | [5 empty] | 0 | 19.439 | 55 | 2.0176 | 1.8426 | 1.1772 | 1.0345 | 0.80811 | 40.0538
2005-10-31 | 12:39 | 0 | 21.39 | 0 | 2 | 0 | 47.85 | 47.528 | 28.545 | 28.28 | 24.98 | 24.906 | 15.742 | 1 | 0 | 58.482 | 56.195 | 48.307 | 22.16 | 0 | 0 | 56.912 | 34.938 | [5 empty] | 0 | 19.57 | 56 | 2.0123 | 1.8376 | 1.177 | 1.0345 | 0.80313 | 39.9105
2005-10-31 | 12:40 | 0 | 21.365 | 0 | 2 | 1 | 47.85 | 47.988 | 28.761 | 28.4 | 25.124 | 25.075 | 15.692 | 1 | 0 | 58.482 | 56.195 | 48.331 | 22.16 | 0 | 0 | 56.912 | 34.938 | [5 empty] | 0 | 19.45 | 57 | 2.0269 | 1.8515 | 1.1776 | 1.0345 | 0.81697 | 40.3067
2005-10-31 | 12:41 | 0 | 21.365 | 0 | 2 | 0 | 47.941 | 48.079 | 29.146 | 28.425 | 25.365 | 25.026 | 15.764 | 2 | 0 | 58.482 | 56.195 | 48.354 | 22.16 | 0 | 0 | 56.912 | 34.962 | [5 empty] | 0 | 19.516 | 0 | 2.0059 | 1.8315 | 1.1768 | 1.0345 | 0.79704 | 39.7344
2005-10-31 | 12:42 | 1 | 21.39 | 0 | 1 | 0 | 48.629 | 48.193 | 29.653 | 28.736 | 25.58 | 24.98 | 15.84 | 1 | 0 | 58.525 | 56.218 | 48.331 | 22.16 | 0 | 0 | 56.912 | 34.986 | [5 empty] | 21.39 | 19.893 | 1 | 1.9838 | 1.8105 | 0.92061 | 0.77922 | 1.0313 | 51.9846
2005-10-31 | 12:43 | 0 | 21.365 | 0 | 2 | 0 | 48.905 | 48.492 | 30.205 | 29.315 | 25.629 | 25.026 | 15.764 | 1 | 0 | 58.525 | 56.195 | 48.354 | 22.184 | 0 | 0 | 56.889 | 34.962 | [5 empty] | 0 | 19.59 | 2 | 2.0059 | 1.8315 | 0.92151 | 0.77922 | 1.0523 | 52.4598
2005-10-31 | 12:44 | 0 | 21.365 | 1 | 2 | 0 | 49.201 | 49.042 | 30.783 | 29.82 | 25.799 | 25.075 | 15.79 | 1 | 0 | 58.637 | 56.238 | 48.331 | 22.209 | 0 | 0 | 56.889 | 34.962 | [5 empty] | 0 | 19.381 | 3 | 1.9984 | 1.8243 | 0.9212 | 0.77922 | 1.0451 | 52.2985
2005-10-31 | 12:45 | 0 | 21.365 | 0 | 2 | 0 | 49.523 | 49.133 | 31.242 | 30.254 | 25.605 | 25.195 | 15.764 | 2 | 0 | 58.616 | 56.238 | 48.331 | 22.16 | 0 | 0 | 56.912 | 34.916 | [5 empty] | 0 | 19.269 | 4 | 2.0059 | 1.8315 | 0.92151 | 0.77922 | 1.0523 | 52.4598
2005-10-31 | 12:46 | 0 | 21.39 | 0 | 2 | 0 | 41.188 | 49.409 | 31.578 | 30.759 | 23.028 | 25.244 | 15.742 | 0 | 0 | 58.594 | 56.218 | 48.492 | 22.184 | 0 | 0 | 56.823 | 34.938 | [5 empty] | 0 | 10.429 | 5 | 2.0123 | 1.8376 | 0.92177 | 0.77922 | 1.0584 | 52.5954
2005-10-31 | 12:47 | 0 | 21.348 | 0 | 1 | 0 | 35.134 | 48.522 | 31.705 | 31.151 | 21.493 | 25.034 | 15.797 | 1 | 0 | 58.6 | 56.202 | 48.361 | 22.143 | 0 | 0 | 56.85 | 34.921 | [5 empty] | 0 | 3.983 | 6 | 1.9963 | 1.8224 | 0.92112 | 0.77922 | 1.0432 | 52.2548
2005-10-31 | 12:48 | 0 | 21.348 | 0 | 2 | 0 | 33.512 | 40.42 | 31.875 | 31.49 | 20.507 | 25.227 | 15.644 | 0 | 0 | 58.594 | 56.175 | 48.333 | 22.138 | 0 | 0 | 56.779 | 34.916 | [5 empty] | 0 | 2.022 | 7 | 2.0409 | 1.8647 | 0.92292 | 0.77922 | 1.0855 | 53.1892
2005-10-31 | 12:49 | 0 | 21.348 | 0 | 2 | 0 | 33.043 | 35.792 | 31.97 | 31.634 | 20.071 | 25.178 | 15.649 | 0 | 0 | 58.6 | 56.202 | 48.405 | 22.167 | 0 | 0 | 56.83 | 34.993 | [5 empty] | 0 | 1.409 | 8 | 2.0394 | 1.8634 | 0.92286 | 0.77922 | 1.0841 | 53.1593
2005-10-31 | 12:50 | 0 | 21.373 | 0 | 2 | 0 | 32.948 | 34.242 | 32.019 | 31.899 | 19.923 | 25.154 | 15.699 | 0 | 0 | 58.6 | 56.202 | 48.499 | 22.167 | 0 | 0 | 56.83 | 34.921 | [5 empty] | 0 | 1.049 | 9 | 2.0249 | 1.8495 | 0.92227 | 0.77922 | 1.0703 | 52.858
2005-10-31 | 12:51 | 0 | 21.348 | 0 | 1 | 0 | 32.807 | 33.677 | 32.019 | 31.899 | 19.749 | 25.154 | 15.699 | 0 | 0 | 58.578 | 56.223 | 48.522 | 22.192 | 0 | 0 | 56.85 | 34.921 | [5 empty] | 0 | 0.908 | 10 | 2.0249 | 1.8495 | 0.92227 | 0.77922 | 1.0703 | 52.858
2005-10-31 | 12:52 | 0 | 21.348 | 0 | 2 | 0 | 32.83 | 33.443 | 31.995 | 32.115 | 19.453 | 25.227 | 15.772 | 0 | 0 | 58.555 | 56.179 | 48.452 | 22.143 | 0 | 0 | 56.873 | 34.921 | [5 empty] | 0 | 0.715 | 11 | 2.0036 | 1.8293 | 0.92141 | 0.77922 | 1.0501 | 52.4103
2005-10-31 | 12:53 | 0 | 21.373 | 0 | 2 | 0 | 32.689 | 33.278 | 31.705 | 31.97 | 19.377 | 25.107 | 15.674 | 1 | 0 | 58.6 | 56.179 | 48.429 | 22.167 | 0 | 0 | 56.896 | 34.969 | [5 empty] | 0 | 0.719 | 12 | 2.0321 | 1.8564 | 0.92257 | 0.77922 | 1.0772 | 53.0092
2005-10-31 | 12:54 | 0 | 21.373 | 0 | 2 | 0 | 32.665 | 33.113 | 31.514 | 31.899 | 19.279 | 25.274 | 15.649 | 0 | 0 | 58.6 | 56.156 | 48.384 | 22.167 | 0 | 0 | 56.873 | 34.969 | [5 empty] | 0 | 0.766 | 13 | 2.0394 | 1.8634 | 0.92286 | 0.77922 | 1.0841 | 53.1593
2005-10-31 | 12:55 | 0 | 21.294 | 0 | 1 | 0 | 32.591 | 32.991 | 31.051 | 31.774 | 26.017 | 25.078 | 15.644 | 0 | 0 | 58.482 | 56.105 | 48.424 | 22.138 | 0 | 0 | 56.823 | 34.988 | [5 empty] | 0 | 0.817 | 14 | 2.0409 | 1.8647 | 0.92292 | 0.77922 | 1.0855 | 53.1892
2005-10-31 | 12:56 | 0 | 21.294 | 1 | 2 | 0 | 47.53 | 32.919 | 30.737 | 31.387 | 25.173 | 25.173 | 15.644 | 0 | 0 | 58.466 | 56.156 | 48.429 | 22.167 | 0 | 0 | 56.807 | 34.969 | [5 empty] | 0 | 16.143 | 15 | 2.0409 | 1.8647 | 0.92292 | 0.77922 | 1.0855 | 53.1892
2005-10-31 | 12:57 | 0 | 21.324 | 0 | 2 | 0 | 41.69 | 34.38 | 30.141 | 31.031 | 22.072 | 25.178 | 15.624 | 0 | 0 | 58.466 | 56.156 | 48.452 | 22.167 | 0 | 0 | 56.873 | 34.993 | [5 empty] | 0 | 10.659 | 16 | 2.0467 | 1.8703 | 0.92316 | 0.77922 | 1.0911 | 53.3083
2005-10-31 | 12:58 | 0 | 21.319 | 0 | 1 | 0 | 34.988 | 45.49 | 29.678 | 30.666 | 20.456 | 25.102 | 15.619 | 1 | 0 | 58.393 | 56.058 | 48.401 | 22.113 | 0 | 0 | 56.823 | 34.964 | [5 empty] | 0 | 4.322 | 17 | 2.0481 | 1.8717 | 0.92322 | 0.77922 | 1.0924 | 53.338
2005-10-31 | 12:59 | 0 | 21.294 | 0 | 2 | 0 | 32.802 | 40.604 | 29.388 | 30.112 | 19.792 | 25.198 | 15.594 | 0 | 0 | 58.438 | 56.058 | 48.377 | 22.138 | 0 | 0 | 56.779 | 34.94 | [5 empty] | 0 | 2.69 | 18 | 2.0554 | 1.8786 | 0.92351 | 0.77922 | 1.0994 | 53.4857
2005-10-31 | 13:00 | 0 | 21.294 | 0 | 2 | 0 | 31.845 | 35.433 | 29.028 | 29.702 | 19.473 | 25.124 | 15.694 | 0 | 0 | 58.461 | 56.105 | 48.377 | 22.162 | 0 | 0 | 56.868 | 34.964 | [5 empty] | 0 | 2.143 | 19 | 2.0263 | 1.8509 | 0.92233 | 0.77922 | 1.0717 | 52.8883
2005-10-31 | 13:01 | 0 | 21.319 | 0 | 1 | 0 | 31.171 | 33.342 | 28.81 | 29.317 | 19.028 | 25.124 | 15.644 | 0 | 0 | 58.347 | 56.082 | 48.356 | 22.162 | 0 | 0 | 56.757 | 34.916 | [5 empty] | 0 | 1.854 | 20 | 2.0409 | 1.8647 | 0.92292 | 0.77922 | 1.0855 | 53.1892
2005-10-31 | 13:02 | 0 | 21.294 | 0 | 2 | 0 | 30.666 | 32.399 | 28.618 | 29.003 | 18.952 | 25.053 | 15.644 | 0 | 0 | 58.347 | 56.082 | 48.447 | 22.138 | 0 | 0 | 56.734 | 34.916 | [5 empty] | 0 | 1.663 | 21 | 2.0409 | 1.8647 | 0.92292 | 0.77922 | 1.0855 | 53.1892
2005-10-31 | 13:03 | 0 | 21.294 | 0 | 1 | 0 | 30.327 | 31.75 | 28.449 | 28.883 | 18.706 | 24.958 | 15.694 | 0 | 0 | 58.347 | 56.014 | 48.356 | 22.162 | 0 | 0 | 56.802 | 34.964 | [5 empty] | 0 | 1.444 | 22 | 2.0263 | 1.8509 | 0.92233 | 0.77922 | 1.0717 | 52.8883
2005-10-31 | 13:04 | 0 | 21.294 | 0 | 2 | 0 | 29.871 | 31.171 | 28.4 | 28.689 | 18.608 | 25.078 | 15.669 | 0 | 0 | 58.347 | 56.014 | 48.356 | 22.162 | 0 | 0 | 56.779 | 34.94 | [5 empty] | 0 | 1.182 | 23 | 2.0336 | 1.8578 | 0.92263 | 0.77922 | 1.0786 | 53.0393
2005-10-31 | 13:05 | 0 | 21.272 | 0 | 1 | 0 | 29.582 | 30.786 | 28.329 | 28.52 | 18.583 | 24.98 | 15.669 | 0 | 0 | 58.304 | 56.014 | 48.356 | 22.138 | 0 | 0 | 56.779 | 34.964 | [5 empty] | 0 | 1.062 | 24 | 2.0336 | 1.8578 | 0.92263 | 0.77922 | 1.0786 | 53.0393
2005-10-31 | 13:06 | 0 | 21.26 | 0 | 2 | 0 | 29.305 | 30.318 | 28.246 | 28.439 | 21.767 | 25.043 | 15.634 | 0 | 0 | 58.295 | 55.991 | 48.219 | 22.116 | 0 | 0 | 56.711 | 34.895 | [5 empty] | 0 | 0.866 | 25 | 2.0438 | 1.8675 | 0.92304 | 0.77922 | 1.0883 | 53.2488
2005-10-31 | 13:07 | 1 | 21.282 | 0 | 1 | 0 | 43.245 | 30.075 | 28.221 | 28.292 | 24.487 | 24.945 | 15.558 | 1 | 0 | 58.267 | 56 | 48.228 | 22.125 | 0 | 0 | 56.72 | 34.928 | [5 empty] | 21.282 | 14.953 | 26 | 2.0659 | 1.8885 | 0.92394 | 0.77922 | 1.1093 | 53.6967
2005-10-31 | 13:08 | 0 | 21.282 | 1 | 2 | 0 | 42.329 | 30.124 | 28.197 | 28.341 | 21.836 | 24.945 | 15.631 | 0 | 0 | 58.224 | 55.977 | 48.228 | 22.15 | 0 | 0 | 56.72 | 34.928 | [5 empty] | 0 | 13.988 | 27 | 2.0447 | 1.8683 | 0.92307 | 0.77922 | 1.0891 | 53.2667
2005-10-31 | 13:09 | 0 | 21.282 | 0 | 2 | 0 | 33.213 | 41.554 | 28.076 | 28.197 | 20.249 | 25.016 | 15.606 | 0 | 0 | 58.244 | 55.953 | 48.228 | 22.15 | 0 | 0 | 56.743 | 34.928 | [5 empty] | 0 | 5.016 | 28 | 2.0519 | 1.8753 | 0.92337 | 0.77922 | 1.096 | 53.4149
2005-10-31 | 13:10 | 0 | 21.275 | 0 | 1 | 0 | 30.403 | 40.442 | 27.971 | 28.189 | 19.402 | 24.864 | 15.624 | 0 | 0 | 58.171 | 55.902 | 48.244 | 22.094 | 0 | 0 | 56.647 | 34.921 | [5 empty] | 0 | 2.214 | 29 | 2.0467 | 1.8703 | 0.92316 | 0.77922 | 1.0911 | 53.3083
2005-10-31 | 13:11 | 0 | 21.331 | 0 | 2 | 0 | 29.496 | 33.823 | 28.099 | 28.099 | 19.065 | 24.847 | 15.707 | 1 | 0 | 58.201 | 55.977 | 48.319 | 22.15 | 0 | 0 | 56.677 | 34.952 | [5 empty] | 0 | 1.397 | 30 | 2.0225 | 1.8473 | 0.92218 | 0.77922 | 1.0681 | 52.8094
2005-10-31 | 13:12 | 0 | 21.307 | 0 | 1 | 0 | 29.087 | 31.063 | 28.172 | 28.003 | 18.744 | 24.872 | 15.707 | 0 | 0 | 58.224 | 55.932 | 48.251 | 22.175 | 0 | 0 | 56.677 | 34.952 | [5 empty] | 0 | 1.084 | 31 | 2.0225 | 1.8473 | 0.92218 | 0.77922 | 1.0681 | 52.8094
2005-10-31 | 13:13 | 0 | 21.356 | 0 | 2 | 0 | 28.846 | 30.124 | 28.027 | 27.954 | 18.57 | 24.872 | 15.656 | 0 | 0 | 58.224 | 55.953 | 48.16 | 22.175 | 0 | 0 | 56.72 | 34.976 | [5 empty] | 0 | 0.892 | 32 | 2.0374 | 1.8614 | 0.92278 | 0.77922 | 1.0822 | 53.1173
2005-10-31 | 13:14 | 0 | 21.275 | 0 | 1 | 0 | 28.719 | 29.56 | 27.9 | 28.045 | 18.266 | 24.769 | 15.649 | 0 | 0 | 58.149 | 55.855 | 48.198 | 22.143 | 0 | 0 | 56.67 | 34.921 | [5 empty] | 0 | 0.674 | 33 | 2.0394 | 1.8634 | 0.92286 | 0.77922 | 1.0841 | 53.1593
2005-10-31 | 13:15 | 0 | 21.275 | 0 | 2 | 0 | 28.599 | 29.369 | 27.9 | 27.947 | 18.266 | 24.791 | 15.624 | 0 | 0 | 58.149 | 55.879 | 48.289 | 22.118 | 0 | 0 | 56.647 | 34.921 | [5 empty] | 0 | 0.652 | 34 | 2.0467 | 1.8703 | 0.92316 | 0.77922 | 1.0911 | 53.3083
2005-10-31 | 13:16 | 0 | 21.275 | 0 | 2 | 0 | 28.525 | 29.104 | 27.851 | 27.971 | 18.092 | 24.769 | 15.697 | 0 | 0 | 58.149 | 55.855 | 48.244 | 22.118 | 0 | 0 | 56.647 | 34.897 | [5 empty] | 0 | 0.554 | 35 | 2.0254 | 1.8501 | 0.9223 | 0.77922 | 1.0708 | 52.8701
2005-10-31 | 13:17 | 0 | 21.25 | 0 | 1 | 0 | 28.454 | 29.03 | 27.78 | 27.922 | 18.092 | 24.815 | 15.697 | 0 | 0 | 58.103 | 55.855 | 48.13 | 22.118 | 0 | 0 | 56.69 | 34.873 | [5 empty] | 0 | 0.532 | 36 | 2.0254 | 1.8501 | 0.9223 | 0.77922 | 1.0708 | 52.8701
2005-10-31 | 13:18 | 0 | 21.25 | 0 | 2 | 0 | 38.562 | 28.886 | 27.755 | 27.826 | 24.116 | 24.791 | 15.624 | 0 | 0 | 58.103 | 55.809 | 48.107 | 22.118 | 0 | 0 | 56.579 | 34.873 | [5 empty] | 0 | 10.736 | 37 | 2.0467 | 1.8703 | 0.92316 | 0.77922 | 1.0911 | 53.3083
2005-10-31 | 13:19 | 0 | 21.25 | 1 | 2 | 0 | 43.238 | 29.008 | 27.731 | 27.755 | 21.709 | 24.913 | 15.674 | 1 | 0 | 58.126 | 55.809 | 48.107 | 22.118 | 0 | 0 | 56.601 | 34.873 | [5 empty] | 0 | 15.483 | 38 | 2.0321 | 1.8564 | 0.92257 | 0.77922 | 1.0772 | 53.0092
2005-10-31 | 13:20 | 0 | 21.25 | 0 | 1 | 0 | 33.182 | 40.114 | 27.537 | 27.682 | 20.018 | 24.84 | 15.649 | 0 | 0 | 58.06 | 55.809 | 48.221 | 22.118 | 0 | 0 | 56.535 | 34.897 | [5 empty] | 0 | 5.5 | 39 | 2.0394 | 1.8634 | 0.92286 | 0.77922 | 1.0841 | 53.1593
2005-10-31 | 13:21 | 0 | 21.331 | 0 | 2 | 0 | 29.979 | 40.332 | 27.618 | 27.642 | 19.163 | 24.823 | 15.682 | 0 | 0 | 58.112 | 55.839 | 48.16 | 22.15 | 0 | 0 | 56.565 | 34.928 | [5 empty] | 0 | 2.337 | 40 | 2.0298 | 1.8542 | 0.92247 | 0.77922 | 1.075 | 52.9609
2005-10-31 | 13:22 | 0 | 21.299 | 0 | 2 | 0 | 28.984 | 33.275 | 27.611 | 27.635 | 18.465 | 24.791 | 15.747 | 0 | 0 | 58.06 | 55.788 | 48.151 | 22.118 | 0 | 0 | 56.601 | 34.897 | [5 empty] | 0 | 1.349 | 41 | 2.0109 | 1.8362 | 0.92171 | 0.77922 | 1.057 | 52.5647
2005-10-31 | 13:23 | 0 | 21.299 | 0 | 1 | 0 | 28.525 | 30.502 | 27.611 | 27.441 | 18.168 | 24.889 | 15.747 | 1 | 0 | 58.082 | 55.832 | 48.083 | 22.143 | 0 | 0 | 56.579 | 34.921 | [5 empty] | 0 | 1.084 | 42 | 2.0109 | 1.8362 | 0.92171 | 0.77922 | 1.057 | 52.5647
2005-10-31 | 13:24 | 0 | 21.299 | 0 | 2 | 0 | 28.356 | 29.464 | 27.611 | 27.586 | 17.969 | 24.864 | 15.797 | 0 | 0 | 58.103 | 55.855 | 48.151 | 22.192 | 0 | 0 | 56.579 | 34.921 | [5 empty] | 0 | 0.77 | 43 | 1.9963 | 1.8224 | 0.92112 | 0.77922 | 1.0432 | 52.2548
2005-10-31 | 13:25 | 0 | 21.27 | 0 | 1 | 0 | 28.135 | 29.001 | 27.581 | 27.652 | 17.841 | 24.931 | 15.742 | 0 | 0 | 58.009 | 55.736 | 48.102 | 22.113 | 0 | 0 | 56.574 | 34.845 | [5 empty] | 0 | 0.483 | 44 | 2.0123 | 1.8376 | 0.92177 | 0.77922 | 1.0584 | 52.5954
2005-10-31 | 13:26 | 0 | 21.299 | 0 | 2 | 0 | 28.14 | 28.741 | 27.78 | 27.611 | 17.748 | 25.105 | 15.822 | 0 | 0 | 58.06 | 55.764 | 48.06 | 22.155 | 0 | 0 | 56.569 | 34.861 | [5 empty] | 0 | 0.529 | 45 | 1.989 | 1.8155 | 0.92082 | 0.77922 | 1.0362 | 52.0981
2005-10-31 | 13:27 | 0 | 21.333 | 0 | 2 | 0 | 28.101 | 28.729 | 27.812 | 27.79 | 17.733 | 25.284 | 15.807 | 0 | 0 | 58.048 | 55.888 | 48.093 | 22.152 | 0 | 0 | 56.59 | 34.859 | [5 empty] | 0 | 0.311 | 46 | 1.9934 | 1.8196 | 0.921 | 0.77922 | 1.0404 | 52.1923
2005-10-31 | 13:28 | 0 | 21.309 | 0 | 2 | 0 | 28.03 | 28.486 | 27.547 | 27.692 | 17.61 | 25.114 | 15.757 | 0 | 0 | 58.025 | 55.729 | 48.093 | 22.152 | 0 | 0 | 56.567 | 34.859 | [5 empty] | 0 | 0.338 | 47 | 2.008 | 1.8335 | 0.92159 | 0.77922 | 1.0542 | 52.5031
2005-10-31 | 13:29 | 0 | 21.333 | 0 | 1 | 0 | 34.156 | 28.366 | 27.571 | 27.596 | 23.477 | 25.114 | 15.757 | 0 | 0 | 58.025 | 55.729 | 48.072 | 22.152 | 0 | 0 | 56.59 | 34.859 | [5 empty] | 0 | 6.56 | 48 | 2.008 | 1.8335 | 0.92159 | 0.77922 | 1.0542 | 52.5031
2005-10-31 | 13:30 | 0 | 21.333 | 0 | 2 | 0 | 43.13 | 28.535 | 27.547 | 27.476 | 21.598 | 25.114 | 15.757 | 1 | 0 | 58.025 | 55.753 | 48.048 | 22.152 | 0 | 0 | 56.544 | 34.837 | [5 empty] | 0 | 15.654 | 49 | 2.008 | 1.8335 | 0.92159 | 0.77922 | 1.0542 | 52.5031
2005-10-31 | 13:31 | 0 | 21.309 | 1 | 2 | 0 | 32.792 | 39.724 | 27.5 | 27.5 | 20.151 | 25.21 | 15.707 | 0 | 0 | 58.002 | 55.729 | 48.163 | 22.152 | 0 | 0 | 56.478 | 34.79 | [5 empty] | 0 | 5.292 | 50 | 2.0225 | 1.8473 | 0.92218 | 0.77922 | 1.0681 | 52.8094
2005-10-31 | 13:32 | 0 | 21.304 | 0 | 2 | 0 | 29.543 | 38.662 | 27.446 | 27.495 | 19.01 | 25.181 | 15.676 | 0 | 0 | 58.041 | 55.725 | 48.02 | 22.148 | 0 | 0 | 56.496 | 34.785 | [5 empty] | 0 | 2.048 | 51 | 2.0315 | 1.8559 | 0.92254 | 0.77922 | 1.0767 | 52.9971
2005-10-31 | 13:33 | 0 | 21.333 | 0 | 2 | 0 | 28.584 | 32.076 | 27.62 | 27.356 | 18.374 | 25.333 | 15.732 | 0 | 0 | 58.025 | 55.706 | 48.048 | 22.128 | 0 | 0 | 56.524 | 34.79 | [5 empty] | 0 | 1.228 | 52 | 2.0152 | 1.8404 | 0.92188 | 0.77922 | 1.0612 | 52.6568
2005-10-31 | 13:34 | 0 | 21.28 | 0 | 1 | 0 | 28.17 | 29.734 | 27.566 | 27.397 | 18.047 | 25.159 | 15.676 | 0 | 0 | 57.929 | 55.655 | 48.02 | 22.099 | 0 | 0 | 56.451 | 34.809 | [5 empty] | 0 | 0.773 | 53 | 2.0315 | 1.8559 | 0.92254 | 0.77922 | 1.0767 | 52.9971
2005-10-31 | 13:35 | 0 | 21.28 | 0 | 2 | 0 | 28.025 | 28.989 | 27.542 | 27.422 | 17.851 | 25.254 | 15.702 | 0 | 0 | 57.952 | 55.678 | 48.088 | 22.123 | 0 | 0 | 56.496 | 34.83 | [5 empty] | 0 | 0.603 | 54 | 2.024 | 1.8487 | 0.92224 | 0.77922 | 1.0695 | 52.8398
2005-10-31 | 13:36 | 0 | 21.333 | 0 | 2 | 0 | 27.956 | 28.584 | 27.547 | 27.427 | 17.733 | 25.188 | 15.757 | 1 | 0 | 57.957 | 55.683 | 48.093 | 22.152 | 0 | 0 | 56.59 | 34.859 | [5 empty] | 0 | 0.529 | 55 | 2.008 | 1.8335 | 0.92159 | 0.77922 | 1.0542 | 52.5031
2005-10-31 | 13:37 | 0 | 21.304 | 0 | 2 | 0 | 27.88 | 28.385 | 27.591 | 27.446 | 17.554 | 25.205 | 15.727 | 0 | 0 | 57.907 | 55.631 | 48.02 | 22.099 | 0 | 0 | 56.496 | 34.737 | [5 empty] | 0 | 0.434 | 56 | 2.0167 | 1.8418 | 0.92194 | 0.77922 | 1.0625 | 52.6874
2005-10-31 | 13:38 | 0 | 21.333 | 0 | 2 | 0 | 27.861 | 28.344 | 27.571 | 27.427 | 17.509 | 25.284 | 15.83 | 0 | 0 | 57.957 | 55.659 | 47.978 | 22.152 | 0 | 0 | 56.501 | 34.79 | [5 empty] | 0 | 0.434 | 57 | 1.9867 | 1.8133 | 0.92073 | 0.77922 | 1.034 | 52.0478
2005-10-31 | 13:39 | 0 | 21.333 | 0 | 2 | 0 | 27.836 | 28.221 | 27.525 | 27.402 | 17.559 | 25.259 | 15.855 | 0 | 0 | 57.934 | 55.659 | 48.093 | 22.152 | 0 | 0 | 56.478 | 34.79 | [5 empty] | 0 | 0.434 | 58 | 1.9794 | 1.8063 | 0.92043 | 0.77922 | 1.0271 | 51.8896
2005-10-31 | 13:40 | 0 | 21.333 | 0 | 2 | 0 | 30.511 | 28.15 | 27.525 | 27.476 | 23.285 | 25.259 | 15.807 | 0 | 0 | 57.913 | 55.636 | 48.025 | 22.273 | 0 | 0 | 56.478 | 34.813 | [5 empty] | 0 | 3.035 | 59 | 1.9934 | 1.8196 | 0.921 | 0.77922 | 1.0404 | 52.1923
2005-10-31 | 13:41 | 0 | 21.333 | 0 | 2 | 0 | 43.109 | 28.175 | 27.451 | 27.525 | 21.549 | 25.259 | 15.757 | 0 | 0 | 57.891 | 55.636 | 48.093 | 22.128 | 0 | 0 | 56.478 | 34.837 | [5 empty] | 0 | 15.584 | 60 | 2.008 | 1.8335 | 0.92159 | 0.77922 | 1.0542 | 52.5031
2005-10-31 | 13:42 | 0 | 21.333 | 0 | 2 | 0 | 32.627 | 39.511 | 27.476 | 27.38 | 19.955 | 25.259 | 15.757 | 1 | 0 | 57.891 | 55.615 | 48.002 | 22.152 | 0 | 0 | 56.432 | 34.813 | [5 empty] | 0 | 5.247 | 61 | 2.008 | 1.8335 | 0.92159 | 0.77922 | 1.0542 | 52.5031
2005-10-31 | 13:43 | 0 | 21.255 | 1 | 2 | 0 | 29.398 | 37.464 | 27.397 | 27.373 | 19.01 | 25.205 | 15.702 | 0 | 0 | 57.863 | 55.564 | 47.997 | 22.123 | 0 | 0 | 56.451 | 34.83 | [5 empty] | 0 | 2.025 | 62 | 2.024 | 1.8487 | 0.92224 | 0.77922 | 1.0695 | 52.8398
2005-10-31 | 13:44 | 0 | 21.333 | 0 | 2 | 0 | 28.415 | 31.352 | 27.402 | 27.476 | 18.424 | 25.235 | 15.707 | 0 | 0 | 57.868 | 55.592 | 48.025 | 22.152 | 0 | 0 | 56.501 | 34.837 | [5 empty] | 0 | 0.939 | 63 | 2.0225 | 1.8473 | 0.92218 | 0.77922 | 1.0681 | 52.8094
2005-10-31 | 13:45 | 0 | 21.304 | 0 | 1 | 0 | 28.121 | 29.325 | 27.373 | 27.422 | 18.072 | 25.11 | 15.727 | 0 | 0 | 57.84 | 55.54 | 47.95 | 22.123 | 0 | 0 | 56.496 | 34.785 | [5 empty] | 0 | 0.699 | 64 | 2.0167 | 1.8418 | 0.92194 | 0.77922 | 1.0625 | 52.6874
2005-10-31 | 13:46 | 0 | 21.304 | 0 | 2 | 0 | 27.88 | 28.699 | 27.446 | 27.277 | 17.899 | 25.181 | 15.752 | 0 | 0 | 57.863 | 55.564 | 47.985 | 22.111 | 0 | 0 | 56.462 | 34.725 | [5 empty] | 0 | 0.603 | 65 | 2.0094 | 1.8348 | 0.92165 | 0.77922 | 1.0556 | 52.5339
2005-10-31 | 13:47 | 0 | 21.336 | 0 | 2 | 0 | 27.839 | 28.466 | 27.478 | 27.309 | 17.833 | 25.166 | 15.857 | 0 | 0 | 57.87 | 55.594 | 47.959 | 22.155 | 0 | 0 | 56.458 | 34.768 | [5 empty] | 0 | 0.53 | 66 | 1.9788 | 1.8058 | 0.92041 | 0.77922 | 1.0266 | 51.8769
2005-10-31 | 13:48 | 0 | 21.331 | 0 | 2 | 0 | 27.738 | 28.197 | 27.424 | 27.4 | 17.705 | 25.137 | 15.802 | 1 | 0 | 57.82 | 55.519 | 47.976 | 22.221 | 0 | 0 | 56.407 | 34.787 | [5 empty] | 0 | 0.338 | 67 | 1.9949 | 1.821 | 0.92106 | 0.77922 | 1.0418 | 52.2236
2005-10-31 | 13:49 | 0 | 21.336 | 0 | 3 | 0 | 27.718 | 28.057 | 27.527 | 27.358 | 17.587 | 25.215 | 15.832 | 0 | 0 | 57.893 | 55.547 | 47.959 | 22.13 | 0 | 0 | 56.435 | 34.792 | [5 empty] | 0 | 0.36 | 68 | 1.9861 | 1.8127 | 0.9207 | 0.77922 | 1.0335 | 52.0352
2005-10-31 | 13:50 | 0 | 21.307 | 0 | 2 | 0 | 27.642 | 28.027 | 27.353 | 27.353 | 17.482 | 25.161 | 15.802 | 0 | 0 | 57.797 | 55.519 | 47.908 | 22.125 | 0 | 0 | 56.385 | 34.787 | [5 empty] | 0 | 0.289 | 69 | 1.9949 | 1.821 | 0.92106 | 0.77922 | 1.0418 | 52.2236
2005-10-31 | 13:51 | 1 | 21.307 | 0 | 2 | 0 | 28.461 | 27.929 | 27.304 | 27.28 | 23.739 | 25.112 | 15.951 | 0 | 0 | 57.82 | 55.543 | 47.861 | 22.15 | 0 | 0 | 56.43 | 34.811 | [5 empty] | 21.307 | 1.181 | 70 | 1.9515 | 1.7798 | 0.9193 | 0.77922 | 1.0005 | 51.2712
2005-10-31 | 13:52 | 0 | 21.307 | 0 | 2 | 0 | 44.092 | 27.954 | 27.304 | 27.378 | 24.077 | 24.992 | 15.802 | 0 | 0 | 57.777 | 55.496 | 47.931 | 22.15 | 0 | 0 | 56.407 | 34.811 | [5 empty] | 0 | 16.714 | 71 | 1.9949 | 1.821 | 0.92106 | 0.77922 | 1.0418 | 52.2236
2005-10-31 | 13:53 | 0 | 21.331 | 0 | 2 | 0 | 45.845 | 39.368 | 27.353 | 27.233 | 24.413 | 25.137 | 15.827 | 1 | 0 | 57.82 | 55.496 | 47.931 | 22.125 | 0 | 0 | 56.364 | 34.739 | [5 empty] | 0 | 18.612 | 72 | 1.9876 | 1.8141 | 0.92076 | 0.77922 | 1.0349 | 52.0667
2005-10-31 | 13:54 | 0 | 21.307 | 1 | 2 | 0 | 45.866 | 45.133 | 27.329 | 27.208 | 24.293 | 25.112 | 15.802 | 2 | 0 | 57.777 | 55.475 | 47.885 | 22.125 | 0 | 0 | 56.341 | 34.715 | [5 empty] | 0 | 18.658 | 73 | 1.9949 | 1.821 | 0.92106 | 0.77922 | 1.0418 | 52.2236
2005-10-31 | 13:55 | 0 | 21.307 | 0 | 2 | 0 | 45.707 | 45.775 | 27.353 | 27.233 | 24.077 | 25.232 | 15.754 | 1 | 0 | 57.82 | 55.475 | 47.861 | 22.101 | 0 | 0 | 56.318 | 34.694 | [5 empty] | 0 | 18.474 | 74 | 2.0088 | 1.8343 | 0.92162 | 0.77922 | 1.0551 | 52.5216
2005-10-31 | 13:56 | 0 | 21.336 | 0 | 2 | 0 | 45.826 | 45.735 | 27.549 | 27.262 | 23.719 | 25.092 | 15.81 | 1 | 0 | 57.804 | 55.48 | 47.959 | 22.155 | 0 | 0 | 56.3 | 34.84 | [5 empty] | 0 | 18.564 | 75 | 1.9925 | 1.8188 | 0.92096 | 0.77922 | 1.0396 | 52.1735
2005-10-31 | 13:57 | 1 | 21.307 | 0 | 2 | 1 | 45.728 | 45.866 | 27.618 | 27.353 | 23.548 | 24.943 | 15.802 | 1 | 0 | 57.797 | 55.475 | 48.023 | 22.101 | 0 | 0 | 56.318 | 34.739 | [5 empty] | 21.307 | 18.375 | 76 | 1.9949 | 1.821 | 0.92106 | 0.77922 | 1.0418 | 52.2236
2005-10-31 | 13:58 | 0 | 21.336 | 0 | 2 | 0 | 45.665 | 45.894 | 27.768 | 27.383 | 23.599 | 25.141 | 15.832 | 2 | 0 | 57.893 | 55.503 | 47.913 | 22.13 | 0 | 0 | 56.346 | 34.744 | [5 empty] | 0 | 18.282 | 0 | 1.9861 | 1.8127 | 0.9207 | 0.77922 | 1.0335 | 52.0352
2005-10-31 | 13:59 | 0 | 21.331 | 0 | 2 | 0 | 45.752 | 45.798 | 27.738 | 27.544 | 23.859 | 25.041 | 15.827 | 1 | 0 | 57.866 | 55.566 | 48.023 | 22.221 | 0 | 0 | 56.296 | 34.715 | [5 empty] | 0 | 18.208 | 1 | 1.9876 | 1.8141 | 1.366 | 1.2245 | 0.5896 | 29.6641
2005-10-31 | 14:00 | 0 | 21.331 | 0 | 2 | 0 | 46.211 | 45.866 | 27.883 | 27.569 | 24.053 | 25.087 | 15.729 | 1 | 0 | 57.888 | 55.475 | 47.908 | 22.101 | 0 | 0 | 56.296 | 34.715 | [5 empty] | 0 | 18.642 | 2 | 2.0161 | 1.8412 | 1.3672 | 1.2245 | 0.61672 | 30.5897
2005-10-31 | 14:01 | 0 | 21.307 | 0 | 2 | 0 | 46.463 | 46.188 | 28.052 | 27.665 | 24.148 | 25.112 | 15.802 | 1 | 0 | 57.866 | 55.475 | 47.931 | 22.101 | 0 | 0 | 56.318 | 34.739 | [5 empty] | 0 | 18.798 | 3 | 1.9949 | 1.821 | 1.3663 | 1.2245 | 0.59652 | 29.9027
2005-10-31 | 14:02 | 0 | 21.336 | 0 | 2 | 0 | 46.354 | 46.652 | 28.057 | 27.888 | 24.251 | 25.07 | 15.785 | 1 | 0 | 57.893 | 55.48 | 47.959 | 22.155 | 0 | 0 | 56.369 | 34.723 | [5 empty] | 0 | 18.466 | 4 | 1.9998 | 1.8257 | 1.3665 | 1.2245 | 0.60122 | 30.064
2005-10-31 | 14:03 | 1 | 21.307 | 1 | 2 | 0 | 46.508 | 46.645 | 28.148 | 27.809 | 24.509 | 25.087 | 15.656 | 2 | 0 | 57.888 | 55.475 | 47.908 | 22.101 | 0 | 0 | 56.318 | 34.67 | [5 empty] | 21.307 | 18.699 | 5 | 2.0374 | 1.8614 | 1.368 | 1.2245 | 0.63693 | 31.2623
2005-10-31 | 14:04 | 0 | 21.282 | 0 | 2 | 0 | 46.83 | 46.669 | 28.197 | 28.027 | 24.631 | 25.063 | 15.704 | 1 | 0 | 57.888 | 55.475 | 47.931 | 22.125 | 0 | 0 | 56.318 | 34.715 | [5 empty] | 0 | 18.803 | 6 | 2.0234 | 1.8481 | 1.3675 | 1.2245 | 0.62364 | 30.8216
2005-10-31 | 14:05 | 0 | 21.282 | 0 | 2 | 0 | 46.968 | 46.853 | 28.412 | 28.052 | 24.776 | 25.041 | 15.704 | 1 | 0 | 57.932 | 55.475 | 47.999 | 22.125 | 0 | 0 | 56.296 | 34.715 | [5 empty] | 0 | 18.916 | 7 | 2.0234 | 1.8481 | 1.3675 | 1.2245 | 0.62364 | 30.8216
2005-10-31 | 14:06 | 0 | 21.282 | 0 | 2 | 0 | 47.29 | 47.129 | 28.726 | 28.074 | 25.016 | 25.112 | 15.78 | 1 | 0 | 57.955 | 55.475 | 48.046 | 22.101 | 0 | 0 | 56.309 | 34.751 | [5 empty] | 0 | 19.216 | 8 | 2.0013 | 1.8271 | 1.3666 | 1.2245 | 0.60261 | 30.1113
2005-10-31 | 14:07 | 0 | 21.333 | 0 | 2 | 0 | 47.567 | 47.339 | 29.234 | 28.39 | 25.043 | 25.164 | 15.782 | 2 | 0 | 58.025 | 55.524 | 48.095 | 22.177 | 0 | 0 | 56.346 | 34.79 | [5 empty] | 0 | 19.177 | 9 | 2.0007 | 1.8265 | 1.3666 | 1.2245 | 0.60205 | 30.0924
2005-10-31 | 14:08 | 1 | 21.309 | 0 | 2 | 0 | 48.004 | 47.705 | 29.812 | 28.969 | 25.284 | 25.139 | 15.782 | 1 | 0 | 58.005 | 55.524 | 48.072 | 22.177 | 0 | 0 | 56.323 | 34.79 | [5 empty] | 21.309 | 19.035 | 10 | 2.0007 | 1.8265 | 1.3666 | 1.2245 | 0.60205 | 30.0924
2005-10-31 | 14:09 | 0 | 21.341 | 0 | 2 | 0 | 48.125 | 47.941 | 30.374 | 29.361 | 25.509 | 25.195 | 15.815 | 1 | 0 | 58.034 | 55.554 | 48.034 | 22.184 | 0 | 0 | 56.375 | 34.797 | [5 empty] | 0 | 18.764 | 11 | 1.9911 | 1.8174 | 1.3662 | 1.2245 | 0.59292 | 29.7788
2005-10-31 | 14:10 | 0 | 21.309 | 0 | 1 | 0 | 48.69 | 48.233 | 30.825 | 29.933 | 25.622 | 25.213 | 15.782 | 1 | 0 | 58.048 | 55.524 | 47.981 | 22.152 | 0 | 0 | 56.389 | 34.766 | [5 empty] | 0 | 18.757 | 12 | 2.0007 | 1.8265 | 1.3666 | 1.2245 | 0.60205 | 30.0924
2005-10-31 | 14:11 | 0 | 21.333 | 0 | 2 | 0 | 49.241 | 48.508 | 31.235 | 30.462 | 24.825 | 25.284 | 15.855 | 1 | 0 | 58.071 | 55.547 | 47.981 | 22.177 | 0 | 0 | 56.435 | 34.766 | [5 empty] | 0 | 18.779 | 13 | 1.9794 | 1.8063 | 1.3657 | 1.2245 | 0.58185 | 29.3947
2005-10-31 | 14:12 | 0 | 21.309 | 0 | 2 | 0 | 39.162 | 49.173 | 31.379 | 30.872 | 23.043 | 25.355 | 15.805 | 1 | 0 | 58.071 | 55.501 | 48.004 | 22.152 | 0 | 0 | 56.458 | 34.744 | [5 empty] | 0 | 8.29 | 14 | 1.994 | 1.8202 | 1.3663 | 1.2245 | 0.59569 | 29.8742
2005-10-31 | 14:13 | 0 | 21.309 | 1 | 2 | 0 | 34.72 | 47.154 | 31.45 | 31.257 | 21.792 | 25.284 | 15.83 | 0 | 0 | 58.025 | 55.524 | 48.048 | 22.152 | 0 | 0 | 56.458 | 34.766 | [5 empty] | 0 | 3.463 | 15 | 1.9867 | 1.8133 | 1.366 | 1.2245 | 0.58877 | 29.6353
2005-10-31 | 14:14 | 0 | 21.26 | 0 | 1 | 0 | 33.426 | 39.184 | 31.546 | 31.306 | 20.877 | 25.259 | 15.805 | 1 | 0 | 58.071 | 55.524 | 48.072 | 22.152 | 0 | 0 | 56.435 | 34.744 | [5 empty] | 0 | 2.12 | 16 | 1.994 | 1.8202 | 1.3663 | 1.2245 | 0.59569 | 29.8742
2005-10-31 | 14:15 | 0 | 21.309 | 0 | 2 | 0 | 32.981 | 35.354 | 31.522 | 31.426 | 20.397 | 25.284 | 15.855 | 0 | 0 | 58.071 | 55.547 | 48.142 | 22.273 | 0 | 0 | 56.346 | 34.79 | [5 empty] | 0 | 1.555 | 17 | 1.9794 | 1.8063 | 1.3657 | 1.2245 | 0.58185 | 29.3947
2005-10-31 | 14:16 | 0 | 21.309 | 0 | 2 | 0 | 32.864 | 34.084 | 31.379 | 31.546 | 20.078 | 25.235 | 15.83 | 0 | 0 | 58.048 | 55.524 | 48.209 | 22.177 | 0 | 0 | 56.389 | 34.766 | [5 empty] | 0 | 1.318 | 18 | 1.9867 | 1.8133 | 1.366 | 1.2245 | 0.58877 | 29.6353
2005-10-31 | 14:17 | 0 | 21.333 | 0 | 1 | 0 | 32.627 | 33.591 | 31.33 | 31.426 | 19.807 | 25.308 | 15.805 | 0 | 0 | 58.094 | 55.501 | 48.048 | 22.152 | 0 | 0 | 56.323 | 34.766 | [5 empty] | 0 | 1.201 | 19 | 1.994 | 1.8202 | 1.3663 | 1.2245 | 0.59569 | 29.8742
2005-10-31 | 14:18 | 0 | 21.333 | 0 | 2 | 0 | 32.51 | 33.285 | 31.112 | 31.426 | 19.46 | 25.259 | 15.83 | 0 | 0 | 58.025 | 55.501 | 48.072 | 22.177 | 0 | 0 | 56.323 | 34.79 | [5 empty] | 0 | 1.084 | 20 | 1.9867 | 1.8133 | 1.366 | 1.2245 | 0.58877 | 29.6353
2005-10-31 | 14:19 | 0 | 21.302 | 0 | 2 | 0 | 32.287 | 33.019 | 30.769 | 31.274 | 19.38 | 25.203 | 15.873 | 0 | 0 | 57.975 | 55.447 | 48.065 | 22.121 | 0 | 0 | 56.27 | 34.758 | [5 empty] | 0 | 1.013 | 21 | 1.9742 | 1.8014 | 1.3655 | 1.2245 | 0.57686 | 29.2204
2005-10-31 | 14:20 | 0 | 21.309 | 0 | 1 | 0 | 32.125 | 32.933 | 30.536 | 31.112 | 19.312 | 25.333 | 15.855 | 0 | 0 | 58.005 | 55.477 | 48.186 | 22.152 | 0 | 0 | 56.234 | 34.79 | [5 empty] | 0 | 1.013 | 22 | 1.9794 | 1.8063 | 1.3657 | 1.2245 | 0.58185 | 29.3947
2005-10-31 | 14:21 | 0 | 21.309 | 0 | 2 | 0 | 32.174 | 32.651 | 30.318 | 30.872 | 26.946 | 25.404 | 15.855 | 0 | 0 | 57.982 | 55.456 | 48.048 | 22.177 | 0 | 0 | 56.254 | 34.766 | [5 empty] | 0 | 1.302 | 23 | 1.9794 | 1.8063 | 1.3657 | 1.2245 | 0.58185 | 29.3947
2005-10-31 | 14:22 | 0 | 21.309 | 0 | 1 | 0 | 49.103 | 32.51 | 29.884 | 30.536 | 24.32 | 25.308 | 15.905 | 1 | 0 | 57.959 | 55.433 | 48.004 | 22.177 | 0 | 0 | 56.211 | 34.79 | [5 empty] | 0 | 18.567 | 24 | 1.9649 | 1.7925 | 1.3651 | 1.2245 | 0.56801 | 28.9082
2005-10-31 | 14:23 | 0 | 21.309 | 0 | 2 | 0 | 39.562 | 35.12 | 29.619 | 30.222 | 21.792 | 25.235 | 15.905 | 0 | 0 | 57.936 | 55.433 | 48.095 | 22.201 | 0 | 0 | 56.188 | 34.79 | [5 empty] | 0 | 9.34 | 25 | 1.9649 | 1.7925 | 1.3651 | 1.2245 | 0.56801 | 28.9082
2005-10-31 | 14:24 | 0 | 21.284 | 1 | 2 | 0 | 33.849 | 45.527 | 29.187 | 29.862 | 20.492 | 25.213 | 15.905 | 0 | 0 | 57.913 | 55.433 | 48.048 | 22.152 | 0 | 0 | 56.188 | 34.79 | [5 empty] | 0 | 3.987 | 26 | 1.9649 | 1.7925 | 1.3651 | 1.2245 | 0.56801 | 28.9082
2005-10-31 | 14:25 | 0 | 21.284 | 0 | 1 | 0 | 32.005 | 39.279 | 28.873 | 29.548 | 19.832 | 25.259 | 15.855 | 0 | 0 | 57.893 | 55.433 | 48.095 | 22.177 | 0 | 0 | 56.188 | 34.861 | [5 empty] | 0 | 2.457 | 27 | 1.9794 | 1.8063 | 1.3657 | 1.2245 | 0.58185 | 29.3947
2005-10-31 | 14:26 | 0 | 21.284 | 0 | 2 | 0 | 31.137 | 34.438 | 28.68 | 29.209 | 19.387 | 25.188 | 15.805 | 1 | 0 | 57.87 | 55.433 | 48.048 | 22.152 | 0 | 0 | 56.275 | 34.859 | [5 empty] | 0 | 1.928 | 28 | 1.994 | 1.8202 | 1.3663 | 1.2245 | 0.59569 | 29.8742
2005-10-31 | 14:27 | 0 | 21.294 | 0 | 1 | 0 | 30.568 | 32.613 | 28.496 | 28.859 | 19.199 | 25.22 | 15.84 | 0 | 0 | 57.877 | 55.393 | 47.941 | 22.138 | 0 | 0 | 56.241 | 34.845 | [5 empty] | 0 | 1.709 | 29 | 1.9838 | 1.8105 | 1.3659 | 1.2245 | 0.586 | 29.5393
2005-10-31 | 14:28 | 0 | 21.27 | 0 | 2 | 0 | 30.183 | 31.676 | 28.329 | 28.761 | 18.927 | 25.149 | 15.742 | 0 | 0 | 57.831 | 55.37 | 47.988 | 22.138 | 0 | 0 | 56.218 | 34.892 | [5 empty] | 0 | 1.422 | 30 | 2.0123 | 1.8376 | 1.367 | 1.2245 | 0.61312 | 30.4684
2005-10-31 | 14:29 | 0 | 21.294 | 0 | 1 | 0 | 29.844 | 31.097 | 28.305 | 28.496 | 18.927 | 25.244 | 15.767 | 0 | 0 | 57.831 | 55.37 | 47.941 | 22.138 | 0 | 0 | 56.241 | 34.845 | [5 empty] | 0 | 1.348 | 31 | 2.005 | 1.8307 | 1.3667 | 1.2245 | 0.6062 | 30.2339
2005-10-31 | 14:30 | 0 | 21.245 | 0 | 2 | 0 | 29.557 | 30.641 | 28.111 | 28.425 | 18.829 | 25.075 | 15.742 | 0 | 0 | 57.809 | 55.37 | 48.058 | 22.138 | 0 | 0 | 56.241 | 34.799 | [5 empty] | 0 | 1.132 | 32 | 2.0123 | 1.8376 | 1.367 | 1.2245 | 0.61312 | 30.4684
2005-10-31 | 14:31 | 0 | 21.27 | 0 | 1 | 0 | 29.219 | 30.303 | 28.062 | 28.184 | 18.583 | 25.075 | 15.767 | 0 | 0 | 57.831 | 55.349 | 47.873 | 22.162 | 0 | 0 | 56.241 | 34.775 | [5 empty] | 0 | 1.035 | 33 | 2.005 | 1.8307 | 1.3667 | 1.2245 | 0.6062 | 30.2339
2005-10-31 | 14:32 | 0 | 21.245 | 0 | 2 | 0 | 29.05 | 29.893 | 27.942 | 28.111 | 24.715 | 25.029 | 15.742 | 0 | 0 | 57.765 | 55.302 | 47.988 | 22.162 | 0 | 0 | 56.241 | 34.751 | [5 empty] | 0 | 0.939 | 34 | 2.0123 | 1.8376 | 1.367 | 1.2245 | 0.61312 | 30.4684
2005-10-31 | 14:33 | 0 | 21.245 | 0 | 2 | 0 | 47.255 | 29.604 | 27.966 | 28.086 | 23.68 | 25.053 | 15.717 | 0 | 0 | 57.742 | 55.279 | 47.873 | 22.138 | 0 | 0 | 56.241 | 34.775 | [5 empty] | 0 | 19.169 | 35 | 2.0196 | 1.8445 | 1.3673 | 1.2245 | 0.62004 | 30.7012
2005-10-31 | 14:34 | 0 | 21.245 | 0 | 1 | 0 | 39.076 | 30.977 | 27.871 | 27.966 | 21.39 | 25.1 | 15.792 | 1 | 0 | 57.765 | 55.279 | 47.85 | 22.138 | 0 | 0 | 56.241 | 34.751 | [5 empty] | 0 | 11.11 | 36 | 1.9978 | 1.8238 | 1.3664 | 1.2245 | 0.59928 | 29.9977
2005-10-31 | 14:35 | 0 | 21.27 | 0 | 2 | 0 | 32.014 | 43.539 | 27.726 | 27.942 | 20.136 | 25.149 | 15.792 | 0 | 0 | 57.765 | 55.279 | 47.805 | 22.162 | 0 | 0 | 56.241 | 34.775 | [5 empty] | 0 | 4.072 | 37 | 1.9978 | 1.8238 | 1.3664 | 1.2245 | 0.59928 | 29.9977
2005-10-31 | 14:36 | 0 | 21.27 | 1 | 2 | 0 | 29.844 | 38.277 | 27.726 | 27.821 | 19.347 | 25.029 | 15.767 | 0 | 0 | 57.697 | 55.256 | 47.826 | 22.113 | 0 | 0 | 56.195 | 34.799 | [5 empty] | 0 | 2.023 | 38 | 2.005 | 1.8307 | 1.3667 | 1.2245 | 0.6062 | 30.2339
2005-10-31 | 14:37 | 0 | 21.27 | 0 | 1 | 0 | 29.074 | 32.613 | 27.75 | 27.797 | 18.977 | 25.075 | 15.792 | 0 | 0 | 57.72 | 55.279 | 47.782 | 22.138 | 0 | 0 | 56.172 | 34.823 | [5 empty] | 0 | 1.277 | 39 | 1.9978 | 1.8238 | 1.3664 | 1.2245 | 0.59928 | 29.9977
2005-10-31 | 14:38 | 0 | 21.238 | 0 | 2 | 0 | 28.802 | 30.44 | 27.765 | 27.814 | 18.844 | 24.948 | 15.832 | 0 | 0 | 57.644 | 55.181 | 47.796 | 22.13 | 0 | 0 | 56.165 | 34.792 | [5 empty] | 0 | 0.988 | 40 | 1.9861 | 1.8127 | 1.366 | 1.2245 | 0.58821 | 29.6161
2005-10-31 | 14:39 | 0 | 21.238 | 0 | 1 | 0 | 28.537 | 29.572 | 27.718 | 27.669 | 18.673 | 24.923 | 15.782 | 0 | 0 | 57.624 | 55.181 | 47.819 | 22.106 | 0 | 0 | 56.188 | 34.861 | [5 empty] | 0 | 0.868 | 41 | 2.0007 | 1.8265 | 1.3666 | 1.2245 | 0.60205 | 30.0924
2005-10-31 | 14:40 | 0 | 21.27 | 0 | 2 | 0 | 28.425 | 29.315 | 27.797 | 27.726 | 18.731 | 25.004 | 15.815 | 0 | 0 | 57.674 | 55.232 | 47.896 | 22.162 | 0 | 0 | 56.241 | 34.775 | [5 empty] | 0 | 0.699 | 42 | 1.9911 | 1.8174 | 1.3662 | 1.2245 | 0.59292 | 29.7788
2005-10-31 | 14:41 | 0 | 21.213 | 0 | 1 | 0 | 28.319 | 28.971 | 27.694 | 27.79 | 18.449 | 25.092 | 15.709 | 0 | 0 | 57.624 | 55.181 | 47.752 | 22.106 | 0 | 0 | 56.165 | 34.696 | [5 empty] | 0 | 0.529 | 43 | 2.0219 | 1.8467 | 1.3674 | 1.2245 | 0.62226 | 30.7754
2005-10-31 | 14:42 | 0 | 21.238 | 0 | 2 | 0 | 28.297 | 28.802 | 27.669 | 27.863 | 18.055 | 24.972 | 15.659 | 1 | 0 | 57.601 | 55.181 | 47.775 | 22.13 | 0 | 0 | 56.098 | 34.696 | [5 empty] | 0 | 0.434 | 44 | 2.0365 | 1.8606 | 1.368 | 1.2245 | 0.6361 | 31.2349
2005-10-31 | 14:43 | 1 | 21.238 | 0 | 2 | 0 | 28.273 | 28.682 | 27.669 | 27.765 | 21.888 | 24.997 | 15.709 | 0 | 0 | 57.555 | 55.181 | 47.775 | 22.13 | 0 | 0 | 56.119 | 34.696 | [5 empty] | 21.238 | 0.508 | 45 | 2.0219 | 1.8467 | 1.3674 | 1.2245 | 0.62226 | 30.7754
2005-10-31 | 14:44 | 0 | 21.262 | 0 | 1 | 0 | 44.564 | 28.633 | 27.574 | 27.79 | 23.55 | 24.948 | 15.807 | 0 | 0 | 57.601 | 55.134 | 47.728 | 22.13 | 0 | 0 | 56.051 | 34.72 | [5 empty] | 0 | 16.774 | 46 | 1.9934 | 1.8196 | 1.3663 | 1.2245 | 0.59513 | 29.8551
2005-10-31 | 14:45 | 0 | 21.238 | 0 | 2 | 0 | 39.679 | 29.668 | 27.478 | 27.574 | 21.093 | 24.997 | 15.709 | 0 | 0 | 57.578 | 55.134 | 47.728 | 22.106 | 0 | 0 | 56.075 | 34.72 | [5 empty] | 0 | 12.105 | 47 | 2.0219 | 1.8467 | 1.3674 | 1.2245 | 0.62226 | 30.7754
2005-10-31 | 14:46 | 0 | 21.262 | 0 | 2 | 1 | 31.789 | 42.568 | 27.429 | 27.5 | 19.709 | 25.021 | 15.759 | 1 | 0 | 57.555 | 55.134 | 47.682 | 22.13 | 0 | 0 | 56.075 | 34.744 | [5 empty] | 0 | 4.289 | 48 | 2.0074 | 1.8329 | 1.3668 | 1.2245 | 0.60842 | 30.3091
2005-10-31 | 14:47 | 0 | 21.26 | 0 | 1 | 0 | 29.425 | 37.655 | 27.427 | 27.476 | 19.015 | 25.139 | 15.707 | 0 | 0 | 57.578 | 55.111 | 47.705 | 22.128 | 0 | 0 | 56.096 | 34.718 | [5 empty] | 0 | 1.949 | 0 | 2.0225 | 1.8473 | 1.3674 | 1.2245 | 0.62281 | 30.7939
2005-10-31 | 14:48 | 0 | 21.26 | 1 | 2 | 0 | 28.631 | 31.956 | 27.62 | 27.451 | 18.671 | 24.994 | 15.732 | 0 | 0 | 57.532 | 55.111 | 47.705 | 22.128 | 0 | 0 | 56.072 | 34.718 | [5 empty] | 0 | 1.18 | 1 | 2.0152 | 1.8404 | 1.6811 | 1.5385 | 0.30192 | 14.9819
2005-10-31 | 14:49 | 0 | 21.23 | 0 | 2 | 0 | 28.29 | 29.805 | 27.517 | 27.468 | 18.492 | 24.965 | 15.651 | 0 | 0 | 57.482 | 55.083 | 47.698 | 22.099 | 0 | 0 | 56.044 | 34.62 | [5 empty] | 0 | 0.822 | 2 | 2.0388 | 1.8628 | 1.6821 | 1.5385 | 0.32434 | 15.9082
2005-10-31 | 14:50 | 0 | 21.26 | 0 | 1 | 0 | 28.101 | 29.114 | 27.547 | 27.378 | 18.226 | 24.994 | 15.606 | 0 | 0 | 57.555 | 55.111 | 47.705 | 22.103 | 0 | 0 | 56.119 | 34.624 | [5 empty] | 0 | 0.723 | 3 | 2.0519 | 1.8753 | 1.6826 | 1.5385 | 0.3368 | 16.4137
2005-10-31 | 14:51 | 0 | 21.23 | 0 | 2 | 0 | 28 | 28.721 | 27.613 | 27.446 | 18.047 | 25.061 | 15.601 | 0 | 0 | 57.528 | 55.06 | 47.654 | 22.074 | 0 | 0 | 56.023 | 34.548 | [5 empty] | 0 | 0.554 | 4 | 2.0534 | 1.8766 | 1.6827 | 1.5385 | 0.33818 | 16.4694
2005-10-31 | 14:52 | 0 | 21.26 | 0 | 2 | 0 | 27.956 | 28.486 | 27.62 | 27.547 | 17.929 | 24.97 | 15.656 | 0 | 0 | 57.466 | 55.064 | 47.726 | 22.103 | 0 | 0 | 56.005 | 34.601 | [5 empty] | 0 | 0.409 | 5 | 2.0374 | 1.8614 | 1.682 | 1.5385 | 0.32296 | 15.8517
2005-10-31 | 14:53 | 0 | 21.26 | 0 | 1 | 0 | 27.932 | 28.366 | 27.642 | 27.547 | 17.979 | 24.945 | 15.631 | 0 | 0 | 57.51 | 55.064 | 47.658 | 22.103 | 0 | 0 | 56.028 | 34.624 | [5 empty] | 0 | 0.385 | 6 | 2.0447 | 1.8683 | 1.6823 | 1.5385 | 0.32988 | 16.1337
2005-10-31 | 14:54 | 0 | 21.211 | 0 | 2 | 0 | 27.91 | 28.295 | 27.522 | 27.642 | 19.782 | 24.945 | 15.606 | 0 | 0 | 57.466 | 55.02 | 47.705 | 22.128 | 0 | 0 | 56.028 | 34.648 | [5 empty] | 0 | 0.268 | 7 | 2.0519 | 1.8753 | 1.6826 | 1.5385 | 0.3368 | 16.4137
2005-10-31 | 14:55 | 0 | 21.206 | 0 | 2 | 0 | 41.083 | 28.192 | 27.446 | 27.446 | 23.496 | 24.867 | 15.626 | 0 | 0 | 57.439 | 54.992 | 47.63 | 22.099 | 0 | 0 | 55.953 | 34.62 | [5 empty] | 0 | 13.637 | 8 | 2.0461 | 1.8697 | 1.6824 | 1.5385 | 0.33126 | 16.1898
2005-10-31 | 14:56 | 0 | 21.211 | 0 | 2 | 0 | 39.301 | 29.329 | 27.378 | 27.356 | 21.333 | 24.945 | 15.606 | 1 | 0 | 57.466 | 55.041 | 47.635 | 22.103 | 0 | 0 | 55.981 | 34.624 | [5 empty] | 0 | 11.945 | 9 | 2.0519 | 1.8753 | 1.6826 | 1.5385 | 0.3368 | 16.4137
2005-10-31 | 14:57 | 0 | 21.23 | 0 | 2 | 0 | 31.276 | 42.092 | 27.348 | 27.302 | 19.651 | 24.965 | 15.553 | 0 | 0 | 57.439 | 54.992 | 47.584 | 22.074 | 0 | 0 | 55.953 | 34.572 | [5 empty] | 0 | 3.974 | 10 | 2.0674 | 1.8899 | 1.6832 | 1.5385 | 0.35147 | 17.0008
2005-10-31 | 14:58 | 0 | 21.26 | 0 | 2 | 0 | 29.04 | 35.775 | 27.427 | 27.282 | 18.917 | 24.945 | 15.606 | 1 | 0 | 57.443 | 55.02 | 47.726 | 22.103 | 0 | 0 | 55.958 | 34.601 | [5 empty] | 0 | 1.758 | 11 | 2.0519 | 1.8753 | 1.6826 | 1.5385 | 0.3368 | 16.4137
2005-10-31 | 14:59 | 0 | 21.23 | 1 | 2 | 0 | 28.29 | 30.793 | 27.373 | 27.326 | 18.417 | 24.891 | 15.601 | 0 | 0 | 57.416 | 54.968 | 47.721 | 22.099 | 0 | 0 | 55.977 | 34.596 | [5 empty] | 0 | 0.964 | 12 | 2.0534 | 1.8766 | 1.6827 | 1.5385 | 0.33818 | 16.4694
2005-10-31 | 15:00 | 0 | 21.26 | 0 | 1 | 0 | 28.052 | 29.258 | 27.427 | 27.282 | 18.077 | 24.921 | 15.583 | 0 | 0 | 57.421 | 54.973 | 47.635 | 22.103 | 0 | 0 | 56.028 | 34.624 | [5 empty] | 0 | 0.77 | 13 | 2.0586 | 1.8816 | 1.6829 | 1.5385 | 0.34316 | 16.6695
2005-10-31 | 15:01 | 0 | 21.23 | 0 | 2 | 0 | 27.927 | 28.65 | 27.446 | 27.422 | 17.899 | 24.845 | 15.676 | 0 | 0 | 57.393 | 54.968 | 47.677 | 22.074 | 0 | 0 | 55.93 | 34.596 | [5 empty] | 0 | 0.505 | 14 | 2.0315 | 1.8559 | 1.6818 | 1.5385 | 0.31742 | 15.6246
2005-10-31 | 15:02 | 0 | 21.255 | 0 | 2 | 0 | 27.807 | 28.312 | 27.542 | 27.373 | 17.823 | 24.94 | 15.626 | 0 | 0 | 57.393 | 54.968 | 47.56 | 22.074 | 0 | 0 | 55.907 | 34.62 | [5 empty] | 0 | 0.434 | 15 | 2.0461 | 1.8697 | 1.6824 | 1.5385 | 0.33126 | 16.1898
2005-10-31 | 15:03 | 0 | 21.23 | 0 | 2 | 0 | 27.711 | 28.265 | 27.422 | 27.348 | 17.801 | 24.845 | 15.626 | 0 | 0 | 57.37 | 54.945 | 47.539 | 22.074 | 0 | 0 | 55.886 | 34.572 | [5 empty] | 0 | 0.363 | 16 | 2.0461 | 1.8697 | 1.6824 | 1.5385 | 0.33126 | 16.1898
2005-10-31 | 15:04 | 0 | 21.206 | 0 | 2 | 0 | 27.638 | 28.096 | 27.397 | 27.348 | 17.552 | 24.845 | 15.576 | 0 | 0 | 57.37 | 54.922 | 47.56 | 22.099 | 0 | 0 | 55.839 | 34.572 | [5 empty] | 0 | 0.29 | 17 | 2.0607 | 1.8836 | 1.683 | 1.5385 | 0.3451 | 16.7471
2005-10-31 | 15:05 | 0 | 21.255 | 0 | 2 | 0 | 27.711 | 28.023 | 27.397 | 27.446 | 17.381 | 24.725 | 15.724 | 0 | 0 | 57.325 | 54.945 | 47.56 | 22.123 | 0 | 0 | 55.816 | 34.572 | [5 empty] | 0 | 0.265 | 18 | 2.0176 | 1.8426 | 1.6812 | 1.5385 | 0.30414 | 15.0743
2005-10-31 | 15:06 | 0 | 21.284 | 0 | 2 | 0 | 37.844 | 27.981 | 27.522 | 27.378 | 23.043 | 24.825 | 15.707 | 0 | 0 | 57.398 | 54.926 | 47.544 | 22.128 | 0 | 0 | 55.827 | 34.565 | [5 empty] | 0 | 10.466 | 19 | 2.0225 | 1.8473 | 1.6814 | 1.5385 | 0.30884 | 15.2701
2005-10-31 | 15:07 | 0 | 21.201 | 0 | 2 | 0 | 46.039 | 29.101 | 27.319 | 27.27 | 23.803 | 24.622 | 15.646 | 1 | 0 | 57.27 | 54.842 | 47.553 | 22.069 | 0 | 0 | 55.806 | 34.519 | [5 empty] | 0 | 18.769 | 20 | 2.0403 | 1.8642 | 1.6821 | 1.5385 | 0.32573 | 15.9647
2005-10-31 | 15:08 | 1 | 21.208 | 0 | 2 | 0 | 46.459 | 42.75 | 27.255 | 27.231 | 24.291 | 24.653 | 15.629 | 1 | 0 | 57.3 | 54.873 | 47.605 | 22.076 | 0 | 0 | 55.813 | 34.526 | [5 empty] | 21.208 | 19.228 | 21 | 2.0452 | 1.8689 | 1.6823 | 1.5385 | 0.33043 | 16.1561
2005-10-31 | 15:09 | 0 | 21.177 | 0 | 2 | 0 | 46.062 | 45.88 | 27.343 | 27.174 | 24.067 | 24.742 | 15.646 | 2 | 0 | 57.316 | 54.819 | 47.483 | 22.045 | 0 | 0 | 55.783 | 34.519 | [5 empty] | 0 | 18.888 | 22 | 2.0403 | 1.8642 | 1.6821 | 1.5385 | 0.32573 | 15.9647
2005-10-31 | 15:10 | 0 | 21.233 | 1 | 2 | 0 | 45.773 | 46.116 | 27.326 | 27.351 | 23.785 | 24.629 | 15.752 | 1 | 0 | 57.3 | 54.873 | 47.605 | 22.076 | 0 | 0 | 55.837 | 34.526 | [5 empty] | 0 | 18.422 | 23 | 2.0094 | 1.8348 | 1.6809 | 1.5385 | 0.29638 | 14.7498
2005-10-31 | 15:11 | 0 | 21.208 | 0 | 2 | 0 | 45.931 | 45.84 | 27.542 | 27.206 | 23.665 | 24.798 | 15.777 | 1 | 0 | 57.3 | 54.849 | 47.537 | 22.076 | 0 | 0 | 55.86 | 34.55 | [5 empty] | 0 | 18.725 | 24 | 2.0021 | 1.8279 | 1.6806 | 1.5385 | 0.28946 | 14.4578
2005-10-31 | 15:12 | 0 | 21.177 | 0 | 2 | 0 | 46.039 | 45.901 | 27.559 | 27.174 | 23.658 | 24.668 | 15.795 | 1 | 0 | 57.27 | 54.842 | 47.553 | 22.045 | 0 | 0 | 55.76 | 34.495 | [5 empty] | 0 | 18.865 | 25 | 1.9969 | 1.8229 | 1.6804 | 1.5385 | 0.28448 | 14.2462
2005-10-31 | 15:13 | 1 | 21.152 | 0 | 2 | 0 | 46.132 | 46.132 | 27.633 | 27.319 | 23.778 | 24.742 | 15.795 | 1 | 0 | 57.316 | 54.819 | 47.621 | 22.045 | 0 | 0 | 55.76 | 34.519 | [5 empty] | 21.152 | 18.813 | 26 | 1.9969 | 1.8229 | 1.6804 | 1.5385 | 0.28448 | 14.2462
2005-10-31 | 15:14 | 0 | 21.201 | 0 | 2 | 0 | 46.428 | 46.2 | 27.799 | 27.488 | 23.994 | 24.742 | 15.82 | 2 | 0 | 57.316 | 54.842 | 47.53 | 22.069 | 0 | 0 | 55.713 | 34.565 | [5 empty] | 0 | 18.94 | 27 | 1.9896 | 1.816 | 1.6801 | 1.5385 | 0.27756 | 13.9506
2005-10-31 | 15:15 | 0 | 21.177 | 0 | 2 | 0 | 46.979 | 46.361 | 27.873 | 27.559 | 24.139 | 24.742 | 15.795 | 1 | 0 | 57.361 | 54.819 | 47.507 | 22.045 | 0 | 0 | 55.713 | 34.541 | [5 empty] | 0 | 19.42 | 28 | 1.9969 | 1.8229 | 1.6804 | 1.5385 | 0.28448 | 14.2462
2005-10-31 | 15:16 | 0 | 21.177 | 0 | 2 | 0 | 47.047 | 46.774 | 27.944 | 27.753 | 24.212 | 24.742 | 15.697 | 1 | 0 | 57.338 | 54.819 | 47.53 | 22.069 | 0 | 0 | 55.76 | 34.541 | [5 empty] | 0 | 19.294 | 29 | 2.0254 | 1.8501 | 1.6815 | 1.5385 | 0.31161 | 15.3848
2005-10-31 | 15:17 | 0 | 21.152 | 0 | 1 | 0 | 47.117 | 47.208 | 28.089 | 27.777 | 24.357 | 24.862 | 15.719 | 1 | 0 | 57.361 | 54.842 | 47.53 | 22.02 | 0 | 0 | 55.692 | 34.519 | [5 empty] | 0 | 19.34 | 30 | 2.019 | 1.844 | 1.6813 | 1.5385 | 0.30552 | 15.132
2005-10-31 | 15:18 | 0 | 21.177 | 0 | 2 | 0 | 47.301 | 47.301 | 28.064 | 27.824 | 24.477 | 24.791 | 15.719 | 1 | 0 | 57.405 | 54.842 | 47.507 | 22.045 | 0 | 0 | 55.713 | 34.519 | [5 empty] | 0 | 19.477 | 31 | 2.019 | 1.844 | 1.6813 | 1.5385 | 0.30552 | 15.132
2005-10-31 | 15:19 | 1 | 21.208 | 1 | 2 | 0 | 47.584 | 47.399 | 28.265 | 27.905 | 24.725 | 24.965 | 15.729 | 2 | 0 | 57.48 | 54.873 | 47.584 | 22.076 | 0 | 0 | 55.743 | 34.572 | [5 empty] | 21.208 | 19.679 | 32 | 2.0161 | 1.8412 | 1.6812 | 1.5385 | 0.30275 | 15.0166
2005-10-31 | 15:20 | 0 | 21.152 | 0 | 2 | 0 | 47.92 | 47.574 | 28.307 | 27.944 | 24.837 | 25.007 | 15.646 | 1 | 0 | 57.45 | 54.842 | 47.53 | 22.045 | 0 | 0 | 55.736 | 34.541 | [5 empty] | 0 | 19.976 | 33 | 2.0403 | 1.8642 | 1.6821 | 1.5385 | 0.32573 | 15.9647
2005-10-31 | 15:21 | 0 | 21.152 | 0 | 2 | 0 | 48.354 | 47.896 | 28.403 | 27.969 | 25.078 | 24.862 | 15.697 | 1 | 0 | 57.45 | 54.842 | 47.621 | 22.045 | 0 | 0 | 55.692 | 34.541 | [5 empty] | 0 | 20.385 | 34 | 2.0254 | 1.8501 | 1.6815 | 1.5385 | 0.31161 | 15.3848
2005-10-31 | 15:22 | 0 | 21.152 | 0 | 2 | 0 | 48.562 | 48.286 | 28.643 | 28.064 | 25.102 | 24.911 | 15.795 | 1 | 0 | 57.494 | 54.842 | 47.53 | 22.045 | 0 | 0 | 55.736 | 34.541 | [5 empty] | 0 | 20.498 | 35 | 1.9969 | 1.8229 | 1.6804 | 1.5385 | 0.28448 | 14.2462
2005-10-31 | 15:23 | 0 | 21.152 | 0 | 1 | 0 | 48.562 | 48.629 | 29.003 | 28.378 | 25.296 | 24.958 | 15.646 | 2 | 0 | 57.473 | 54.819 | 47.553 | 22.069 | 0 | 0 | 55.76 | 34.589 | [5 empty] | 0 | 20.184 | 36 | 2.0403 | 1.8642 | 1.6821 | 1.5385 | 0.32573 | 15.9647
2005-10-31 | 15:24 | 0 | 21.128 | 0 | 2 | 0 | 48.951 | 48.767 | 29.462 | 28.618 | 25.561 | 24.982 | 15.697 | 1 | 0 | 57.494 | 54.866 | 47.553 | 22.045 | 0 | 0 | 55.713 | 34.589 | [5 empty] | 0 | 20.333 | 37 | 2.0254 | 1.8501 | 1.6815 | 1.5385 | 0.31161 | 15.3848
2005-10-31 | 15:25 | 1 | 21.152 | 0 | 2 | 1 | 49.456 | 48.79 | 29.822 | 29.126 | 25.681 | 24.958 | 15.719 | 1 | 0 | 57.473 | 54.842 | 47.574 | 22.069 | 0 | 0 | 55.76 | 34.636 | [5 empty] | 21.152 | 20.33 | 38 | 2.019 | 1.844 | 1.6813 | 1.5385 | 0.30552 | 15.132
2005-10-31 | 15:26 | 0 | 21.159 | 0 | 2 | 0 | 44.135 | 49.257 | 30.362 | 29.543 | 23.665 | 25.208 | 15.802 | 1 | 0 | 57.523 | 54.873 | 47.56 | 22.076 | 0 | 0 | 55.771 | 34.646 | [5 empty] | 0 | 14.592 | 0 | 1.9949 | 1.821 | 1.6803 | 1.5385 | 0.28254 | 14.1637
2005-10-31 | 15:27 | 0 | 21.147 | 0 | 1 | 0 | 35.476 | 49.5 | 30.516 | 30.011 | 21.942 | 25.073 | 15.787 | 0 | 0 | 57.539 | 54.91 | 47.642 | 22.086 | 0 | 0 | 55.804 | 34.656 | [5 empty] | 0 | 5.465 | 1 | 1.9992 | 1.8252 | 0.93149 | 0.78947 | 1.0357 | 51.8043
2005-10-31 | 15:28 | 0 | 21.199 | 0 | 2 | 0 | 32.921 | 42.884 | 30.786 | 30.401 | 21.032 | 25.173 | 15.89 | 1 | 0 | 57.567 | 54.915 | 47.738 | 22.14 | 0 | 0 | 55.764 | 34.73 | [5 empty] | 0 | 2.52 | 2 | 1.9692 | 1.7966 | 0.93027 | 0.78947 | 1.0072 | 51.1455
2005-10-31 | 15:29 | 0 | 21.169 | 1 | 2 | 0 | 32.179 | 36.277 | 30.926 | 30.516 | 20.377 | 25.168 | 15.762 | 0 | 0 | 57.562 | 54.887 | 47.71 | 22.111 | 0 | 0 | 55.713 | 34.656 | [5 empty] | 0 | 1.663 | 3 | 2.0065 | 1.8321 | 0.93178 | 0.78947 | 1.0426 | 51.9612
2005-10-31 | 15:30 | 0 | 21.169 | 0 | 1 | 0 | 31.963 | 33.809 | 30.901 | 30.71 | 19.985 | 25.266 | 15.961 | 0 | 0 | 57.583 | 54.863 | 47.619 | 22.086 | 0 | 0 | 55.69 | 34.608 | [5 empty] | 0 | 1.253 | 4 | 1.9486 | 1.777 | 0.92943 | 0.78947 | 0.98752 | 50.6796
2005-10-31 | 15:31 | 0 | 21.169 | 0 | 2 | 0 | 31.914 | 32.986 | 30.83 | 30.806 | 19.913 | 25.168 | 15.986 | 0 | 0 | 57.562 | 54.887 | 47.689 | 22.111 | 0 | 0 | 55.645 | 34.632 | [5 empty] | 0 | 1.108 | 5 | 1.9413 | 1.7701 | 0.92914 | 0.78947 | 0.9806 | 50.5132
2005-10-31 | 15:32 | 0 | 21.169 | 0 | 1 | 0 | 31.818 | 32.586 | 30.781 | 30.83 | 19.739 | 25.168 | 16.059 | 0 | 0 | 57.562 | 54.887 | 47.733 | 22.086 | 0 | 0 | 55.599 | 34.632 | [5 empty] | 0 | 0.988 | 6 | 1.92 | 1.7499 | 0.92828 | 0.78947 | 0.9604 | 50.0201
2005-10-31 | 15:33 | 0 | 21.194 | 0 | 2 | 0 | 31.843 | 32.397 | 30.636 | 30.975 | 19.54 | 25.073 | 16.182 | 0 | 0 | 57.516 | 54.863 | 47.619 | 22.086 | 0 | 0 | 55.575 | 34.632 | [5 empty] | 0 | 0.868 | 7 | 1.8842 | 1.7158 | 0.92683 | 0.78947 | 0.92635 | 49.164
2005-10-31 | 15:34 | 0 | 21.169 | 0 | 2 | 0 | 31.72 | 32.252 | 30.421 | 30.781 | 19.515 | 25.122 | 16.232 | 0 | 0 | 57.516 | 54.842 | 47.642 | 22.133 | 0 | 0 | 55.666 | 34.632 | [5 empty] | 0 | 0.939 | 8 | 1.8696 | 1.702 | 0.92624 | 0.78947 | 0.91251 | 48.8066
2005-10-31 | 15:35 | 0 | 21.169 | 0 | 1 | 0 | 31.625 | 32.13 | 30.131 | 30.59 | 21.194 | 25.193 | 16.232 | 0 | 0 | 57.494 | 54.842 | 47.71 | 22.111 | 0 | 0 | 55.666 | 34.584 | [5 empty] | 0 | 1.035 | 9 | 1.8696 | 1.702 | 0.92624 | 0.78947 | 0.91251 | 48.8066
2005-10-31 | 15:36 | 0 | 21.169 | 0 | 2 | 0 | 42.174 | 32.059 | 29.795 | 30.347 | 25.723 | 25.144 | 16.232 | 0 | 0 | 57.471 | 54.819 | 47.572 | 22.111 | 0 | 0 | 55.713 | 34.584 | [5 empty] | 0 | 11.827 | 10 | 1.8696 | 1.702 | 0.92624 | 0.78947 | 0.91251 | 48.8066
2005-10-31 | 15:37 | 0 | 21.147 | 0 | 2 | 0 | 45.257 | 32.059 | 29.462 | 30.256 | 23.271 | 25.173 | 16.212 | 1 | 0 | 57.432 | 54.824 | 47.6 | 22.116 | 0 | 0 | 55.741 | 34.589 | [5 empty] | 0 | 15.001 | 11 | 1.8755 | 1.7075 | 0.92647 | 0.78947 | 0.91804 | 48.9502
2005-10-31 | 15:38 | 0 | 21.169 | 0 | 1 | 0 | 35.689 | 41.822 | 29.143 | 29.866 | 21.338 | 25.122 | 16.084 | 0 | 0 | 57.405 | 54.796 | 47.572 | 22.111 | 0 | 0 | 55.713 | 34.584 | [5 empty] | 0 | 5.823 | 12 | 1.9127 | 1.7429 | 0.92798 | 0.78947 | 0.95348 | 49.8487
2005-10-31 | 15:39 | 0 | 21.169 | 0 | 2 | 0 | 32.539 | 43.303 | 28.854 | 29.553 | 20.282 | 25.122 | 16.008 | 1 | 0 | 57.359 | 54.796 | 47.595 | 22.111 | 0 | 0 | 55.713 | 34.538 | [5 empty] | 0 | 2.986 | 13 | 1.9349 | 1.764 | 0.92888 | 0.78947 | 0.97451 | 50.3657
2005-10-31 | 15:40 | 0 | 21.223 | 0 | 1 | 0 | 31.318 | 36.328 | 28.739 | 29.197 | 19.892 | 25.222 | 16.016 | 0 | 0 | 57.432 | 54.8 | 47.532 | 22.116 | 0 | 0 | 55.788 | 34.519 | [5 empty] | 0 | 2.121 | 14 | 1.9325 | 1.7618 | 0.92878 | 0.78947 | 0.9723 | 50.3119
2005-10-31 | 15:41 | 0 | 21.169 | 1 | 2 | 0 | 30.734 | 33.175 | 28.422 | 28.927 | 19.812 | 25.122 | 16.109 | 0 | 0 | 57.313 | 54.772 | 47.528 | 22.111 | 0 | 0 | 55.713 | 34.514 | [5 empty] | 0 | 1.807 | 15 | 1.9055 | 1.736 | 0.92769 | 0.78947 | 0.94656 | 49.676
2005-10-31 | 15:42 | 0 | 21.169 | 0 | 1 | 0 | 30.205 | 31.914 | 28.278 | 28.542 | 19.417 | 25.073 | 15.935 | 0 | 0 | 57.382 | 54.749 | 47.528 | 22.086 | 0 | 0 | 55.645 | 34.514 | [5 empty] | 0 | 1.663 | 16 | 1.9561 | 1.7842 | 0.92974 | 0.78947 | 0.99472 | 50.8514
2005-10-31 | 15:43 | 0 | 21.123 | 0 | 2 | 0 | 29.866 | 31.166 | 28.035 | 28.422 | 19.221 | 24.977 | 15.86 | 0 | 0 | 57.313 | 54.705 | 47.504 | 22.086 | 0 | 0 | 55.645 | 34.56 | [5 empty] | 0 | 1.444 | 17 | 1.978 | 1.805 | 0.93063 | 0.78947 | 1.0155 | 51.3395
2005-10-31 | 15:44 | 0 | 21.123 | 0 | 1 | 0 | 29.506 | 30.734 | 28.013 | 28.253 | 19.096 | 25.024 | 15.812 | 0 | 0 | 57.313 | 54.705 | 47.504 | 22.086 | 0 | 0 | 55.69 | 34.538 | [5 empty] | 0 | 1.253 | 18 | 1.9919 | 1.8182 | 0.93119 | 0.78947 | 1.0288 | 51.6462
2005-10-31 | 15:45 | 0 | 21.098 | 0 | 2 | 0 | 29.217 | 30.325 | 27.915 | 28.155 | 19.176 | 24.958 | 15.817 | 0 | 0 | 57.297 | 54.733 | 47.486 | 22.14 | 0 | 0 | 55.65 | 34.567 | [5 empty] | 0 | 1.062 | 19 | 1.9905 | 1.8169 | 0.93113 | 0.78947 | 1.0274 | 51.6145
2005-10-31 | 15:46 | 0 | 21.123 | 0 | 1 | 0 | 29.072 | 29.938 | 27.844 | 28.084 | 18.972 | 24.928 | 15.762 | 0 | 0 | 57.27 | 54.681 | 47.551 | 22.086 | 0 | 0 | 55.666 | 34.467 | [5 empty] | 0 | 0.988 | 20 | 2.0065 | 1.8321 | 0.93178 | 0.78947 | 1.0426 | 51.9612
2005-10-31 | 15:47 | 0 | 21.162 | 0 | 2 | 0 | 34.67 | 29.712 | 27.785 | 27.954 | 25.063 | 24.943 | 15.852 | 0 | 0 | 57.284 | 54.695 | 47.565 | 22.125 | 0 | 0 | 55.636 | 34.529 | [5 empty] | 0 | 6.716 | 21 | 1.9803 | 1.8072 | 0.93072 | 0.78947 | 1.0177 | 51.3909
2005-10-31 | 15:48 | 0 | 21.113 | 0 | 1 | 0 | 46.51 | 29.423 | 27.689 | 27.858 | 22.461 | 24.918 | 15.827 | 1 | 0 | 57.238 | 54.672 | 47.518 | 22.101 | 0 | 0 | 55.566 | 34.529 | [5 empty] | 0 | 18.652 | 22 | 1.9876 | 1.8141 | 0.93102 | 0.78947 | 1.0246 | 51.5508
2005-10-31 | 15:49 | 0 | 21.194 | 0 | 2 | 0 | 34.959 | 36.557 | 27.696 | 27.961 | 20.568 | 25.215 | 15.908 | 0 | 0 | 57.245 | 54.726 | 47.434 | 22.157 | 0 | 0 | 55.596 | 34.584 | [5 empty] | 0 | 6.998 | 23 | 1.964 | 1.7917 | 0.93006 | 0.78947 | 1.0022 | 51.0284
2005-10-31 | 15:50 | 0 | 21.169 | 0 | 1 | 0 | 30.781 | 43.042 | 27.625 | 27.817 | 19.689 | 24.904 | 15.81 | 0 | 0 | 57.224 | 54.635 | 47.458 | 22.108 | 0 | 0 | 55.62 | 34.56 | [5 empty] | 0 | 2.964 | 24 | 1.9925 | 1.8188 | 0.93122 | 0.78947 | 1.0293 | 51.6589
2005-10-31 | 15:51 | 0 | 21.137 | 0 | 2 | 0 | 29.401 | 35.352 | 27.64 | 27.809 | 19.161 | 24.847 | 15.827 | 1 | 0 | 57.172 | 54.604 | 47.495 | 22.101 | 0 | 0 | 55.589 | 34.529 | [5 empty] | 0 | 1.592 | 25 | 1.9876 | 1.8141 | 0.93102 | 0.78947 | 1.0246 | 51.5508
2005-10-31 | 15:52 | 0 | 21.113 | 1 | 2 | 0 | 28.822 | 31.374 | 27.738 | 27.665 | 18.987 | 24.943 | 15.802 | 0 | 0 | 57.195 | 54.604 | 47.404 | 22.076 | 0 | 0 | 55.613 | 34.529 | [5 empty] | 0 | 1.157 | 26 | 1.9949 | 1.821 | 0.93131 | 0.78947 | 1.0315 | 51.7096
2005-10-31 | 15:53 | 0 | 21.145 | 0 | 1 | 0 | 28.589 | 29.984 | 27.792 | 27.625 | 18.849 | 24.967 | 15.802 | 0 | 0 | 57.195 | 54.625 | 47.381 | 22.101 | 0 | 0 | 55.566 | 34.505 | [5 empty] | 0 | 0.964 | 27 | 1.9949 | 1.821 | 0.93131 | 0.78947 | 1.0315 | 51.7096
2005-10-31 | 15:54 | 0 | 21.145 | 0 | 2 | 0 | 28.469 | 29.408 | 27.817 | 27.672 | 18.922 | 24.926 | 15.835 | 0 | 0 | 57.224 | 54.635 | 47.388 | 22.133 | 0 | 0 | 55.573 | 34.488 | [5 empty] | 0 | 0.797 | 28 | 1.9852 | 1.8119 | 0.93092 | 0.78947 | 1.0224 | 51.4998
2005-10-31 | 15:55 | 0 | 21.113 | 0 | 1 | 0 | 28.314 | 29.062 | 27.714 | 27.714 | 18.691 | 24.798 | 15.802 | 0 | 0 | 57.149 | 54.581 | 47.381 | 22.125 | 0 | 0 | 55.566 | 34.505 | [5 empty] | 0 | 0.6 | 29 | 1.9949 | 1.821 | 0.93131 | 0.78947 | 1.0315 | 51.7096
2005-10-31 | 15:56 | 0 | 21.169 | 0 | 2 | 0 | 28.3 | 28.854 | 27.721 | 27.77 | 18.701 | 25.024 | 15.885 | 0 | 0 | 57.179 | 54.611 | 47.364 | 22.133 | 0 | 0 | 55.62 | 34.536 | [5 empty] | 0 | 0.53 | 30 | 1.9707 | 1.798 | 0.93033 | 0.78947 | 1.0086 | 51.178
2005-10-31 | 15:57 | 0 | 21.137 | 0 | 1 | 0 | 28.339 | 28.677 | 27.714 | 27.738 | 18.668 | 25.016 | 15.827 | 0 | 0 | 57.195 | 54.581 | 47.357 | 22.148 | 0 | 0 | 55.543 | 34.505 | [5 empty] | 0 | 0.601 | 31 | 1.9876 | 1.8141 | 0.93102 | 0.78947 | 1.0246 | 51.5508
2005-10-31 | 15:58 | 0 | 21.169 | 0 | 2 | 0 | 30.273 | 28.611 | 27.552 | 27.745 | 24.759 | 24.904 | 15.737 | 0 | 0 | 57.11 | 54.565 | 47.434 | 22.157 | 0 | 0 | 55.596 | 34.536 | [5 empty] | 0 | 2.528 | 32 | 2.0138 | 1.839 | 0.93208 | 0.78947 | 1.0495 | 52.117
2005-10-31 | 15:59 | 0 | 21.137 | 0 | 1 | 0 | 46.968 | 28.484 | 27.449 | 27.569 | 22.751 | 24.847 | 15.729 | 0 | 0 | 57.081 | 54.511 | 47.404 | 22.125 | 0 | 0 | 55.522 | 34.481 | [5 empty] | 0 | 19.399 | 33 | 2.0161 | 1.8412 | 0.93217 | 0.78947 | 1.0517 | 52.1666
2005-10-31 | 16:00 | 0 | 21.12 | 0 | 2 | 0 | 35.122 | 34.23 | 27.407 | 27.625 | 20.473 | 25.048 | 15.712 | 1 | 0 | 57.11 | 54.541 | 47.32 | 22.133 | 0 | 0 | 55.529 | 34.536 | [5 empty] | 0 | 7.497 | 34 | 2.0211 | 1.8459 | 0.93237 | 0.78947 | 1.0564 | 52.2717
2005-10-31 | 16:01 | 0 | 21.113 | 0 | 2 | 0 | 30.46 | 42.566 | 27.4 | 27.495 | 19.53 | 24.872 | 15.654 | 0 | 0 | 57.11 | 54.541 | 47.273 | 22.157 | 0 | 0 | 55.505 | 34.56 | [5 empty] | 0 | 2.965 | 35 | 2.038 | 1.862 | 0.93306 | 0.78947 | 1.0725 | 52.6262
2005-10-31 | 16:02 | 0 | 21.12 | 0 | 1 | 0 | 29.07 | 35.029 | 27.36 | 27.432 | 19.02 | 24.999 | 15.614 | 0 | 0 | 57.09 | 54.541 | 47.479 | 22.157 | 0 | 0 | 55.505 | 34.605 | [5 empty] | 0 | 1.638 | 36 | 2.0496 | 1.873 | 0.93353 | 0.78947 | 1.0836 | 52.8674
2005-10-31 | 16:03 | 0 | 21.113 | 0 | 2 | 0 | 28.459 | 30.965 | 27.424 | 27.4 | 18.643 | 25.063 | 15.556 | 0 | 0 | 57.06 | 54.511 | 47.266 | 22.125 | 0 | 0 | 55.543 | 34.553 | [5 empty] | 0 | 1.059 | 37 | 2.0665 | 1.8891 | 0.93421 | 0.78947 | 1.0996 | 53.2122
2005-10-31 | 16:04 | 0 | 21.137 | 1 | 2 | 0 | 28.219 | 29.521 | 27.618 | 27.375 | 18.47 | 25.038 | 15.556 | 0 | 0 | 57.06 | 54.488 | 47.266 | 22.101 | 0 | 0 | 55.543 | 34.529 | [5 empty] | 0 | 0.844 | 38 | 2.0665 | 1.8891 | 0.93421 | 0.78947 | 1.0996 | 53.2122
2005-10-31 | 16:05 | 0 | 21.113 | 0 | 1 | 0 | 28.123 | 28.942 | 27.449 | 27.618 | 18.321 | 24.894 | 15.604 | 0 | 0 | 57.014 | 54.467 | 47.313 | 22.125 | 0 | 0 | 55.522 | 34.505 | [5 empty] | 0 | 0.505 | 39 | 2.0525 | 1.8758 | 0.93365 | 0.78947 | 1.0863 | 52.9272
2005-10-31 | 16:06 | 0 | 21.088 | 0 | 2 | 0 | 27.978 | 28.628 | 27.473 | 27.52 | 18.223 | 24.894 | 15.382 | 0 | 0 | 56.992 | 54.443 | 47.381 | 22.125 | 0 | 0 | 55.522 | 34.481 | [5 empty] | 0 | 0.458 | 40 | 2.1172 | 1.9373 | 0.93627 | 0.78947 | 1.1478 | 54.2136
2005-10-31 | 16:07 | 0 | 21.088 | 0 | 1 | 0 | 27.954 | 28.388 | 27.495 | 27.593 | 18.1 | 24.872 | 15.506 | 1 | 0 | 57.014 | 54.443 | 47.357 | 22.125 | 0 | 0 | 55.543 | 34.457 | [5 empty] | 0 | 0.361 | 41 | 2.0811 | 1.9029 | 0.9348 | 0.78947 | 1.1135 | 53.5049
2005-10-31 | 16:08 | 0 | 21.12 | 0 | 2 | 0 | 27.915 | 28.324 | 27.576 | 27.505 | 18.082 | 24.904 | 15.44 | 0 | 0 | 57.067 | 54.45 | 47.273 | 22.157 | 0 | 0 | 55.552 | 34.464 | [5 empty] | 0 | 0.41 | 42 | 2.1003 | 1.9212 | 0.93558 | 0.78947 | 1.1317 | 53.8851
2005-10-31 | 16:09 | 1 | 21.113 | 0 | 2 | 0 | 28.412 | 28.17 | 27.4 | 27.544 | 24.872 | 24.774 | 15.234 | 0 | 0 | 56.992 | 54.467 | 47.243 | 22.148 | 0 | 0 | 55.498 | 34.433 | [5 empty] | 21.113 | 0.868 | 43 | 2.1603 | 1.9782 | 0.93801 | 0.78947 | 1.1888 | 55.0284
2005-10-31 | 16:10 | 0 | 21.137 | 0 | 2 | 0 | 45.499 | 28.17 | 27.375 | 27.375 | 22.341 | 24.847 | 15.184 | 0 | 0 | 56.946 | 54.397 | 47.22 | 22.125 | 0 | 0 | 55.475 | 34.412 | [5 empty] | 0 | 18.124 | 44 | 2.1748 | 1.9921 | 0.9386 | 0.78947 | 1.2026 | 55.2963
2005-10-31 | 16:11 | 0 | 21.088 | 0 | 2 | 0 | 34.457 | 35.232 | 27.4 | 27.351 | 20.149 | 24.943 | 15.086 | 0 | 0 | 56.925 | 54.397 | 47.243 | 22.101 | 0 | 0 | 55.475 | 34.388 | [5 empty] | 0 | 7.106 | 45 | 2.2034 | 2.0192 | 0.93976 | 0.78947 | 1.2297 | 55.8113
2005-10-31 | 16:12 | 0 | 21.056 | 0 | 2 | 0 | 29.92 | 40.607 | 27.272 | 27.417 | 19.055 | 24.791 | 15.028 | 1 | 0 | 56.896 | 54.366 | 47.213 | 22.094 | 0 | 0 | 55.398 | 34.357 | [5 empty] | 0 | 2.503 | 46 | 2.2202 | 2.0352 | 0.94044 | 0.78947 | 1.2458 | 56.1098
2005-10-31 | 16:13 | 0 | 21.162 | 0 | 1 | 0 | 28.653 | 33.048 | 27.495 | 27.424 | 18.618 | 24.992 | 15.086 | 0 | 0 | 56.946 | 54.443 | 47.266 | 22.148 | 0 | 0 | 55.498 | 34.433 | [5 empty] | 0 | 1.229 | 47 | 2.2034 | 2.0192 | 0.93976 | 0.78947 | 1.2297 | 55.8113
2005-10-31 | 16:14 | 0 | 21.137 | 0 | 2 | 0 | 28.148 | 29.977 | 27.375 | 27.4 | 18.248 | 24.894 | 14.887 | 0 | 0 | 56.925 | 54.397 | 47.243 | 22.125 | 0 | 0 | 55.522 | 34.457 | [5 empty] | 0 | 0.748 | 48 | 2.2613 | 2.0743 | 0.94211 | 0.78947 | 1.2848 | 56.8169
2005-10-31 | 16:15 | 0 | 21.162 | 0 | 2 | 0 | 28.003 | 28.918 | 27.424 | 27.375 | 18.075 | 24.798 | 14.864 | 0 | 0 | 56.925 | 54.42 | 47.266 | 22.148 | 0 | 0 | 55.475 | 34.481 | [5 empty] | 0 | 0.628 | 49 | 2.268 | 2.0806 | 0.94238 | 0.78947 | 1.2912 | 56.9299
2005-10-31 | 16:16 | 0 | 21.137 | 1 | 2 | 0 | 27.834 | 28.508 | 27.473 | 27.28 | 17.851 | 24.918 | 14.814 | 0 | 0 | 56.969 | 54.397 | 47.22 | 22.125 | 0 | 0 | 55.522 | 34.457 | [5 empty] | 0 | 0.554 | 50 | 2.2826 | 2.0945 | 0.94297 | 0.78947 | 1.305 | 57.1731
2005-10-31 | 16:17 | 0 | 21.162 | 0 | 2 | 0 | 27.76 | 28.314 | 27.449 | 27.351 | 17.778 | 24.798 | 14.814 | 0 | 0 | 56.925 | 54.42 | 47.22 | 22.148 | 0 | 0 | 55.522 | 34.457 | [5 empty] | 0 | 0.409 | 51 | 2.2826 | 2.0945 | 0.94297 | 0.78947 | 1.305 | 57.1731
2005-10-31 | 16:18 | 0 | 21.162 | 0 | 2 | 0 | 27.714 | 28.148 | 27.4 | 27.351 | 17.655 | 24.894 | 14.741 | 0 | 0 | 56.946 | 54.397 | 47.175 | 22.148 | 0 | 0 | 55.498 | 34.388 | [5 empty] | 0 | 0.363 | 52 | 2.3038 | 2.1147 | 0.94383 | 0.78947 | 1.3252 | 57.5226
2005-10-31 | 16:19 | 0 | 21.13 | 0 | 1 | 0 | 27.657 | 28.091 | 27.368 | 27.319 | 17.424 | 24.815 | 14.658 | 0 | 0 | 56.916 | 54.322 | 47.145 | 22.069 | 0 | 0 | 55.398 | 34.357 | [5 empty] | 0 | 0.338 | 53 | 2.328 | 2.1377 | 0.94481 | 0.78947 | 1.3482 | 57.9123
2005-10-31 | 16:20 | 0 | 21.184 | 0 | 2 | 0 | 27.665 | 28.003 | 27.4 | 27.375 | 23.209 | 24.872 | 14.691 | 1 | 0 | 56.925 | 54.373 | 47.196 | 22.125 | 0 | 0 | 55.428 | 34.433 | [5 empty] | 0 | 0.29 | 54 | 2.3184 | 2.1285 | 0.94442 | 0.78947 | 1.3391 | 57.7583
2005-10-31 | 16:21 | 0 | 21.152 | 0 | 2 | 0 | 44.645 | 27.873 | 27.417 | 27.297 | 22.574 | 24.791 | 14.731 | 0 | 0 | 56.827 | 54.343 | 47.236 | 22.14 | 0 | 0 | 55.398 | 34.402 | [5 empty] | 0 | 17.348 | 55 | 2.3067 | 2.1175 | 0.94395 | 0.78947 | 1.328 | 57.57
2005-10-31 | 16:22 | 0 | 21.152 | 0 | 2 | 0 | 34.498 | 35.014 | 27.297 | 27.343 | 20.48 | 24.646 | 14.709 | 0 | 0 | 56.827 | 54.299 | 47.145 | 22.116 | 0 | 0 | 55.375 | 34.402 | [5 empty] | 0 | 7.155 | 56 | 2.3131 | 2.1235 | 0.94421 | 0.78947 | 1.3341 | 57.6738
2005-10-31 | 16:23 | 0 | 21.13 | 0 | 2 | 0 | 29.705 | 39.736 | 27.297 | 27.319 | 19.153 | 24.766 | 14.608 | 1 | 0 | 56.896 | 54.322 | 47.122 | 22.116 | 0 | 0 | 55.398 | 34.45 | [5 empty] | 0 | 2.386 | 57 | 2.3426 | 2.1515 | 0.9454 | 0.78947 | 1.362 | 58.1431
2005-10-31 | 16:24 | 0 | 21.152 | 0 | 2 | 0 | 28.427 | 32.235 | 27.319 | 27.513 | 18.437 | 24.766 | 14.658 | 0 | 0 | 56.827 | 54.299 | 47.145 | 22.116 | 0 | 0 | 55.354 | 34.45 | [5 empty] | 0 | 0.914 | 58 | 2.328 | 2.1377 | 0.94481 | 0.78947 | 1.3482 | 57.9123
2005-10-31 | 16:25 | 0 | 21.152 | 0 | 2 | 0 | 28.018 | 29.489 | 27.417 | 27.223 | 18.017 | 24.717 | 14.608 | 0 | 0 | 56.827 | 54.299 | 47.152 | 22.172 | 0 | 0 | 55.337 | 34.457 | [5 empty] | 0 | 0.795 | 59 | 2.3426 | 2.1515 | 0.9454 | 0.78947 | 1.362 | 58.1431
2005-10-31 | 16:26 | 0 | 21.177 | 0 | 2 | 0 | 27.826 | 28.67 | 27.463 | 27.272 | 17.796 | 24.575 | 14.583 | 0 | 0 | 56.85 | 54.299 | 47.145 | 22.116 | 0 | 0 | 55.33 | 34.426 | [5 empty] | 0 | 0.554 | 60 | 2.3498 | 2.1584 | 0.94569 | 0.78947 | 1.369 | 58.2575
2005-10-31 | 16:27 | 0 | 21.13 | 1 | 2 | 0 | 27.682 | 28.307 | 27.368 | 27.223 | 17.72 | 24.597 | 14.535 | 0 | 0 | 56.85 | 54.299 | 47.122 | 22.116 | 0 | 0 | 55.33 | 34.426 | [5 empty] | 0 | 0.459 | 61 | 2.3638 | 2.1717 | 0.94626 | 0.78947 | 1.3822 | 58.4751
2005-10-31 | 16:28 | 0 | 21.152 | 0 | 2 | 0 | 27.633 | 28.138 | 27.297 | 27.248 | 17.499 | 24.695 | 14.46 | 0 | 0 | 56.873 | 54.275 | 47.122 | 22.116 | 0 | 0 | 55.307 | 34.402 | [5 empty] | 0 | 0.385 | 62 | 2.3856 | 2.1925 | 0.94715 | 0.78947 | 1.403 | 58.8099
2005-10-31 | 16:29 | 0 | 21.152 | 0 | 2 | 0 | 27.633 | 28.042 | 27.297 | 27.272 | 17.449 | 24.575 | 14.56 | 0 | 0 | 56.873 | 54.299 | 47.122 | 22.14 | 0 | 0 | 55.216 | 34.402 | [5 empty] | 0 | 0.361 | 63 | 2.3565 | 2.1648 | 0.94597 | 0.78947 | 1.3753 | 58.3621
2005-10-31 | 16:30 | 0 | 21.13 | 0 | 3 | 0 | 27.586 | 27.897 | 27.223 | 27.223 | 17.275 | 24.597 | 14.412 | 0 | 0 | 56.804 | 54.252 | 47.145 | 22.116 | 0 | 0 | 55.216 | 34.38 | [5 empty] | 0 | 0.363 | 64 | 2.3996 | 2.2058 | 0.94771 | 0.78947 | 1.4163 | 59.0211
2005-10-31 | 16:31 | 0 | 21.098 | 0 | 2 | 0 | 27.481 | 27.866 | 27.191 | 27.191 | 21.409 | 24.519 | 14.329 | 0 | 0 | 56.775 | 54.245 | 47.045 | 22.062 | 0 | 0 | 55.277 | 34.325 | [5 empty] | 0 | 0.29 | 65 | 2.4238 | 2.2287 | 0.94869 | 0.78947 | 1.4393 | 59.3804
2005-10-31 | 16:32 | 0 | 21.152 | 0 | 2 | 0 | 43.451 | 27.826 | 27.248 | 27.177 | 24.188 | 24.575 | 14.435 | 0 | 0 | 56.804 | 54.252 | 47.098 | 22.094 | 0 | 0 | 55.354 | 34.357 | [5 empty] | 0 | 16.274 | 66 | 2.3929 | 2.1994 | 0.94744 | 0.78947 | 1.4099 | 58.9202
2005-10-31 | 16:33 | 0 | 21.13 | 0 | 2 | 0 | 46.043 | 35.273 | 27.152 | 27.103 | 24.526 | 24.551 | 14.362 | 2 | 0 | 56.804 | 54.229 | 47.166 | 22.116 | 0 | 0 | 55.284 | 34.402 | [5 empty] | 0 | 18.94 | 67 | 2.4142 | 2.2196 | 0.9483 | 0.78947 | 1.4301 | 59.2384
2005-10-31 | 16:34 | 1 | 21.177 | 0 | 2 | 0 | 46.456 | 44.921 | 27.199 | 27.103 | 24.791 | 24.551 | 14.435 | 1 | 0 | 56.827 | 54.229 | 47.052 | 22.094 | 0 | 0 | 55.26 | 34.38 | [5 empty] | 21.177 | 19.353 | 68 | 2.3929 | 2.1994 | 0.94744 | 0.78947 | 1.4099 | 58.9202
2005-10-31 | 16:35 | 0 | 21.12 | 0 | 2 | 0 | 46.312 | 46.151 | 27.216 | 27 | 24.59 | 24.543 | 14.304 | 1 | 0 | 56.754 | 54.222 | 47.068 | 22.062 | 0 | 0 | 55.253 | 34.349 | [5 empty] | 0 | 19.312 | 69 | 2.4311 | 2.2357 | 0.94899 | 0.78947 | 1.4462 | 59.4872
2005-10-31 | 16:36 | 0 | 21.12 | 0 | 2 | 0 | 46.197 | 46.335 | 27.311 | 27.096 | 24.085 | 24.519 | 14.279 | 2 | 0 | 56.754 | 54.222 | 47.021 | 22.084 | 0 | 0 | 55.253 | 34.325 | [5 empty] | 0 | 19.101 | 70 | 2.4384 | 2.2426 | 0.94928 | 0.78947 | 1.4531 | 59.5934
2005-10-31 | 16:37 | 0 | 21.177 | 1 | 2 | 0 | 46.09 | 46.295 | 27.513 | 27.177 | 23.996 | 24.597 | 14.289 | 1 | 0 | 56.804 | 54.299 | 47.166 | 22.238 | 0 | 0 | 55.284 | 34.474 | [5 empty] | 0 | 18.913 | 71 | 2.4354 | 2.2398 | 0.94916 | 0.78947 | 1.4503 | 59.551
2005-10-31 | 16:38 | 0 | 21.12 | 0 | 2 | 0 | 46.104 | 46.312 | 27.53 | 27.265 | 24.06 | 24.59 | 14.231 | 1 | 0 | 56.798 | 54.222 | 47.021 | 22.062 | 0 | 0 | 55.23 | 34.325 | [5 empty] | 0 | 18.839 | 72 | 2.4523 | 2.2559 | 0.94985 | 0.78947 | 1.4664 | 59.7955
2005-10-31 | 16:39 | 1 | 21.12 | 0 | 2 | 0 | 46.47 | 46.288 | 27.696 | 27.385 | 23.891 | 24.565 | 14.256 | 1 | 0 | 56.82 | 54.222 | 47.091 | 22.108 | 0 | 0 | 55.23 | 34.349 | [5 empty] | 21.12 | 19.085 | 73 | 2.4451 | 2.2489 | 0.94955 | 0.78947 | 1.4595 | 59.6906
2005-10-31 | 16:40 | 0 | 21.145 | 0 | 2 | 0 | 46.197 | 46.54 | 27.77 | 27.41 | 24.036 | 24.663 | 14.304 | 2 | 0 | 56.866 | 54.222 | 47.091 | 22.062 | 0 | 0 | 55.277 | 34.349 | [5 empty] | 0 | 18.787 | 74 | 2.4311 | 2.2357 | 0.94899 | 0.78947 | 1.4462 | 59.4872
2005-10-31 | 16:41 | 0 | 21.12 | 0 | 2 | 1 | 46.356 | 46.494 | 27.939 | 27.674 | 24.085 | 24.614 | 14.13 | 1 | 0 | 56.82 | 54.198 | 47.091 | 22.037 | 0 | 0 | 55.23 | 34.371 | [5 empty] | 0 | 18.682 | 75 | 2.4817 | 2.2838 | 0.95104 | 0.78947 | 1.4943 | 60.2134
2005-10-31 | 16:42 | 0 | 21.145 | 0 | 2 | 0 | 46.678 | 46.517 | 27.986 | 27.65 | 24.229 | 24.639 | 14.057 | 1 | 0 | 56.866 | 54.222 | 47.045 | 22.037 | 0 | 0 | 55.23 | 34.325 | [5 empty] | 0 | 19.028 | 0 | 2.503 | 2.304 | 0.9519 | 0.78947 | 1.5145 | 60.5093
2005-10-31 | 16:43 | 0 | 21.169 | 0 | 2 | 0 | 46.792 | 46.884 | 28.01 | 27.696 | 24.276 | 24.639 | 14.007 | 1 | 0 | 56.909 | 54.245 | 47.091 | 22.062 | 0 | 0 | 55.3 | 34.325 | [5 empty] | 0 | 19.096 | 1 | 2.5176 | 2.3179 | 1.0454 | 0.88235 | 1.4355 | 57.0198
2005-10-31 | 16:44 | 0 | 21.145 | 0 | 2 | 0 | 46.863 | 47.068 | 28.13 | 27.866 | 24.445 | 24.639 | 13.959 | 2 | 0 | 56.909 | 54.268 | 47.068 | 22.084 | 0 | 0 | 55.253 | 34.349 | [5 empty] | 0 | 18.997 | 2 | 2.5315 | 2.3311 | 1.0459 | 0.88235 | 1.4488 | 57.2298
2005-10-31 | 16:45 | 1 | 21.169 | 0 | 2 | 0 | 46.863 | 47.068 | 28.444 | 27.915 | 24.565 | 24.808 | 13.909 | 1 | 0 | 56.932 | 54.292 | 47.136 | 22.084 | 0 | 0 | 55.23 | 34.371 | [5 empty] | 21.169 | 18.948 | 3 | 2.5461 | 2.345 | 1.0465 | 0.88235 | 1.4626 | 57.4461
2005-10-31 | 16:46 | 0 | 21.169 | 0 | 2 | 0 | 46.998 | 47.136 | 28.709 | 28.035 | 24.71 | 24.663 | 13.859 | 1 | 0 | 56.932 | 54.222 | 47.091 | 22.062 | 0 | 0 | 55.207 | 34.349 | [5 empty] | 0 | 18.963 | 4 | 2.5607 | 2.3588 | 1.0471 | 0.88235 | 1.4765 | 57.66
2005-10-31 | 16:47 | 0 | 21.177 | 1 | 2 | 0 | 47.486 | 47.096 | 29.246 | 28.307 | 24.742 | 24.813 | 13.793 | 1 | 0 | 56.937 | 54.273 | 47.119 | 22.067 | 0 | 0 | 55.19 | 34.354 | [5 empty] | 0 | 19.179 | 5 | 2.5799 | 2.3771 | 1.0479 | 0.88235 | 1.4947 | 57.9386
2005-10-31 | 16:48 | 0 | 21.177 | 0 | 2 | 0 | 47.439 | 47.532 | 29.751 | 28.837 | 24.933 | 24.886 | 13.841 | 1 | 0 | 56.937 | 54.25 | 47.234 | 22.067 | 0 | 0 | 55.19 | 34.33 | [5 empty] | 0 | 18.602 | 6 | 2.5659 | 2.3638 | 1.0473 | 0.88235 | 1.4815 | 57.7364
2005-10-31 | 16:49 | 0 | 21.098 | 0 | 2 | 0 | 47.777 | 47.642 | 30.325 | 29.288 | 24.928 | 24.808 | 13.763 | 2 | 0 | 56.955 | 54.198 | 47.068 | 22.015 | 0 | 0 | 55.139 | 34.256 | [5 empty] | 0 | 18.489 | 7 | 2.5886 | 2.3854 | 1.0482 | 0.88235 | 1.503 | 58.0638
2005-10-31 | 16:50 | 0 | 21.123 | 0 | 2 | 0 | 48.375 | 47.824 | 30.781 | 29.962 | 25.146 | 24.808 | 13.64 | 1 | 0 | 56.909 | 54.175 | 47.115 | 22.037 | 0 | 0 | 55.116 | 34.278 | [5 empty] | 0 | 18.413 | 8 | 2.6244 | 2.4194 | 1.0497 | 0.88235 | 1.5371 | 58.5687
2005-10-31 | 16:51 | 1 | 21.177 | 0 | 2 | 0 | 49.112 | 48.289 | 31.22 | 30.401 | 25.441 | 24.813 | 13.67 | 1 | 0 | 56.982 | 54.25 | 47.119 | 22.091 | 0 | 0 | 55.19 | 34.237 | [5 empty] | 21.177 | 18.711 | 9 | 2.6157 | 2.4111 | 1.0493 | 0.88235 | 1.5288 | 58.4468
2005-10-31 | 16:52 | 0 | 21.177 | 0 | 1 | 0 | 48.746 | 48.769 | 31.509 | 30.884 | 24.452 | 24.886 | 13.693 | 1 | 0 | 56.96 | 54.226 | 47.119 | 22.045 | 0 | 0 | 55.144 | 34.237 | [5 empty] | 0 | 17.862 | 10 | 2.609 | 2.4048 | 1.0491 | 0.88235 | 1.5224 | 58.3528
2005-10-31 | 16:53 | 0 | 21.177 | 0 | 2 | 0 | 38.421 | 49.526 | 31.629 | 31.244 | 22.309 | 24.911 | 13.62 | 1 | 0 | 57.005 | 54.226 | 47.21 | 22.067 | 0 | 0 | 55.144 | 34.354 | [5 empty] | 0 | 7.177 | 11 | 2.6303 | 2.425 | 1.0499 | 0.88235 | 1.5426 | 58.6495
2005-10-31 | 16:54 | 0 | 21.177 | 0 | 2 | 0 | 34.636 | 46.34 | 31.629 | 31.438 | 20.887 | 24.886 | 13.67 | 0 | 0 | 56.982 | 54.25 | 47.21 | 22.045 | 0 | 0 | 55.097 | 34.285 | [5 empty] | 0 | 3.198 | 12 | 2.6157 | 2.4111 | 1.0493 | 0.88235 | 1.5288 | 58.4468
2005-10-31 | 16:55 | 0 | 21.152 | 0 | 1 | 0 | 33.531 | 38.796 | 31.75 | 31.558 | 19.794 | 24.958 | 13.595 | 0 | 0 | 57.005 | 54.203 | 47.164 | 22.045 | 0 | 0 | 55.144 | 34.261 | [5 empty] | 0 | 1.973 | 13 | 2.6375 | 2.4319 | 1.0502 | 0.88235 | 1.5496 | 58.7499
2005-10-31 | 16:56 | 0 | 21.177 | 0 | 2 | 0 | 33.156 | 35.411 | 31.607 | 31.558 | 19.078 | 25.007 | 13.62 | 0 | 0 | 57.026 | 54.273 | 47.234 | 22.067 | 0 | 0 | 55.167 | 34.33 | [5 empty] | 0 | 1.598 | 14 | 2.6303 | 2.425 | 1.0499 | 0.88235 | 1.5426 | 58.6495
2005-10-31 | 16:57 | 0 | 21.177 | 0 | 2 | 0 | 32.945 | 34.213 | 31.463 | 31.583 | 18.633 | 24.958 | 13.595 | 0 | 0 | 57.005 | 54.226 | 47.187 | 22.067 | 0 | 0 | 55.167 | 34.33 | [5 empty] | 0 | 1.362 | 15 | 2.6375 | 2.4319 | 1.0502 | 0.88235 | 1.5496 | 58.7499
2005-10-31 | 16:58 | 0 | 21.177 | 1 | 1 | 0 | 32.732 | 33.79 | 31.294 | 31.485 | 18.361 | 24.958 | 13.67 | 0 | 0 | 57.026 | 54.226 | 47.143 | 22.045 | 0 | 0 | 55.144 | 34.306 | [5 empty] | 0 | 1.247 | 16 | 2.6157 | 2.4111 | 1.0493 | 0.88235 | 1.5288 | 58.4468
2005-10-31 | 16:59 | 0 | 21.177 | 0 | 2 | 0 | 32.546 | 33.39 | 31.053 | 31.414 | 18.585 | 24.933 | 13.768 | 0 | 0 | 56.982 | 54.203 | 47.187 | 22.067 | 0 | 0 | 55.097 | 34.306 | [5 empty] | 0 | 1.132 | 17 | 2.5872 | 2.384 | 1.0482 | 0.88235 | 1.5017 | 58.043
2005-10-31 | 17:00 | 0 | 21.152 | 0 | 1 | 0 | 32.304 | 33.228 | 30.786 | 31.244 | 18.263 | 24.958 | 13.57 | 0 | 0 | 56.96 | 54.203 | 47.187 | 22.045 | 0 | 0 | 55.097 | 34.306 | [5 empty] | 0 | 1.06 | 18 | 2.6448 | 2.4388 | 1.0505 | 0.88235 | 1.5565 | 58.8499
2005-10-31 | 17:01 | 0 | 21.147 | 0 | 2 | 0 | 32.13 | 32.893 | 30.541 | 30.999 | 17.813 | 24.977 | 13.688 | 1 | 0 | 56.909 | 54.175 | 47.182 | 22.037 | 0 | 0 | 55.048 | 34.302 | [5 empty] | 0 | 1.131 | 19 | 2.6105 | 2.4062 | 1.0491 | 0.88235 | 1.5238 | 58.3733
2005-10-31 | 17:02 | 0 | 21.128 | 0 | 2 | 0 | 33.579 | 32.663 | 30.112 | 30.81 | 25.512 | 25.053 | 13.645 | 0 | 0 | 56.96 | 54.203 | 47.143 | 22.067 | 0 | 0 | 55.029 | 34.354 | [5 empty] | 0 | 2.769 | 20 | 2.623 | 2.4181 | 1.0496 | 0.88235 | 1.5357 | 58.5484
2005-10-31 | 17:03 | 0 | 21.177 | 0 | 1 | 0 | 49.733 | 32.522 | 29.776 | 30.376 | 23.03 | 24.911 | 13.67 | 0 | 0 | 56.891 | 54.18 | 47.119 | 22.045 | 0 | 0 | 55.029 | 34.33 | [5 empty] | 0 | 19.357 | 21 | 2.6157 | 2.4111 | 1.0493 | 0.88235 | 1.5288 | 58.4468
2005-10-31 | 17:04 | 0 | 21.152 | 0 | 2 | 0 | 38.538 | 36.892 | 29.486 | 30.112 | 20.745 | 24.982 | 13.67 | 0 | 0 | 56.848 | 54.203 | 47.143 | 22.045 | 0 | 0 | 54.983 | 34.33 | [5 empty] | 0 | 8.426 | 22 | 2.6157 | 2.4111 | 1.0493 | 0.88235 | 1.5288 | 58.4468
2005-10-31 | 17:05 | 0 | 21.152 | 0 | 2 | 0 | 33.531 | 45.994 | 29.173 | 29.776 | 19.571 | 24.911 | 13.718 | 1 | 0 | 56.848 | 54.159 | 47.096 | 22.045 | 0 | 0 | 54.959 | 34.306 | [5 empty] | 0 | 3.755 | 23 | 2.6017 | 2.3979 | 1.0488 | 0.88235 | 1.5155 | 58.2501
2005-10-31 | 17:06 | 0 | 21.098 | 0 | 1 | 0 | 31.769 | 38.65 | 28.854 | 29.408 | 18.849 | 24.904 | 13.887 | 0 | 0 | 56.798 | 54.131 | 47.206 | 22.037 | 0 | 0 | 54.887 | 34.302 | [5 empty] | 0 | 2.361 | 24 | 2.5525 | 2.3511 | 1.0468 | 0.88235 | 1.4687 | 57.5405
2005-10-31 | 17:07 | 0 | 21.15 | 0 | 2 | 0 | 31.002 | 34.165 | 28.569 | 29.17 | 18.359 | 24.931 | 13.839 | 0 | 0 | 56.802 | 54.156 | 47.117 | 22.042 | 0 | 0 | 54.915 | 34.328 | [5 empty] | 0 | 1.832 | 25 | 2.5665 | 2.3644 | 1.0474 | 0.88235 | 1.482 | 57.7448
2005-10-31 | 17:08 | 0 | 21.206 | 0 | 1 | 0 | 30.528 | 32.48 | 28.577 | 28.937 | 18.047 | 24.94 | 13.995 | 0 | 0 | 56.832 | 54.142 | 47.124 | 22.074 | 0 | 0 | 54.966 | 34.337 | [5 empty] | 0 | 1.591 | 26 | 2.5211 | 2.3212 | 1.0455 | 0.88235 | 1.4388 | 57.0726
2005-10-31 | 17:09 | 0 | 21.181 | 1 | 2 | 0 | 30.144 | 31.661 | 28.336 | 28.817 | 17.972 | 24.818 | 13.922 | 0 | 0 | 56.809 | 54.142 | 47.103 | 22.074 | 0 | 0 | 54.966 | 34.383 | [5 empty] | 0 | 1.327 | 27 | 2.5423 | 2.3414 | 1.0464 | 0.88235 | 1.459 | 57.3901
2005-10-31 | 17:10 | 0 | 21.15 | 0 | 1 | 0 | 29.798 | 31.002 | 28.111 | 28.52 | 17.718 | 24.715 | 13.839 | 0 | 0 | 56.757 | 54.112 | 47.073 | 22.042 | 0 | 0 | 54.959 | 34.328 | [5 empty] | 0 | 1.278 | 28 | 2.5665 | 2.3644 | 1.0474 | 0.88235 | 1.482 | 57.7448
2005-10-31 | 17:11 | 0 | 21.132 | 0 | 2 | 0 | 29.516 | 30.673 | 28.192 | 28.407 | 17.502 | 24.771 | 13.947 | 0 | 0 | 56.786 | 54.142 | 47.08 | 22.074 | 0 | 0 | 55.013 | 34.359 | [5 empty] | 0 | 1.109 | 29 | 2.535 | 2.3345 | 1.0461 | 0.88235 | 1.4521 | 57.282
2005-10-31 | 17:12 | 0 | 21.132 | 0 | 1 | 0 | 29.276 | 30.31 | 28.118 | 28.312 | 17.479 | 24.771 | 13.824 | 0 | 0 | 56.763 | 54.21 | 47.171 | 22.17 | 0 | 0 | 55.036 | 34.431 | [5 empty] | 0 | 0.964 | 30 | 2.5709 | 2.3685 | 1.0475 | 0.88235 | 1.4862 | 57.8082
2005-10-31 | 17:13 | 0 | 21.181 | 0 | 2 | 0 | 29.251 | 29.901 | 28.096 | 28.192 | 25.132 | 24.842 | 13.897 | 0 | 0 | 56.809 | 54.096 | 47.033 | 22.025 | 0 | 0 | 55.06 | 34.337 | [5 empty] | 0 | 1.059 | 31 | 2.5496 | 2.3483 | 1.0467 | 0.88235 | 1.466 | 57.4977
2005-10-31 | 17:14 | 0 | 21.125 | 0 | 1 | 0 | 49.021 | 29.58 | 27.871 | 28.16 | 22.474 | 24.644 | 13.914 | 1 | 0 | 56.734 | 54.065 | 47.094 | 22.042 | 0 | 0 | 55.006 | 34.306 | [5 empty] | 0 | 20.861 | 32 | 2.5446 | 2.3436 | 1.0465 | 0.88235 | 1.4613 | 57.4246
2005-10-31 | 17:15 | 0 | 21.157 | 0 | 2 | 0 | 37.837 | 32.456 | 27.831 | 28.096 | 20.414 | 24.676 | 13.824 | 0 | 0 | 56.697 | 54.072 | 47.01 | 22.074 | 0 | 0 | 55.036 | 34.359 | [5 empty] | 0 | 9.741 | 33 | 2.5709 | 2.3685 | 1.0475 | 0.88235 | 1.4862 | 57.8082
2005-10-31 | 17:16 | 0 | 21.157 | 0 | 2 | 0 | 31.661 | 44.489 | 27.831 | 27.902 | 19.181 | 24.722 | 13.799 | 0 | 0 | 56.697 | 54.049 | 46.965 | 22.049 | 0 | 0 | 55.013 | 34.337 | [5 empty] | 0 | 3.759 | 34 | 2.5781 | 2.3754 | 1.0478 | 0.88235 | 1.4931 | 57.9134
2005-10-31 | 17:17 | 0 | 21.181 | 0 | 1 | 0 | 29.781 | 37.368 | 27.878 | 27.853 | 18.366 | 24.916 | 13.799 | 1 | 0 | 56.72 | 54.072 | 46.965 | 22.049 | 0 | 0 | 55.036 | 34.314 | [5 empty] | 0 | 1.928 | 35 | 2.5781 | 2.3754 | 1.0478 | 0.88235 | 1.4931 | 57.9134
2005-10-31 | 17:18 | 0 | 21.157 | 0 | 2 | 0 | 29.106 | 32.262 | 27.782 | 27.878 | 17.874 | 24.698 | 13.723 | 0 | 0 | 56.652 | 54.005 | 46.965 | 22.049 | 0 | 0 | 55.013 | 34.337 | [5 empty] | 0 | 1.228 | 36 | 2.6003 | 2.3965 | 1.0487 | 0.88235 | 1.5141 | 58.2295
2005-10-31 | 17:19 | 0 | 21.125 | 0 | 1 | 0 | 28.761 | 30.376 | 27.75 | 27.871 | 17.595 | 24.666 | 13.69 | 0 | 0 | 56.622 | 53.974 | 46.935 | 22.018 | 0 | 0 | 54.891 | 34.306 | [5 empty] | 0 | 0.89 | 37 | 2.6099 | 2.4056 | 1.0491 | 0.88235 | 1.5233 | 58.3651
2005-10-31 | 17:20 | 0 | 21.157 | 0 | 2 | 0 | 28.601 | 29.636 | 27.782 | 27.878 | 17.429 | 24.722 | 13.698 | 0 | 0 | 56.652 | 54.049 | 47.033 | 22.194 | 0 | 0 | 54.945 | 34.314 | [5 empty] | 0 | 0.723 | 38 | 2.6075 | 2.4034 | 1.049 | 0.88235 | 1.521 | 58.3323
2005-10-31 | 17:21 | 0 | 21.132 | 1 | 1 | 0 | 28.528 | 29.276 | 27.807 | 27.853 | 17.255 | 24.676 | 13.675 | 0 | 0 | 56.631 | 54.028 | 47.056 | 22.096 | 0 | 0 | 54.945 | 34.29 | [5 empty] | 0 | 0.675 | 39 | 2.6142 | 2.4098 | 1.0493 | 0.88235 | 1.5274 | 58.4264
2005-10-31 | 17:22 | 0 | 21.157 | 0 | 2 | 0 | 28.383 | 29.035 | 27.758 | 27.782 | 17.132 | 24.722 | 13.748 | 0 | 0 | 56.631 | 54.028 | 46.919 | 22.074 | 0 | 0 | 54.945 | 34.29 | [5 empty] | 0 | 0.601 | 40 | 2.593 | 2.3896 | 1.0484 | 0.88235 | 1.5072 | 58.1261
2005-10-31 | 17:23 | 0 | 21.125 | 0 | 2 | 0 | 28.305 | 28.859 | 27.726 | 27.799 | 17.074 | 24.715 | 13.643 | 0 | 0 | 56.579 | 53.951 | 46.888 | 22.042 | 0 | 0 | 54.915 | 34.235 | [5 empty] | 0 | 0.506 | 41 | 2.6236 | 2.4186 | 1.0497 | 0.88235 | 1.5363 | 58.5565
2005-10-31 | 17:24 | 0 | 21.125 | 0 | 1 | 0 | 28.28 | 28.665 | 27.701 | 27.775 | 23.003 | 24.715 | 13.665 | 0 | 0 | 56.533 | 53.951 | 46.912 | 22.042 | 0 | 0 | 54.868 | 34.258 | [5 empty] | 0 | 0.505 | 42 | 2.6172 | 2.4125 | 1.0494 | 0.88235 | 1.5302 | 58.4672
2005-10-31 | 17:25 | 0 | 21.132 | 0 | 2 | 0 | 47.399 | 28.65 | 27.662 | 27.709 | 22.361 | 24.771 | 13.675 | 0 | 0 | 56.585 | 53.981 | 46.851 | 22.025 | 0 | 0 | 55.013 | 34.314 | [5 empty] | 0 | 19.69 | 43 | 2.6142 | 2.4098 | 1.0493 | 0.88235 | 1.5274 | 58.4264
2005-10-31 | 17:26 | 0 | 21.125 | 0 | 2 | 0 | 37.619 | 31.46 | 27.606 | 27.63 | 19.915 | 24.859 | 13.69 | 1 | 0 | 56.533 | 53.928 | 46.842 | 22.018 | 0 | 0 | 54.983 | 34.258 | [5 empty] | 0 | 9.989 | 44 | 2.6099 | 2.4056 | 1.0491 | 0.88235 | 1.5233 | 58.3651
2005-10-31 | 17:27 | 0 | 21.061 | 0 | 2 | 0 | 31.058 | 43.432 | 27.422 | 27.471 | 18.64 | 24.676 | 13.7 | 0 | 0 | 56.494 | 53.888 | 46.804 | 21.954 | 0 | 0 | 54.922 | 34.196 | [5 empty] | 0 | 3.587 | 45 | 2.607 | 2.4028 | 1.049 | 0.88235 | 1.5205 | 58.3241
2005-10-31 | 17:28 | 0 | 21.061 | 0 | 1 | 0 | 29.155 | 35.959 | 27.471 | 27.422 | 17.949 | 24.7 | 13.653 | 0 | 0 | 56.474 | 53.867 | 46.989 | 22.099 | 0 | 0 | 54.966 | 34.314 | [5 empty] | 0 | 1.733 | 46 | 2.6206 | 2.4158 | 1.0495 | 0.88235 | 1.5335 | 58.516
2005-10-31 | 17:29 | 0 | 21.061 | 0 | 2 | 0 | 28.53 | 31.227 | 27.517 | 27.397 | 17.554 | 24.725 | 13.552 | 1 | 0 | 56.451 | 53.844 | 46.872 | 21.978 | 0 | 0 | 54.922 | 34.22 | [5 empty] | 0 | 1.133 | 47 | 2.6501 | 2.4438 | 1.0507 | 0.88235 | 1.5615 | 58.9215
2005-10-31 | 17:30 | 0 | 21.061 | 0 | 2 | 0 | 28.192 | 29.565 | 27.542 | 27.422 | 17.233 | 24.747 | 13.504 | 0 | 0 | 56.517 | 53.844 | 46.804 | 21.954 | 0 | 0 | 54.922 | 34.196 | [5 empty] | 0 | 0.77 | 48 | 2.664 | 2.4571 | 1.0513 | 0.88235 | 1.5747 | 59.1111
2005-10-31 | 17:31 | 0 | 21.061 | 0 | 1 | 0 | 28.025 | 29.011 | 27.542 | 27.422 | 17.034 | 24.651 | 13.653 | 0 | 0 | 56.474 | 53.844 | 46.781 | 21.954 | 0 | 0 | 54.922 | 34.196 | [5 empty] | 0 | 0.603 | 49 | 2.6206 | 2.4158 | 1.0495 | 0.88235 | 1.5335 | 58.516
2005-10-31 | 17:32 | 0 | 21.086 | 1 | 2 | 0 | 28 | 28.65 | 27.591 | 27.471 | 16.813 | 24.651 | 13.675 | 0 | 0 | 56.451 | 53.844 | 46.757 | 21.978 | 0 | 0 | 54.898 | 34.22 | [5 empty] | 0 | 0.529 | 50 | 2.6142 | 2.4098 | 1.0493 | 0.88235 | 1.5274 | 58.4264
2005-10-31 | 17:33 | 0 | 21.061 | 0 | 2 | 0 | 27.951 | 28.434 | 27.638 | 27.638 | 16.592 | 24.604 | 13.7 | 0 | 0 | 56.451 | 53.797 | 46.781 | 21.978 | 0 | 0 | 54.875 | 34.22 | [5 empty] | 0 | 0.313 | 51 | 2.607 | 2.4028 | 1.049 | 0.88235 | 1.5205 | 58.3241
2005-10-31 | 17:34 | 0 | 21.086 | 0 | 2 | 0 | 27.951 | 28.29 | 27.493 | 27.542 | 16.566 | 24.604 | 13.675 | 0 | 0 | 56.428 | 53.797 | 46.781 | 21.978 | 0 | 0 | 54.875 | 34.196 | [5 empty] | 0 | 0.409 | 52 | 2.6142 | 2.4098 | 1.0493 | 0.88235 | 1.5274 | 58.4264
2005-10-31 | 17:35 | 1 | 21.027 | 0 | 2 | 0 | 27.942 | 28.182 | 27.412 | 27.532 | 20.598 | 24.57 | 13.542 | 0 | 0 | 56.396 | 53.811 | 46.818 | 21.944 | 0 | 0 | 54.842 | 34.187 | [5 empty] | 21.027 | 0.41 | 53 | 2.653 | 2.4466 | 1.0509 | 0.88235 | 1.5642 | 58.9612
2005-10-31 | 17:36 | 0 | 21.086 | 0 | 2 | 0 | 44.946 | 28.167 | 27.422 | 27.422 | 21.858 | 24.604 | 13.429 | 0 | 0 | 56.405 | 53.82 | 46.736 | 21.978 | 0 | 0 | 54.805 | 34.172 | [5 empty] | 0 | 17.524 | 54 | 2.6859 | 2.4779 | 1.0522 | 0.88235 | 1.5955 | 59.4034
2005-10-31 | 17:37 | 0 | 21.051 | 0 | 2 | 0 | 36.536 | 32.132 | 27.412 | 27.363 | 19.815 | 24.57 | 13.517 | 1 | 0 | 56.373 | 53.741 | 46.725 | 21.944 | 0 | 0 | 54.772 | 34.139 | [5 empty] | 0 | 9.173 | 55 | 2.6602 | 2.4535 | 1.0512 | 0.88235 | 1.5711 | 59.0599
2005-10-31 | 17:38 | 0 | 21.076 | 0 | 1 | 0 | 30.47 | 41.777 | 27.363 | 27.338 | 18.359 | 24.57 | 13.492 | 0 | 0 | 56.35 | 53.787 | 46.795 | 21.944 | 0 | 0 | 54.728 | 34.115 | [5 empty] | 0 | 3.132 | 56 | 2.6675 | 2.4604 | 1.0514 | 0.88235 | 1.5781 | 59.1582
2005-10-31 | 17:39 | 0 | 21.076 | 0 | 2 | 0 | 28.687 | 33.694 | 27.459 | 27.292 | 17.519 | 24.57 | 13.492 | 0 | 0 | 56.396 | 53.741 | 46.704 | 21.92 | 0 | 0 | 54.681 | 34.115 | [5 empty] | 0 | 1.395 | 57 | 2.6675 | 2.4604 | 1.0514 | 0.88235 | 1.5781 | 59.1582
2005-10-31 | 17:40 | 0 | 21.076 | 0 | 2 | 0 | 28.157 | 30.038 | 27.581 | 27.338 | 16.976 | 24.521 | 13.492 | 0 | 0 | 56.396 | 53.741 | 46.704 | 21.944 | 0 | 0 | 54.728 | 34.115 | [5 empty] | 0 | 0.819 | 58 | 2.6675 | 2.4604 | 1.0514 | 0.88235 | 1.5781 | 59.1582
2005-10-31 | 17:41 | 0 | 21.076 | 0 | 2 | 0 | 27.966 | 28.952 | 27.508 | 27.437 | 16.727 | 24.497 | 13.469 | 1 | 0 | 56.35 | 53.741 | 46.704 | 21.944 | 0 | 0 | 54.658 | 34.139 | [5 empty] | 0 | 0.529 | 59 | 2.6742 | 2.4668 | 1.0517 | 0.88235 | 1.5844 | 59.2481
2005-10-31 | 17:42 | 0 | 21.051 | 0 | 2 | 0 | 27.846 | 28.496 | 27.532 | 27.387 | 16.383 | 24.521 | 13.567 | 0 | 0 | 56.327 | 53.741 | 46.725 | 21.944 | 0 | 0 | 54.658 | 34.115 | [5 empty] | 0 | 0.459 | 60 | 2.6457 | 2.4397 | 1.0506 | 0.88235 | 1.5573 | 58.8618
2005-10-31 | 17:43 | 0 | 21.051 | 0 | 2 | 0 | 27.846 | 28.302 | 27.459 | 27.387 | 16.333 | 24.472 | 13.444 | 0 | 0 | 56.307 | 53.72 | 46.795 | 21.944 | 0 | 0 | 54.681 | 34.115 | [5 empty] | 0 | 0.459 | 61 | 2.6815 | 2.4737 | 1.052 | 0.88235 | 1.5913 | 59.3453
2005-10-31 | 17:44 | 0 | 21.051 | 1 | 2 | 0 | 27.723 | 28.182 | 27.557 | 27.459 | 16.184 | 24.448 | 13.419 | 0 | 0 | 56.307 | 53.696 | 46.68 | 21.944 | 0 | 0 | 54.658 | 34.163 | [5 empty] | 0 | 0.264 | 62 | 2.6888 | 2.4806 | 1.0523 | 0.88235 | 1.5983 | 59.442
2005-10-31 | 17:45 | 0 | 21.061 | 0 | 2 | 0 | 27.758 | 28.192 | 27.542 | 27.471 | 16.245 | 24.435 | 13.504 | 0 | 0 | 56.339 | 53.729 | 46.666 | 21.978 | 0 | 0 | 54.714 | 34.127 | [5 empty] | 0 | 0.287 | 63 | 2.664 | 2.4571 | 1.0513 | 0.88235 | 1.5747 | 59.1111
2005-10-31 | 17:46 | 0 | 21.027 | 0 | 2 | 0 | 27.677 | 28.013 | 27.459 | 27.483 | 18.779 | 24.376 | 13.321 | 0 | 0 | 56.284 | 53.673 | 46.657 | 21.944 | 0 | 0 | 54.705 | 34.093 | [5 empty] | 0 | 0.194 | 64 | 2.7173 | 2.5077 | 1.0535 | 0.88235 | 1.6254 | 59.816
2005-10-31 | 17:47 | 0 | 21.027 | 0 | 2 | 0 | 42.975 | 28.037 | 27.387 | 27.363 | 22.28 | 24.401 | 13.492 | 0 | 0 | 56.307 | 53.673 | 46.61 | 21.92 | 0 | 0 | 54.705 | 34.093 | [5 empty] | 0 | 15.612 | 65 | 2.6675 | 2.4604 | 1.0514 | 0.88235 | 1.5781 | 59.1582
2005-10-31 | 17:48 | 0 | 21.051 | 0 | 2 | 0 | 47.413 | 32.012 | 27.363 | 27.387 | 24.183 | 24.448 | 13.469 | 1 | 0 | 56.284 | 53.673 | 46.587 | 21.944 | 0 | 0 | 54.751 | 34.07 | [5 empty] | 0 | 20.026 | 66 | 2.6742 | 2.4668 | 1.0517 | 0.88235 | 1.5844 | 59.2481
2005-10-31 | 17:49 | 1 | 21.051 | 0 | 3 | 1 | 47.756 | 44.96 | 27.387 | 27.338 | 24.376 | 24.401 | 13.343 | 2 | 0 | 56.327 | 53.65 | 46.587 | 21.92 | 0 | 0 | 54.751 | 34.046 | [5 empty] | 21.051 | 20.418 | 67 | 2.7109 | 2.5017 | 1.0532 | 0.88235 | 1.6193 | 59.7327
2005-10-31 | 17:50 | 0 | 21.076 | 0 | 2 | 0 | 47.826 | 47.574 | 27.338 | 27.314 | 24.161 | 24.521 | 13.343 | 1 | 0 | 56.327 | 53.65 | 46.587 | 21.944 | 0 | 0 | 54.751 | 34.07 | [5 empty] | 0 | 20.512 | 0 | 2.7109 | 2.5017 | 1.0532 | 0.88235 | 1.6193 | 59.7327
2005-10-31 | 17:51 | 0 | 20.995 | 0 | 2 | 0 | 47.749 | 47.749 | 27.356 | 27.186 | 23.911 | 24.416 | 13.263 | 1 | 0 | 56.232 | 53.619 | 46.58 | 21.912 | 0 | 0 | 54.651 | 34.038 | [5 empty] | 0 | 20.563 | 1 | 2.7342 | 2.5238 | 2.2408 | 2.069 | 0.45484 | 16.635
2005-10-31 | 17:52 | 0 | 21.051 | 0 | 2 | 0 | 47.665 | 47.689 | 27.652 | 27.292 | 23.822 | 24.546 | 13.271 | 2 | 0 | 56.307 | 53.65 | 46.587 | 21.92 | 0 | 0 | 54.658 | 34.07 | [5 empty] | 0 | 20.373 | 2 | 2.7319 | 2.5216 | 2.2407 | 2.069 | 0.45262 | 16.5681
2005-10-31 | 17:53 | 0 | 21.051 | 0 | 1 | 0 | 47.367 | 47.756 | 27.748 | 27.412 | 23.678 | 24.546 | 13.419 | 1 | 0 | 56.307 | 53.626 | 46.61 | 21.944 | 0 | 0 | 54.681 | 34.07 | [5 empty] | 0 | 19.955 | 3 | 2.6888 | 2.4806 | 2.2389 | 2.069 | 0.41166 | 15.3101
2005-10-31 | 17:54 | 0 | 21.044 | 1 | 2 | 0 | 47.406 | 47.705 | 27.861 | 27.476 | 23.695 | 24.538 | 13.361 | 1 | 0 | 56.321 | 53.619 | 46.58 | 21.888 | 0 | 0 | 54.628 | 34.038 | [5 empty] | 0 | 19.93 | 4 | 2.7057 | 2.4967 | 2.2396 | 2.069 | 0.42771 | 15.8079
2005-10-31 | 17:55 | 1 | 21.076 | 0 | 2 | 0 | 47.367 | 47.619 | 28.013 | 27.603 | 23.798 | 24.57 | 13.321 | 1 | 0 | 56.327 | 53.65 | 46.657 | 21.944 | 0 | 0 | 54.635 | 34.07 | [5 empty] | 21.076 | 19.764 | 5 | 2.7173 | 2.5077 | 2.2401 | 2.069 | 0.43878 | 16.1476
2005-10-31 | 17:56 | 0 | 21.101 | 0 | 2 | 0 | 47.39 | 47.689 | 28.037 | 27.652 | 24.136 | 24.521 | 13.394 | 2 | 0 | 56.373 | 53.673 | 46.657 | 21.92 | 0 | 0 | 54.614 | 34.07 | [5 empty] | 0 | 19.738 | 6 | 2.6961 | 2.4875 | 2.2392 | 2.069 | 0.41858 | 15.5254
2005-10-31 | 17:57 | 0 | 21.044 | 0 | 2 | 0 | 47.269 | 47.544 | 28.126 | 27.814 | 24.055 | 24.489 | 13.288 | 1 | 0 | 56.343 | 53.619 | 46.627 | 21.912 | 0 | 0 | 54.56 | 34.015 | [5 empty] | 0 | 19.455 | 7 | 2.7269 | 2.5169 | 2.2405 | 2.069 | 0.44792 | 16.4256
2005-10-31 | 17:58 | 0 | 21.051 | 0 | 2 | 0 | 47.367 | 47.642 | 28.182 | 27.917 | 24.183 | 24.592 | 13.394 | 1 | 0 | 56.396 | 53.673 | 46.748 | 21.92 | 0 | 0 | 54.567 | 34.07 | [5 empty] | 0 | 19.45 | 8 | 2.6961 | 2.4875 | 2.2392 | 2.069 | 0.41858 | 15.5254
2005-10-31 | 17:59 | 0 | 21.02 | 0 | 2 | 0 | 47.567 | 47.544 | 28.319 | 27.981 | 24.32 | 24.56 | 13.336 | 1 | 0 | 56.366 | 53.643 | 46.673 | 21.888 | 0 | 0 | 54.537 | 34.038 | [5 empty] | 0 | 19.586 | 9 | 2.713 | 2.5036 | 2.2399 | 2.069 | 0.43463 | 16.0205
2005-10-31 | 18:00 | 0 | 20.995 | 0 | 2 | 0 | 47.749 | 47.658 | 28.368 | 28.005 | 24.44 | 24.609 | 13.311 | 1 | 0 | 56.432 | 53.666 | 46.627 | 21.863 | 0 | 0 | 54.583 | 34.038 | [5 empty] | 0 | 19.744 | 10 | 2.7202 | 2.5105 | 2.2402 | 2.069 | 0.44155 | 16.232
2005-10-31 | 18:01 | 1 | 21.02 | 0 | 2 | 0 | 47.91 | 47.934 | 28.633 | 28.079 | 24.465 | 24.68 | 13.336 | 2 | 0 | 56.412 | 53.643 | 46.65 | 21.863 | 0 | 0 | 54.583 | 34.062 | [5 empty] | 21.02 | 19.831 | 11 | 2.713 | 2.5036 | 2.2399 | 2.069 | 0.43463 | 16.0205
2005-10-31 | 18:02 | 0 | 21.027 | 0 | 2 | 0 | 47.894 | 48.102 | 28.952 | 28.255 | 24.641 | 24.641 | 13.321 | 1 | 0 | 56.485 | 53.72 | 46.704 | 21.92 | 0 | 0 | 54.614 | 34.093 | [5 empty] | 0 | 19.639 | 12 | 2.7173 | 2.5077 | 2.2401 | 2.069 | 0.43878 | 16.1476
2005-10-31 | 18:03 | 0 | 21.051 | 0 | 1 | 0 | 47.941 | 48.263 | 29.459 | 28.542 | 24.81 | 24.666 | 13.271 | 1 | 0 | 56.553 | 53.696 | 46.704 | 21.92 | 0 | 0 | 54.614 | 34.115 | [5 empty] | 0 | 19.399 | 13 | 2.7319 | 2.5216 | 2.2407 | 2.069 | 0.45262 | 16.5681
2005-10-31 | 18:04 | 0 | 21.051 | 1 | 2 | 0 | 48.445 | 48.193 | 29.965 | 29.121 | 25.026 | 24.641 | 13.444 | 1 | 0 | 56.485 | 53.696 | 46.795 | 21.92 | 0 | 0 | 54.59 | 34.115 | [5 empty] | 0 | 19.324 | 14 | 2.6815 | 2.4737 | 2.2386 | 2.069 | 0.40474 | 15.0936
2005-10-31 | 18:05 | 0 | 21.02 | 0 | 2 | 0 | 48.737 | 48.438 | 30.607 | 29.643 | 25.114 | 24.705 | 13.361 | 2 | 0 | 56.478 | 53.643 | 46.694 | 21.888 | 0 | 0 | 54.583 | 34.108 | [5 empty] | 0 | 19.094 | 15 | 2.7057 | 2.4967 | 2.2396 | 2.069 | 0.42771 | 15.8079
2005-10-31 | 18:06 | 1 | 21.02 | 0 | 2 | 0 | 49.218 | 48.758 | 30.992 | 30.222 | 25.259 | 24.705 | 13.336 | 1 | 0 | 56.478 | 53.619 | 46.694 | 21.888 | 0 | 0 | 54.56 | 34.108 | [5 empty] | 21.02 | 18.996 | 16 | 2.713 | 2.5036 | 2.2399 | 2.069 | 0.43463 | 16.0205
2005-10-31 | 18:07 | 0 | 21.049 | 0 | 2 | 0 | 49.978 | 49.061 | 31.48 | 30.877 | 24.71 | 24.759 | 13.341 | 1 | 0 | 56.505 | 53.647 | 46.699 | 21.942 | 0 | 0 | 54.565 | 34.113 | [5 empty] | 0 | 19.101 | 17 | 2.7115 | 2.5022 | 2.2398 | 2.069 | 0.43325 | 15.9781
2005-10-31 | 18:08 | 0 | 21.049 | 0 | 1 | 0 | 39.894 | 49.635 | 31.72 | 31.117 | 22.351 | 24.808 | 13.416 | 1 | 0 | 56.551 | 53.694 | 46.746 | 21.917 | 0 | 0 | 54.588 | 34.113 | [5 empty] | 0 | 8.777 | 18 | 2.6897 | 2.4815 | 2.239 | 2.069 | 0.41249 | 15.336
2005-10-31 | 18:09 | 0 | 21.025 | 0 | 2 | 0 | 34.983 | 48.121 | 31.865 | 31.6 | 20.282 | 24.808 | 13.416 | 0 | 0 | 56.528 | 53.647 | 46.746 | 21.917 | 0 | 0 | 54.611 | 34.113 | [5 empty] | 0 | 3.383 | 19 | 2.6897 | 2.4815 | 2.239 | 2.069 | 0.41249 | 15.336
2005-10-31 | 18:10 | 0 | 21.049 | 0 | 2 | 0 | 33.644 | 39.942 | 31.889 | 31.649 | 19.787 | 24.832 | 13.366 | 0 | 0 | 56.551 | 53.694 | 46.746 | 21.942 | 0 | 0 | 54.588 | 34.136 | [5 empty] | 0 | 1.995 | 20 | 2.7042 | 2.4953 | 2.2395 | 2.069 | 0.42633 | 15.7652
2005-10-31 | 18:11 | 0 | 21.025 | 0 | 1 | 0 | 33.268 | 35.852 | 31.745 | 31.794 | 19.367 | 24.879 | 13.268 | 0 | 0 | 56.572 | 53.694 | 46.769 | 21.917 | 0 | 0 | 54.541 | 34.136 | [5 empty] | 0 | 1.474 | 21 | 2.7328 | 2.5224 | 2.2407 | 2.069 | 0.45345 | 16.5932
2005-10-31 | 18:12 | 0 | 21.025 | 0 | 2 | 0 | 33.151 | 34.419 | 31.625 | 31.889 | 19.048 | 24.832 | 13.416 | 0 | 0 | 56.528 | 53.671 | 46.792 | 21.917 | 0 | 0 | 54.518 | 34.136 | [5 empty] | 0 | 1.262 | 22 | 2.6897 | 2.4815 | 2.239 | 2.069 | 0.41249 | 15.336
2005-10-31 | 18:13 | 0 | 21.049 | 0 | 2 | 0 | 33.031 | 33.878 | 31.48 | 31.816 | 18.603 | 24.832 | 13.341 | 0 | 0 | 56.528 | 53.694 | 46.816 | 21.917 | 0 | 0 | 54.518 | 34.136 | [5 empty] | 0 | 1.215 | 23 | 2.7115 | 2.5022 | 2.2398 | 2.069 | 0.43325 | 15.9781
2005-10-31 | 18:14 | 0 | 21.025 | 0 | 1 | 0 | 32.845 | 33.644 | 31.335 | 31.696 | 18.035 | 24.879 | 13.416 | 1 | 0 | 56.551 | 53.694 | 46.884 | 21.917 | 0 | 0 | 54.541 | 34.16 | [5 empty] | 0 | 1.149 | 24 | 2.6897 | 2.4815 | 2.239 | 2.069 | 0.41249 | 15.336
2005-10-31 | 18:15 | 0 | 21.049 | 1 | 2 | 0 | 32.68 | 33.385 | 31.141 | 31.696 | 17.937 | 24.879 | 13.391 | 0 | 0 | 56.483 | 53.647 | 46.792 | 21.942 | 0 | 0 | 54.541 | 34.184 | [5 empty] | 0 | 0.984 | 25 | 2.6969 | 2.4884 | 2.2393 | 2.069 | 0.41941 | 15.5512
2005-10-31 | 18:16 | 0 | 21.025 | 0 | 1 | 0 | 32.468 | 33.173 | 30.781 | 31.384 | 17.811 | 24.904 | 13.341 | 0 | 0 | 56.505 | 53.671 | 46.86 | 21.942 | 0 | 0 | 54.495 | 34.16 | [5 empty] | 0 | 1.084 | 26 | 2.7115 | 2.5022 | 2.2398 | 2.069 | 0.43325 | 15.9781
2005-10-31 | 18:17 | 0 | 20.993 | 0 | 2 | 0 | 32.218 | 32.931 | 30.389 | 31.11 | 24.823 | 24.752 | 13.308 | 0 | 0 | 56.43 | 53.64 | 46.715 | 21.91 | 0 | 0 | 54.464 | 34.105 | [5 empty] | 0 | 1.108 | 27 | 2.7211 | 2.5113 | 2.2402 | 2.069 | 0.44238 | 16.2573
2005-10-31 | 18:18 | 0 | 21.025 | 0 | 2 | 1 | 48.832 | 32.752 | 30.107 | 30.781 | 24.349 | 24.688 | 13.442 | 0 | 0 | 56.46 | 53.647 | 46.837 | 21.942 | 0 | 0 | 54.541 | 34.136 | [5 empty] | 0 | 18.051 | 28 | 2.6821 | 2.4743 | 2.2386 | 2.069 | 0.40529 | 15.1109
2005-10-31 | 18:19 | 0 | 21.025 | 0 | 1 | 0 | 41.375 | 34.278 | 29.938 | 30.443 | 21.338 | 24.808 | 13.442 | 1 | 0 | 56.46 | 53.647 | 46.678 | 21.942 | 0 | 0 | 54.541 | 34.136 | [5 empty] | 0 | 10.932 | 0 | 2.6821 | 2.4743 | 2.2386 | 2.069 | 0.40529 | 15.1109
2005-10-31 | 18:20 | 0 | 20.993 | 0 | 2 | 0 | 34.457 | 46.12 | 29.57 | 30.244 | 19.732 | 24.776 | 13.507 | 0 | 0 | 56.387 | 53.617 | 46.785 | 21.885 | 0 | 0 | 54.464 | 34.081 | [5 empty] | 0 | 4.213 | 1 | 2.6632 | 2.4563 | 1.4189 | 1.25 | 1.2063 | 45.2944
2005-10-31 | 18:21 | 0 | 21.017 | 0 | 2 | 0 | 32.218 | 39.887 | 29.401 | 29.857 | 18.791 | 24.823 | 13.482 | 0 | 0 | 56.407 | 53.57 | 46.692 | 21.885 | 0 | 0 | 54.534 | 34.129 | [5 empty] | 0 | 2.361 | 2 | 2.6704 | 2.4632 | 1.4192 | 1.25 | 1.2132 | 45.43
2005-10-31 | 18:22 | 0 | 21.025 | 0 | 2 | 0 | 31.36 | 34.608 | 29.119 | 29.624 | 18.429 | 24.808 | 13.442 | 0 | 0 | 56.371 | 53.601 | 46.769 | 21.917 | 0 | 0 | 54.518 | 34.16 | [5 empty] | 0 | 1.736 | 3 | 2.6821 | 2.4743 | 1.4197 | 1.25 | 1.2243 | 45.6455
2005-10-31 | 18:23 | 0 | 21.025 | 0 | 1 | 0 | 30.781 | 32.704 | 28.949 | 29.263 | 17.688 | 24.904 | 13.391 | 0 | 0 | 56.416 | 53.58 | 46.699 | 21.893 | 0 | 0 | 54.565 | 34.208 | [5 empty] | 0 | 1.518 | 4 | 2.6969 | 2.4884 | 1.4203 | 1.25 | 1.2384 | 45.9176
2005-10-31 | 18:24 | 0 | 21.017 | 0 | 2 | 0 | 30.364 | 31.808 | 28.773 | 29.038 | 17.607 | 24.872 | 13.434 | 0 | 0 | 56.341 | 53.549 | 46.601 | 21.885 | 0 | 0 | 54.558 | 34.105 | [5 empty] | 0 | 1.326 | 5 | 2.6844 | 2.4765 | 1.4198 | 1.25 | 1.2265 | 45.6884
2005-10-31 | 18:25 | 0 | 21.025 | 0 | 1 | 0 | 30.082 | 31.215 | 28.709 | 28.949 | 17.492 | 24.855 | 13.341 | 0 | 0 | 56.305 | 53.533 | 46.655 | 21.917 | 0 | 0 | 54.541 | 34.16 | [5 empty] | 0 | 1.133 | 6 | 2.7115 | 2.5022 | 1.4209 | 1.25 | 1.2522 | 46.1815
2005-10-31 | 18:26 | 0 | 20.993 | 0 | 2 | 0 | 29.736 | 30.774 | 28.773 | 28.773 | 17.26 | 24.896 | 13.384 | 0 | 0 | 56.341 | 53.526 | 46.624 | 21.885 | 0 | 0 | 54.488 | 34.153 | [5 empty] | 0 | 0.963 | 7 | 2.699 | 2.4903 | 1.4204 | 1.25 | 1.2403 | 45.9547
2005-10-31 | 18:27 | 0 | 21.002 | 1 | 2 | 0 | 29.435 | 30.399 | 28.64 | 28.687 | 17.122 | 24.882 | 13.394 | 0 | 0 | 56.307 | 53.512 | 46.566 | 21.87 | 0 | 0 | 54.546 | 34.139 | [5 empty] | 0 | 0.748 | 8 | 2.6961 | 2.4875 | 1.4203 | 1.25 | 1.2375 | 45.9017
2005-10-31 | 18:28 | 0 | 21.002 | 0 | 2 | 0 | 29.29 | 30.036 | 28.616 | 28.616 | 21.436 | 24.857 | 13.442 | 0 | 0 | 56.241 | 53.512 | 46.657 | 21.895 | 0 | 0 | 54.476 | 34.115 | [5 empty] | 0 | 0.674 | 9 | 2.6821 | 2.4743 | 1.4197 | 1.25 | 1.2243 | 45.6455
2005-10-31 | 18:29 | 0 | 21.002 | 0 | 2 | 0 | 45.189 | 29.82 | 28.496 | 28.567 | 23.339 | 24.906 | 13.318 | 0 | 0 | 56.261 | 53.491 | 46.519 | 21.895 | 0 | 0 | 54.499 | 34.115 | [5 empty] | 0 | 16.622 | 10 | 2.7182 | 2.5086 | 1.4211 | 1.25 | 1.2586 | 46.3019
2005-10-31 | 18:30 | 0 | 21.002 | 0 | 2 | 0 | 38.346 | 32.706 | 28.496 | 28.567 | 20.234 | 25.075 | 13.343 | 1 | 0 | 56.195 | 53.491 | 46.68 | 21.92 | 0 | 0 | 54.523 | 34.139 | [5 empty] | 0 | 9.779 | 11 | 2.7109 | 2.5017 | 1.4209 | 1.25 | 1.2517 | 46.171
2005-10-31 | 18:31 | 0 | 20.978 | 0 | 2 | 0 | 31.843 | 43.185 | 28.518 | 28.687 | 18.776 | 25.051 | 13.416 | 0 | 0 | 56.195 | 53.468 | 46.634 | 21.895 | 0 | 0 | 54.453 | 34.091 | [5 empty] | 0 | 3.156 | 12 | 2.6897 | 2.4815 | 1.42 | 1.25 | 1.2315 | 45.7846
2005-10-31 | 18:32 | 0 | 21.002 | 0 | 2 | 0 | 29.989 | 35.196 | 28.567 | 28.542 | 17.864 | 25.195 | 13.343 | 0 | 0 | 56.195 | 53.468 | 46.496 | 21.895 | 0 | 0 | 54.499 | 34.115 | [5 empty] | 0 | 1.447 | 13 | 2.7109 | 2.5017 | 1.4209 | 1.25 | 1.2517 | 46.171
2005-10-31 | 18:33 | 0 | 21.002 | 0 | 1 | 0 | 29.435 | 31.387 | 28.542 | 28.616 | 17.394 | 25.34 | 13.318 | 1 | 0 | 56.195 | 53.468 | 46.519 | 21.87 | 0 | 0 | 54.476 | 34.091 | [5 empty] | 0 | 0.819 | 14 | 2.7182 | 2.5086 | 1.4211 | 1.25 | 1.2586 | 46.3019
2005-10-31 | 18:34 | 0 | 21.002 | 0 | 2 | 0 | 29.241 | 30.205 | 28.351 | 28.567 | 17.024 | 25.485 | 13.416 | 0 | 0 | 56.195 | 53.444 | 46.519 | 21.895 | 0 | 0 | 54.453 | 34.139 | [5 empty] | 0 | 0.674 | 15 | 2.6897 | 2.4815 | 1.42 | 1.25 | 1.2315 | 45.7846
2005-10-31 | 18:35 | 0 | 20.971 | 0 | 2 | 0 | 29.138 | 29.763 | 28.221 | 28.439 | 16.843 | 25.453 | 13.384 | 0 | 0 | 56.119 | 53.414 | 46.559 | 21.863 | 0 | 0 | 54.378 | 34.132 | [5 empty] | 0 | 0.699 | 16 | 2.699 | 2.4903 | 1.4204 | 1.25 | 1.2403 | 45.9547
2005-10-31 | 18:36 | 0 | 20.995 | 0 | 2 | 0 | 28.969 | 29.499 | 28.126 | 28.27 | 16.571 | 25.524 | 13.434 | 0 | 0 | 56.096 | 53.414 | 46.466 | 21.863 | 0 | 0 | 54.378 | 34.108 | [5 empty] | 0 | 0.699 | 17 | 2.6844 | 2.4765 | 1.4198 | 1.25 | 1.2265 | 45.6884
2005-10-31 | 18:37 | 0 | 20.946 | 0 | 2 | 0 | 28.849 | 29.329 | 28.126 | 28.295 | 16.521 | 25.644 | 13.409 | 0 | 0 | 56.075 | 53.391 | 46.442 | 21.888 | 0 | 0 | 54.378 | 34.06 | [5 empty] | 0 | 0.554 | 18 | 2.6917 | 2.4834 | 1.4201 | 1.25 | 1.2334 | 45.8219
2005-10-31 | 18:38 | 0 | 21.002 | 1 | 2 | 0 | 28.736 | 29.29 | 28.182 | 28.182 | 16.702 | 25.772 | 13.394 | 0 | 0 | 56.105 | 53.377 | 46.452 | 21.87 | 0 | 0 | 54.177 | 34.07 | [5 empty] | 0 | 0.554 | 19 | 2.6961 | 2.4875 | 1.4203 | 1.25 | 1.2375 | 45.9017
2005-10-31 | 18:39 | 0 | 20.924 | 0 | 2 | 0 | 28.535 | 29.04 | 28.15 | 28.126 | 18.349 | 25.718 | 13.286 | 0 | 0 | 56.028 | 53.367 | 46.398 | 21.839 | 0 | 0 | 54.194 | 34.015 | [5 empty] | 0 | 0.409 | 20 | 2.7275 | 2.5174 | 1.4215 | 1.25 | 1.2674 | 46.4685
2005-10-31 | 18:40 | 0 | 20.946 | 0 | 2 | 0 | 41.934 | 28.873 | 28.221 | 28.221 | 22.922 | 25.933 | 13.238 | 0 | 0 | 56.096 | 53.367 | 46.398 | 21.863 | 0 | 0 | 54.217 | 34.038 | [5 empty] | 0 | 13.713 | 21 | 2.7415 | 2.5307 | 1.4221 | 1.25 | 1.2807 | 46.7162
2005-10-31 | 18:41 | 0 | 20.946 | 0 | 3 | 0 | 38.385 | 31.281 | 28.175 | 28.199 | 20.681 | 25.764 | 13.213 | 1 | 0 | 56.051 | 53.346 | 46.398 | 21.863 | 0 | 0 | 54.194 | 34.015 | [5 empty] | 0 | 10.186 | 22 | 2.7488 | 2.5376 | 1.4224 | 1.25 | 1.2876 | 46.8442
2005-10-31 | 18:42 | 0 | 20.946 | 0 | 2 | 0 | 31.426 | 42.238 | 28.126 | 28.221 | 18.892 | 25.74 | 13.361 | 0 | 0 | 56.051 | 53.346 | 46.351 | 21.839 | 0 | 0 | 54.147 | 34.015 | [5 empty] | 0 | 3.205 | 23 | 2.7057 | 2.4967 | 1.4206 | 1.25 | 1.2467 | 46.0763
2005-10-31 | 18:43 | 0 | 20.946 | 0 | 2 | 0 | 29.619 | 34.273 | 28.101 | 28.246 | 17.904 | 25.548 | 13.459 | 0 | 0 | 56.005 | 53.346 | 46.466 | 21.888 | 0 | 0 | 54.147 | 34.06 | [5 empty] | 0 | 1.373 | 24 | 2.6771 | 2.4695 | 1.4195 | 1.25 | 1.2195 | 45.5542
2005-10-31 | 18:44 | 0 | 20.978 | 0 | 2 | 0 | 29.05 | 30.614 | 28.133 | 28.302 | 17.444 | 25.676 | 13.369 | 0 | 0 | 56.012 | 53.421 | 46.452 | 21.92 | 0 | 0 | 54.133 | 34.091 | [5 empty] | 0 | 0.748 | 25 | 2.7033 | 2.4945 | 1.4205 | 1.25 | 1.2445 | 46.0341
2005-10-31 | 18:45 | 0 | 20.946 | 0 | 2 | 0 | 28.775 | 29.619 | 28.199 | 28.126 | 17.064 | 25.573 | 13.311 | 1 | 0 | 55.981 | 53.3 | 46.398 | 21.863 | 0 | 0 | 54.009 | 34.06 | [5 empty] | 0 | 0.649 | 26 | 2.7202 | 2.5105 | 1.4212 | 1.25 | 1.2605 | 46.3384
2005-10-31 | 18:46 | 0 | 20.971 | 0 | 2 | 0 | 28.753 | 29.305 | 28.126 | 28.246 | 16.941 | 25.813 | 13.336 | 0 | 0 | 55.981 | 53.323 | 46.466 | 21.888 | 0 | 0 | 53.918 | 34.084 | [5 empty] | 0 | 0.507 | 27 | 2.713 | 2.5036 | 1.4209 | 1.25 | 1.2536 | 46.2077
2005-10-31 | 18:47 | 0 | 20.929 | 0 | 2 | 0 | 28.515 | 29.094 | 28.057 | 28.106 | 16.773 | 25.553 | 13.218 | 0 | 0 | 55.986 | 53.325 | 46.377 | 21.893 | 0 | 0 | 53.9 | 34.089 | [5 empty] | 0 | 0.409 | 28 | 2.7473 | 2.5363 | 1.4223 | 1.25 | 1.2863 | 46.8187
2005-10-31 | 18:48 | 0 | 20.975 | 0 | 2 | 0 | 28.444 | 28.925 | 28.035 | 28.035 | 16.649 | 25.48 | 13.316 | 0 | 0 | 55.986 | 53.302 | 46.309 | 21.868 | 0 | 0 | 53.853 | 34.065 | [5 empty] | 0 | 0.409 | 29 | 2.7188 | 2.5091 | 1.4212 | 1.25 | 1.2591 | 46.3123
2005-10-31 | 18:49 | 0 | 20.975 | 0 | 2 | 0 | 28.395 | 28.756 | 27.915 | 28.01 | 16.501 | 25.384 | 13.341 | 0 | 0 | 55.963 | 53.325 | 46.377 | 21.915 | 0 | 0 | 53.83 | 34.041 | [5 empty] | 0 | 0.385 | 30 | 2.7115 | 2.5022 | 1.4209 | 1.25 | 1.2522 | 46.1815
2005-10-31 | 18:50 | 0 | 20.975 | 1 | 2 | 0 | 28.346 | 28.66 | 27.915 | 27.986 | 16.33 | 25.529 | 13.316 | 0 | 0 | 56.007 | 53.302 | 46.333 | 21.893 | 0 | 0 | 53.806 | 34.019 | [5 empty] | 0 | 0.36 | 31 | 2.7188 | 2.5091 | 1.4212 | 1.25 | 1.2591 | 46.3123
2005-10-31 | 18:51 | 1 | 21 | 0 | 2 | 0 | 37.894 | 28.589 | 27.866 | 27.961 | 22.878 | 25.36 | 13.291 | 0 | 0 | 55.939 | 53.279 | 46.356 | 21.915 | 0 | 0 | 53.783 | 34.019 | [5 empty] | 21 | 9.933 | 32 | 2.7261 | 2.5161 | 1.4215 | 1.25 | 1.2661 | 46.4425
2005-10-31 | 18:52 | 0 | 20.975 | 0 | 2 | 0 | 47.294 | 29.839 | 27.792 | 27.986 | 24.06 | 25.264 | 13.291 | 1 | 0 | 55.939 | 53.234 | 46.356 | 21.868 | 0 | 0 | 53.738 | 34.019 | [5 empty] | 0 | 19.308 | 33 | 2.7261 | 2.5161 | 1.4215 | 1.25 | 1.2661 | 46.4425
2005-10-31 | 18:53 | 0 | 20.941 | 0 | 2 | 0 | 48.088 | 43.69 | 27.736 | 27.807 | 24.651 | 25.279 | 13.255 | 1 | 0 | 55.907 | 53.225 | 46.3 | 21.834 | 0 | 0 | 53.682 | 33.986 | [5 empty] | 0 | 20.281 | 34 | 2.7365 | 2.526 | 1.4219 | 1.25 | 1.276 | 46.6287
2005-10-31 | 18:54 | 0 | 20.941 | 0 | 2 | 0 | 47.882 | 47.446 | 27.782 | 27.951 | 24.411 | 25.301 | 13.379 | 2 | 0 | 55.86 | 53.202 | 46.3 | 21.858 | 0 | 0 | 53.682 | 33.962 | [5 empty] | 0 | 19.931 | 35 | 2.7004 | 2.4917 | 1.4204 | 1.25 | 1.2417 | 45.9812
2005-10-31 | 18:55 | 1 | 20.941 | 0 | 3 | 0 | 47.836 | 47.859 | 27.88 | 27.88 | 23.928 | 25.23 | 13.331 | 1 | 0 | 55.883 | 53.202 | 46.323 | 21.858 | 0 | 0 | 53.706 | 33.962 | [5 empty] | 20.941 | 19.956 | 36 | 2.7144 | 2.505 | 1.421 | 1.25 | 1.255 | 46.2339
2005-10-31 | 18:56 | 0 | 20.975 | 0 | 1 | 0 | 47.936 | 47.845 | 28.01 | 27.89 | 23.746 | 25.313 | 13.291 | 1 | 0 | 55.939 | 53.279 | 46.424 | 21.893 | 0 | 0 | 53.715 | 34.019 | [5 empty] | 0 | 20.046 | 37 | 2.7261 | 2.5161 | 1.4215 | 1.25 | 1.2661 | 46.4425
2005-10-31 | 18:57 | 0 | 20.966 | 0 | 2 | 0 | 47.607 | 47.812 | 28.167 | 27.856 | 23.567 | 25.35 | 13.255 | 1 | 0 | 55.953 | 53.202 | 46.3 | 21.834 | 0 | 0 | 53.636 | 33.962 | [5 empty] | 0 | 19.751 | 38 | 2.7365 | 2.526 | 1.4219 | 1.25 | 1.276 | 46.6287
2005-10-31 | 18:58 | 0 | 20.941 | 0 | 2 | 0 | 47.446 | 47.768 | 28.265 | 27.927 | 23.761 | 25.24 | 13.391 | 2 | 0 | 55.986 | 53.234 | 46.286 | 21.868 | 0 | 0 | 53.668 | 33.971 | [5 empty] | 0 | 19.519 | 39 | 2.6969 | 2.4884 | 1.4203 | 1.25 | 1.2384 | 45.9176
2005-10-31 | 18:59 | 0 | 20.941 | 0 | 2 | 0 | 47.446 | 47.768 | 28.265 | 27.976 | 24.097 | 25.181 | 13.379 | 1 | 0 | 55.953 | 53.246 | 46.3 | 21.834 | 0 | 0 | 53.615 | 33.986 | [5 empty] | 0 | 19.47 | 40 | 2.7004 | 2.4917 | 1.4204 | 1.25 | 1.2417 | 45.9812
2005-10-31 | 19:00 | 0 | 20.917 | 1 | 2 | 0 | 47.768 | 47.675 | 28.312 | 28.167 | 24.217 | 25.156 | 13.404 | 1 | 0 | 55.953 | 53.225 | 46.391 | 21.858 | 0 | 0 | 53.591 | 33.986 | [5 empty] | 0 | 19.601 | 41 | 2.6932 | 2.4848 | 1.4201 | 1.25 | 1.2348 | 45.8486
2005-10-31 | 19:01 | 1 | 20.941 | 0 | 2 | 0 | 48.179 | 47.721 | 28.432 | 28.265 | 24.411 | 25.205 | 13.281 | 2 | 0 | 55.974 | 53.225 | 46.368 | 21.834 | 0 | 0 | 53.591 | 33.962 | [5 empty] | 20.941 | 19.914 | 42 | 2.729 | 2.5188 | 1.4216 | 1.25 | 1.2688 | 46.4944
2005-10-31 | 19:02 | 0 | 20.966 | 0 | 2 | 0 | 48.041 | 48.065 | 28.555 | 28.312 | 24.482 | 25.181 | 13.379 | 1 | 0 | 56.021 | 53.225 | 46.344 | 21.858 | 0 | 0 | 53.545 | 33.938 | [5 empty] | 0 | 19.729 | 43 | 2.7004 | 2.4917 | 1.4204 | 1.25 | 1.2417 | 45.9812
2005-10-31 | 19:03 | 0 | 20.966 | 0 | 2 | 0 | 47.903 | 48.34 | 28.65 | 28.385 | 24.627 | 25.35 | 13.429 | 1 | 0 | 56.068 | 53.225 | 46.344 | 21.834 | 0 | 0 | 53.545 | 33.914 | [5 empty] | 0 | 19.518 | 44 | 2.6859 | 2.4779 | 1.4198 | 1.25 | 1.2279 | 45.7152
2005-10-31 | 19:04 | 0 | 20.966 | 0 | 2 | 0 | 48.478 | 48.249 | 28.601 | 28.41 | 24.891 | 25.35 | 13.331 | 1 | 0 | 56.068 | 53.225 | 46.438 | 21.858 | 0 | 0 | 53.498 | 33.938 | [5 empty] | 0 | 20.068 | 45 | 2.7144 | 2.505 | 1.421 | 1.25 | 1.255 | 46.2339
2005-10-31 | 19:05 | 0 | 20.966 | 0 | 1 | 0 | 49.073 | 48.293 | 28.795 | 28.481 | 24.989 | 25.47 | 13.356 | 2 | 0 | 56.135 | 53.246 | 46.323 | 21.834 | 0 | 0 | 53.521 | 33.962 | [5 empty] | 0 | 20.592 | 46 | 2.7071 | 2.4981 | 1.4207 | 1.25 | 1.2481 | 46.1026
2005-10-31 | 19:06 | 0 | 20.966 | 0 | 2 | 1 | 48.891 | 48.958 | 28.986 | 28.65 | 25.134 | 25.301 | 13.404 | 1 | 0 | 56.089 | 53.225 | 46.368 | 21.858 | 0 | 0 | 53.498 | 33.986 | [5 empty] | 0 | 20.241 | 47 | 2.6932 | 2.4848 | 1.4201 | 1.25 | 1.2348 | 45.8486
2005-10-31 | 19:07 | 1 | 20.978 | 0 | 2 | 0 | 48.72 | 49.292 | 29.386 | 28.878 | 25.146 | 25.362 | 13.416 | 1 | 0 | 56.126 | 53.237 | 46.473 | 21.87 | 0 | 0 | 53.465 | 34.022 | [5 empty] | 20.978 | 19.842 | 0 | 2.6897 | 2.4815 | 1.42 | 1.25 | 1.2315 | 45.7846
2005-10-31 | 19:08 | 0 | 20.978 | 0 | 2 | 0 | 48.513 | 49.087 | 29.962 | 29.097 | 25.217 | 25.482 | 13.293 | 1 | 0 | 56.172 | 53.237 | 46.358 | 21.846 | 0 | 0 | 53.444 | 33.998 | [5 empty] | 0 | 19.416 | 1 | 2.7255 | 2.5155 | 3.1714 | 3 | -0.4845 | -17.7768
2005-10-31 | 19:09 | 0 | 20.978 | 1 | 2 | 0 | 48.926 | 48.835 | 30.541 | 29.553 | 25.362 | 25.436 | 13.318 | 2 | 0 | 56.15 | 53.26 | 46.426 | 21.846 | 0 | 0 | 53.421 | 33.95 | [5 empty] | 0 | 19.373 | 2 | 2.7182 | 2.5086 | 3.1711 | 3 | -0.49142 | -18.079
2005-10-31 | 19:10 | 0 | 20.978 | 0 | 2 | 0 | 49.339 | 48.996 | 30.999 | 30.131 | 25.578 | 25.507 | 13.195 | 1 | 0 | 56.193 | 53.26 | 46.426 | 21.846 | 0 | 0 | 53.444 | 33.998 | [5 empty] | 0 | 19.208 | 3 | 2.754 | 2.5426 | 3.1726 | 3 | -0.45738 | -16.6076
2005-10-31 | 19:11 | 0 | 20.944 | 0 | 2 | 0 | 49.719 | 49.239 | 31.399 | 30.651 | 25.762 | 25.497 | 13.183 | 1 | 0 | 56.14 | 53.227 | 46.44 | 21.836 | 0 | 0 | 53.388 | 33.893 | [5 empty] | 0 | 19.068 | 4 | 2.7575 | 2.5459 | 3.1727 | 3 | -0.45405 | -16.4661
2005-10-31 | 19:12 | 0 | 21.002 | 0 | 2 | 0 | 50.303 | 49.682 | 31.818 | 31.191 | 26.132 | 25.556 | 13.243 | 1 | 0 | 56.172 | 53.26 | 46.426 | 21.87 | 0 | 0 | 53.465 | 33.95 | [5 empty] | 0 | 19.112 | 5 | 2.74 | 2.5293 | 3.172 | 3 | -0.47066 | -17.1772
2005-10-31 | 19:13 | 1 | 20.968 | 0 | 1 | 0 | 50.546 | 50.062 | 32.049 | 31.544 | 24.58 | 25.642 | 13.258 | 1 | 0 | 56.14 | 53.227 | 46.417 | 21.812 | 0 | 0 | 53.388 | 33.916 | [5 empty] | 20.968 | 19.002 | 6 | 2.7357 | 2.5252 | 3.1719 | 3 | -0.47481 | -17.3564
2005-10-31 | 19:14 | 0 | 20.944 | 0 | 2 | 0 | 40.238 | 50.613 | 32.098 | 31.808 | 22.003 | 25.568 | 13.258 | 1 | 0 | 56.161 | 53.274 | 46.417 | 21.858 | 0 | 0 | 53.342 | 33.94 | [5 empty] | 0 | 8.43 | 7 | 2.7357 | 2.5252 | 3.1719 | 3 | -0.47481 | -17.3564
2005-10-31 | 19:15 | 0 | 20.978 | 0 | 2 | 0 | 35.713 | 48.559 | 32.277 | 32.108 | 20.784 | 25.627 | 13.17 | 0 | 0 | 56.172 | 53.237 | 46.449 | 21.87 | 0 | 0 | 53.421 | 33.998 | [5 empty] | 0 | 3.605 | 8 | 2.7613 | 2.5495 | 3.1729 | 3 | -0.45046 | -16.3132
2005-10-31 | 19:16 | 0 | 20.978 | 0 | 1 | 0 | 34.373 | 40.624 | 32.108 | 32.228 | 19.985 | 25.602 | 13.195 | 0 | 0 | 56.216 | 53.213 | 46.496 | 21.821 | 0 | 0 | 53.444 | 33.95 | [5 empty] | 0 | 2.145 | 9 | 2.754 | 2.5426 | 3.1726 | 3 | -0.45738 | -16.6076
2005-10-31 | 19:17 | 0 | 20.978 | 0 | 2 | 0 | 33.902 | 36.536 | 32.034 | 32.154 | 19.294 | 25.651 | 13.195 | 1 | 0 | 56.172 | 53.237 | 46.519 | 21.846 | 0 | 0 | 53.444 | 33.926 | [5 empty] | 0 | 1.748 | 10 | 2.754 | 2.5426 | 3.1726 | 3 | -0.45738 | -16.6076
2005-10-31 | 19:18 | 0 | 20.919 | 0 | 1 | 0 | 33.61 | 35.163 | 31.735 | 32.024 | 18.47 | 25.762 | 13.258 | 0 | 0 | 56.184 | 53.251 | 46.531 | 21.812 | 0 | 0 | 53.433 | 33.916 | [5 empty] | 0 | 1.586 | 11 | 2.7357 | 2.5252 | 3.1719 | 3 | -0.47481 | -17.3564
2005-10-31 | 19:19 | 0 | 20.978 | 0 | 2 | 0 | 33.433 | 34.562 | 31.578 | 32.059 | 18.158 | 25.747 | 13.195 | 0 | 0 | 56.216 | 53.213 | 46.449 | 21.846 | 0 | 0 | 53.465 | 33.926 | [5 empty] | 0 | 1.374 | 12 | 2.754 | 2.5426 | 3.1726 | 3 | -0.45738 | -16.6076
2005-10-31 | 19:20 | 0 | 20.978 | 1 | 2 | 0 | 33.199 | 34.232 | 31.335 | 32.034 | 17.886 | 25.602 | 13.17 | 0 | 0 | 56.172 | 53.099 | 46.473 | 21.846 | 5 | 0 | 57.316 | 23.869 | [5 empty] | 0 | 1.165 | 13 | 2.7613 | 2.5495 | 3.1729 | 3 | -0.45046 | -16.3132
2005-10-31 | 19:21 | 0 | 20.978 | 0 | 11 | 0 | 43.35 | 33.902 | 31.553 | 45.555 | 45.969 | 25.7 | 13.268 | 0 | 0 | 45.051 | 52.894 | 49.866 | 21.87 | 0 | 0 | 57.987 | 21.316 | [5 empty] | 0 | -2.205 | 14 | 2.7328 | 2.5224 | 3.1717 | 3 | -0.47758 | -17.4762
2005-10-31 | 19:22 | 1 | 20.968 | 0 | 14 | 0 | 57.596 | 33.775 | 34.598 | 49.582 | 53.433 | 25.811 | 13.258 | 2 | 0 | 56.499 | 52.242 | 52.562 | 21.836 | 0 | 0 | 57.977 | 20.823 | [5 empty] | 20.968 | 8.014 | 15 | 2.7357 | 2.5252 | 3.1719 | 3 | -0.47481 | -17.3564
2005-10-31 | 19:23 | 1 | 20.978 | 0 | 15 | 0 | 65.588 | 33.739 | 38.32 | 56.238 | 56.216 | 25.772 | 13.243 | 2 | 0 | 64.107 | 52 | 57.293 | 21.87 | 0 | 0 | 57.875 | 23.749 | [5 empty] | 20.978 | 9.35 | 16 | 2.74 | 2.5293 | 3.172 | 3 | -0.47066 | -17.1772
2005-10-31 | 19:24 | 0 | 21.027 | 0 | 15 | 0 | 68.812 | 33.644 | 41.564 | 60.006 | 56.103 | 25.796 | 13.318 | 1 | 0 | 67.582 | 52.114 | 60.118 | 21.846 | 0 | 0 | 57.74 | 28.927 | [5 empty] | 0 | 8.806 | 17 | 2.7182 | 2.5086 | 3.1711 | 3 | -0.49142 | -18.079
2005-10-31 | 19:25 | 1 | 21.002 | 0 | 15 | 0 | 69.932 | 33.598 | 43.726 | 61.866 | 55.942 | 25.723 | 13.318 | 0 | 0 | 68.921 | 52.618 | 61.82 | 21.893 | 0 | 0 | 57.605 | 32.752 | [5 empty] | 21.002 | 8.066 | 18 | 2.7182 | 2.5086 | 3.1711 | 3 | -0.49142 | -18.079
2005-10-31 | 19:26 | 1 | 20.993 | 1 | 15 | 1 | 70.033 | 33.565 | 45.523 | 62.865 | 56.047 | 25.688 | 13.283 | 0 | 1 | 69.263 | 53.274 | 62.731 | 21.836 | 0 | 0 | 57.553 | 35.608 | [5 empty] | 20.993 | 7.168 | 19 | 2.7284 | 2.5183 | 3.1716 | 3 | -0.48173 | -17.6564
2005-10-31 | 19:27 | 0 | 20.958 | 0 | 15 | 0 | 70.066 | 33.555 | 46.842 | 63.527 | 55.876 | 25.703 | 13.175 | 0 | 0 | 69.451 | 53.928 | 63.415 | 21.802 | 0 | 0 | 57.587 | 37.736 | [5 empty] | 0 | 6.539 | 0 | 2.7598 | 2.5482 | 3.1728 | 3 | -0.45184 | -16.372
2005-10-31 | 19:28 | 1 | 20.983 | 0 | 15 | 0 | 70.111 | 33.577 | 47.92 | 64.066 | 55.967 | 25.512 | 13.223 | 0 | 0 | 69.516 | 54.569 | 64.086 | 21.802 | 0 | 0 | 57.742 | 39.475 | [5 empty] | 20.983 | 6.045 | 1 | 2.7459 | 2.5349 | 1.3043 | 1.1321 | 1.4028 | 51.0877
2005-10-31 | 19:29 | 0 | 21.015 | 0 | 15 | 0 | 70.095 | 33.725 | 48.937 | 64.497 | 55.769 | 25.71 | 13.132 | 1 | 0 | 69.59 | 55.127 | 64.477 | 21.834 | 0 | 0 | 58.018 | 40.918 | [5 empty] | 0 | 5.598 | 2 | 2.7724 | 2.5601 | 1.3054 | 1.1321 | 1.428 | 51.508
2005-10-31 | 19:30 | 1 | 20.958 | 0 | 14 | 0 | 69.956 | 33.742 | 49.731 | 64.894 | 55.876 | 25.487 | 13.125 | 0 | 0 | 69.496 | 55.601 | 64.871 | 21.802 | 0 | 0 | 58.169 | 42.061 | [5 empty] | 20.958 | 5.062 | 3 | 2.7744 | 2.562 | 1.3055 | 1.1321 | 1.4299 | 51.54
2005-10-31 | 19:31 | 0 | 20.99 | 0 | 3 | 0 | 67.987 | 60.978 | 37.65 | 64.744 | 39.554 | 25.615 | 13.132 | 0 | 0 | 68.997 | 56.068 | 64.454 | 21.858 | 0 | 0 | 58.379 | 42.444 | [5 empty] | 0 | 3.243 | 4 | 2.7724 | 2.5601 | 1.3054 | 1.1321 | 1.428 | 51.508
2005-10-31 | 19:32 | 0 | 20.958 | 1 | 2 | 0 | 66.284 | 67.649 | 32.732 | 59.828 | 32.685 | 25.512 | 13.223 | 0 | 0 | 67.496 | 56.375 | 61.645 | 21.802 | 0 | 0 | 58.573 | 42.154 | [5 empty] | 0 | 6.456 | 5 | 2.7459 | 2.5349 | 1.3043 | 1.1321 | 1.4028 | 51.0877
2005-10-31 | 19:33 | 0 | 20.958 | 0 | 0 | 0 | 64.805 | 67.293 | 31.244 | 45.42 | 29.751 | 25.703 | 13.248 | 0 | 0 | 66.284 | 56.645 | 58.304 | 21.826 | 0 | 0 | 58.797 | 41.731 | [5 empty] | 0 | 19.385 | 6 | 2.7386 | 2.528 | 1.304 | 1.1321 | 1.3959 | 50.9708
2005-10-31 | 19:34 | 0 | 20.958 | 0 | 0 | 0 | 64.066 | 67 | 30.57 | 42.812 | 28.16 | 25.607 | 13.223 | 0 | 0 | 65.321 | 56.846 | 55.739 | 21.873 | 0 | 0 | 58.842 | 41.308 | [5 empty] | 0 | 21.254 | 7 | 2.7459 | 2.5349 | 1.3043 | 1.1321 | 1.4028 | 51.0877
2005-10-31 | 19:35 | 0 | 20.934 | 0 | 0 | 0 | 63.504 | 66.733 | 30.352 | 42.554 | 27.196 | 25.512 | 13.273 | 0 | 0 | 64.579 | 56.98 | 53.766 | 21.873 | 0 | 0 | 58.931 | 40.839 | [5 empty] | 0 | 20.95 | 8 | 2.7313 | 2.521 | 1.3038 | 1.1321 | 1.389 | 50.8533
2005-10-31 | 19:36 | 0 | 20.934 | 0 | 0 | 0 | 62.943 | 66.441 | 30.305 | 42.343 | 26.186 | 25.583 | 13.198 | 0 | 0 | 64.043 | 57.071 | 52.345 | 21.873 | 0 | 0 | 58.997 | 40.439 | [5 empty] | 0 | 20.6 | 9 | 2.7531 | 2.5418 | 1.3046 | 1.1321 | 1.4097 | 51.204
2005-10-31 | 19:37 | 0 | 20.934 | 0 | 0 | 0 | 62.361 | 66.037 | 30.497 | 42.202 | 25.222 | 25.534 | 13.248 | 1 | 0 | 63.639 | 57.115 | 51.108 | 21.873 | 0 | 0 | 59.02 | 39.992 | [5 empty] | 0 | 20.159 | 10 | 2.7386 | 2.528 | 1.304 | 1.1321 | 1.3959 | 50.9708
2005-10-31 | 19:38 | 0 | 20.966 | 0 | 0 | 0 | 61.852 | 65.686 | 30.602 | 41.997 | 24.869 | 25.495 | 13.331 | 0 | 0 | 63.31 | 57.213 | 50.242 | 21.905 | 0 | 0 | 59.141 | 39.688 | [5 empty] | 0 | 19.855 | 11 | 2.7144 | 2.505 | 1.3031 | 1.1321 | 1.3729 | 50.5783
2005-10-31 | 19:39 | 0 | 20.909 | 0 | 0 | 0 | 61.263 | 65.23 | 30.715 | 41.731 | 24.018 | 25.463 | 13.248 | 0 | 0 | 62.989 | 57.249 | 49.57 | 21.873 | 0 | 0 | 59.132 | 39.334 | [5 empty] | 0 | 19.532 | 12 | 2.7386 | 2.528 | 1.304 | 1.1321 | 1.3959 | 50.9708
2005-10-31 | 19:40 | 0 | 20.909 | 0 | 0 | 0 | 60.679 | 64.805 | 30.81 | 41.521 | 23.511 | 25.463 | 13.273 | 0 | 0 | 62.788 | 57.318 | 48.928 | 21.848 | 0 | 0 | 59.178 | 39.028 | [5 empty] | 0 | 19.158 | 13 | 2.7313 | 2.521 | 1.3038 | 1.1321 | 1.389 | 50.8533
2005-10-31 | 19:41 | 0 | 20.941 | 0 | 0 | 0 | 60.193 | 64.408 | 31.058 | 41.411 | 23.712 | 25.615 | 13.356 | 0 | 0 | 62.592 | 57.348 | 48.454 | 21.88 | 0 | 0 | 59.23 | 38.779 | [5 empty] | 0 | 18.782 | 14 | 2.7071 | 2.4981 | 1.3028 | 1.1321 | 1.366 | 50.4587
2005-10-31 | 19:42 | 0 | 20.909 | 0 | 0 | 0 | 59.604 | 63.931 | 31.1 | 41.191 | 22.981 | 25.632 | 13.248 | 0 | 0 | 62.384 | 57.361 | 48.195 | 21.873 | 0 | 0 | 59.223 | 38.511 | [5 empty] | 0 | 18.413 | 15 | 2.7386 | 2.528 | 1.304 | 1.1321 | 1.3959 | 50.9708
2005-10-31 | 19:43 | 0 | 20.941 | 0 | 0 | 0 | 59.073 | 63.511 | 31.132 | 40.987 | 22.219 | 25.566 | 13.331 | 0 | 0 | 62.233 | 57.437 | 47.927 | 21.88 | 0 | 0 | 59.185 | 38.332 | [5 empty] | 0 | 18.086 | 16 | 2.7144 | 2.505 | 1.3031 | 1.1321 | 1.3729 | 50.5783
2005-10-31 | 19:44 | 0 | 20.885 | 0 | 0 | 0 | 58.527 | 63.055 | 31.146 | 40.767 | 21.704 | 25.534 | 13.298 | 0 | 0 | 62.069 | 57.43 | 47.829 | 21.848 | 0 | 0 | 59.132 | 38.067 | [5 empty] | 0 | 17.76 | 17 | 2.724 | 2.5141 | 1.3035 | 1.1321 | 1.382 | 50.7352
2005-10-31 | 19:45 | 0 | 20.885 | 0 | 0 | 0 | 57.945 | 62.541 | 31.267 | 40.626 | 21.562 | 25.558 | 13.273 | 0 | 0 | 61.934 | 57.384 | 47.621 | 21.826 | 0 | 0 | 59.132 | 37.878 | [5 empty] | 0 | 17.319 | 18 | 2.7313 | 2.521 | 1.3038 | 1.1321 | 1.389 | 50.8533
2005-10-31 | 19:46 | 0 | 20.941 | 0 | 0 | 0 | 57.482 | 62.144 | 31.347 | 40.471 | 21.424 | 25.566 | 13.281 | 0 | 0 | 61.898 | 57.459 | 47.56 | 21.88 | 0 | 0 | 59.185 | 37.698 | [5 empty] | 0 | 17.011 | 19 | 2.729 | 2.5188 | 1.3037 | 1.1321 | 1.3867 | 50.8156
2005-10-31 | 19:47 | 0 | 20.936 | 0 | 0 | 0 | 56.937 | 61.688 | 31.318 | 40.229 | 20.816 | 25.561 | 13.374 | 0 | 0 | 61.779 | 57.475 | 47.439 | 21.851 | 0 | 0 | 59.134 | 37.457 | [5 empty] | 0 | 16.708 | 20 | 2.7019 | 2.4931 | 1.3026 | 1.1321 | 1.361 | 50.3722
2005-10-31 | 19:48 | 0 | 20.858 | 0 | 1 | 0 | 58.21 | 60.428 | 30.639 | 37.686 | 20.309 | 25.485 | 13.296 | 0 | 0 | 61.64 | 57.491 | 47.32 | 21.846 | 0 | 0 | 59.128 | 37.263 | [5 empty] | 0 | 20.524 | 21 | 2.7246 | 2.5147 | 1.3035 | 1.1321 | 1.3826 | 50.7447
2005-10-31 | 19:49 | 0 | 20.907 | 0 | 1 | 0 | 59.981 | 58.858 | 31.07 | 33.103 | 20.5 | 25.531 | 13.296 | 0 | 0 | 61.617 | 57.448 | 47.273 | 21.846 | 0 | 0 | 59.061 | 37.146 | [5 empty] | 0 | 26.878 | 22 | 2.7246 | 2.5147 | 1.3035 | 1.1321 | 1.3826 | 50.7447
2005-10-31 | 19:50 | 0 | 20.882 | 0 | 0 | 0 | 59.531 | 58.21 | 31.264 | 32.372 | 20.234 | 25.531 | 13.296 | 0 | 0 | 61.549 | 57.468 | 47.229 | 21.821 | 0 | 0 | 59.039 | 37.028 | [5 empty] | 0 | 27.159 | 23 | 2.7246 | 2.5147 | 1.3035 | 1.1321 | 1.3826 | 50.7447
2005-10-31 | 19:51 | 0 | 20.882 | 0 | 0 | 0 | 58.972 | 57.872 | 31.215 | 32.203 | 20.524 | 25.507 | 13.296 | 0 | 0 | 61.483 | 57.468 | 47.182 | 21.821 | 0 | 0 | 59.016 | 36.911 | [5 empty] | 0 | 26.769 | 24 | 2.7246 | 2.5147 | 1.3035 | 1.1321 | 1.3826 | 50.7447
2005-10-31 | 19:52 | 0 | 20.912 | 0 | 0 | 0 | 58.416 | 57.564 | 31.198 | 32.162 | 19.352 | 25.49 | 13.25 | 0 | 0 | 61.441 | 57.475 | 47.21 | 21.875 | 0 | 0 | 59.02 | 36.823 | [5 empty] | 0 | 26.254 | 25 | 2.738 | 2.5274 | 1.304 | 1.1321 | 1.3953 | 50.9615
2005-10-31 | 19:53 | 0 | 20.882 | 0 | 0 | 0 | 57.806 | 57.357 | 31.193 | 32.179 | 19.123 | 25.46 | 13.296 | 0 | 0 | 61.414 | 57.468 | 47.136 | 21.799 | 0 | 0 | 58.993 | 36.629 | [5 empty] | 0 | 25.627 | 26 | 2.7246 | 2.5147 | 1.3035 | 1.1321 | 1.3826 | 50.7447
2005-10-31 | 19:54 | 0 | 20.858 | 0 | 0 | 0 | 57.222 | 57.021 | 31.193 | 32.108 | 19.297 | 25.46 | 13.245 | 0 | 0 | 61.348 | 57.448 | 47.115 | 21.821 | 0 | 0 | 58.881 | 36.536 | [5 empty] | 0 | 25.114 | 27 | 2.7395 | 2.5288 | 1.3041 | 1.1321 | 1.3967 | 50.9849
2005-10-31 | 19:55 | 0 | 20.887 | 0 | 0 | 0 | 56.779 | 56.779 | 31.078 | 31.968 | 19.45 | 25.465 | 13.351 | 0 | 0 | 61.33 | 57.519 | 47.234 | 21.851 | 0 | 0 | 58.931 | 36.493 | [5 empty] | 0 | 24.811 | 28 | 2.7086 | 2.4994 | 1.3028 | 1.1321 | 1.3674 | 50.4827
2005-10-31 | 19:56 | 0 | 20.858 | 0 | 0 | 0 | 56.193 | 56.439 | 31.07 | 31.889 | 19.37 | 25.436 | 13.343 | 0 | 0 | 61.302 | 57.491 | 47.021 | 21.846 | 0 | 0 | 58.927 | 36.371 | [5 empty] | 0 | 24.304 | 29 | 2.7109 | 2.5017 | 1.3029 | 1.1321 | 1.3696 | 50.521
2005-10-31 | 19:57 | 0 | 20.858 | 0 | 0 | 0 | 55.666 | 56.17 | 30.975 | 31.938 | 19.148 | 25.316 | 13.419 | 0 | 0 | 61.168 | 57.425 | 47.045 | 21.821 | 0 | 0 | 58.927 | 36.299 | [5 empty] | 0 | 23.728 | 30 | 2.6888 | 2.4806 | 1.302 | 1.1321 | 1.3485 | 50.1544
2005-10-31 | 19:58 | 0 | 20.858 | 0 | 0 | 0 | 55.139 | 55.781 | 31.048 | 31.818 | 19.543 | 25.316 | 13.419 | 0 | 0 | 61.124 | 57.448 | 46.954 | 21.87 | 0 | 0 | 58.972 | 36.206 | [5 empty] | 0 | 23.321 | 31 | 2.6888 | 2.4806 | 1.302 | 1.1321 | 1.3485 | 50.1544
2005-10-31 | 19:59 | 0 | 20.882 | 0 | 0 | 0 | 54.611 | 55.55 | 31.119 | 31.747 | 19.148 | 25.485 | 13.321 | 0 | 0 | 61.079 | 57.448 | 46.93 | 21.846 | 0 | 0 | 58.904 | 36.136 | [5 empty] | 0 | 22.864 | 32 | 2.7173 | 2.5077 | 1.3032 | 1.1321 | 1.3757 | 50.626
2005-10-31 | 20:00 | 0 | 20.836 | 0 | 0 | 0 | 54.107 | 55.207 | 30.95 | 31.769 | 18.925 | 25.266 | 13.22 | 0 | 0 | 60.99 | 57.448 | 47.091 | 21.846 | 0 | 0 | 58.815 | 36.041 | [5 empty] | 0 | 22.338 | 33 | 2.7467 | 2.5357 | 1.3044 | 1.1321 | 1.4036 | 51.1017
2005-10-31 | 20:01 | 0 | 20.858 | 0 | 0 | 0 | 53.58 | 54.863 | 30.975 | 31.649 | 18.728 | 25.387 | 13.343 | 0 | 0 | 60.944 | 57.468 | 46.977 | 21.821 | 0 | 0 | 58.792 | 35.971 | [5 empty] | 0 | 21.931 | 34 | 2.7109 | 2.5017 | 1.3029 | 1.1321 | 1.3696 | 50.521
2005-10-31 | 20:02 | 0 | 20.823 | 0 | 0 | 0 | 53.043 | 54.602 | 31.036 | 31.568 | 18.422 | 25.232 | 13.185 | 0 | 0 | 60.8 | 57.416 | 46.944 | 21.812 | 0 | 0 | 58.737 | 35.866 | [5 empty] | 0 | 21.475 | 35 | 2.7569 | 2.5454 | 1.3048 | 1.1321 | 1.4133 | 51.2642
2005-10-31 | 20:03 | 0 | 20.858 | 0 | 0 | 0 | 52.616 | 54.359 | 30.904 | 31.504 | 18.185 | 25.195 | 13.321 | 0 | 0 | 60.764 | 57.425 | 46.998 | 21.821 | 0 | 0 | 58.726 | 35.806 | [5 empty] | 0 | 21.112 | 36 | 2.7173 | 2.5077 | 1.3032 | 1.1321 | 1.3757 | 50.626
2005-10-31 | 20:04 | 0 | 20.882 | 0 | 1 | 0 | 49.705 | 53.052 | 31.36 | 31.07 | 17.665 | 25.171 | 13.419 | 0 | 0 | 60.675 | 57.402 | 46.998 | 21.821 | 0 | 0 | 58.746 | 35.758 | [5 empty] | 0 | 18.635 | 37 | 2.6888 | 2.4806 | 1.302 | 1.1321 | 1.3485 | 50.1544
2005-10-31 | 20:05 | 0 | 20.907 | 0 | 2 | 0 | 41.987 | 53.006 | 31.938 | 30.445 | 26.855 | 25.291 | 13.343 | 0 | 0 | 60.652 | 57.425 | 46.93 | 21.821 | 0 | 0 | 58.68 | 35.665 | [5 empty] | 0 | 11.542 | 38 | 2.7109 | 2.5017 | 1.3029 | 1.1321 | 1.3696 | 50.521
2005-10-31 | 20:06 | 0 | 20.907 | 0 | 2 | 0 | 47.273 | 48.375 | 30.3 | 31.529 | 23.099 | 25.146 | 13.271 | 0 | 0 | 60.54 | 57.402 | 47.068 | 21.821 | 0 | 0 | 58.726 | 35.737 | [5 empty] | 0 | 15.744 | 39 | 2.7319 | 2.5216 | 1.3038 | 1.1321 | 1.3895 | 50.8627
2005-10-31 | 20:07 | 0 | 20.909 | 0 | 2 | 0 | 36.28 | 46.636 | 28.714 | 31.051 | 20.139 | 25.078 | 13.298 | 0 | 0 | 60.501 | 57.453 | 47.026 | 21.873 | 0 | 0 | 58.55 | 35.622 | [5 empty] | 0 | 5.229 | 40 | 2.724 | 2.5141 | 1.3035 | 1.1321 | 1.382 | 50.7352
2005-10-31 | 20:08 | 0 | 20.934 | 0 | 2 | 0 | 33.436 | 41.944 | 27.655 | 29.317 | 19.176 | 25.078 | 13.371 | 0 | 0 | 60.41 | 57.43 | 47.026 | 21.873 | 0 | 0 | 58.596 | 35.574 | [5 empty] | 0 | 4.119 | 41 | 2.7028 | 2.4939 | 1.3026 | 1.1321 | 1.3618 | 50.3866
2005-10-31 | 20:09 | 0 | 20.904 | 0 | 2 | 0 | 31.455 | 35.593 | 27.142 | 27.77 | 18.379 | 25.119 | 13.243 | 0 | 0 | 60.316 | 57.402 | 46.86 | 21.868 | 0 | 0 | 58.589 | 35.5 | [5 empty] | 0 | 3.685 | 42 | 2.74 | 2.5293 | 1.3041 | 1.1321 | 1.3973 | 50.9943
2005-10-31 | 20:10 | 0 | 20.934 | 0 | 2 | 0 | 29.678 | 33.249 | 26.98 | 27.076 | 17.768 | 25.078 | 13.248 | 0 | 0 | 60.298 | 57.407 | 46.888 | 21.873 | 0 | 0 | 58.573 | 35.457 | [5 empty] | 0 | 2.602 | 43 | 2.7386 | 2.528 | 1.304 | 1.1321 | 1.3959 | 50.9708
2005-10-31 | 20:11 | 0 | 20.904 | 0 | 2 | 0 | 28.371 | 31.286 | 26.877 | 26.757 | 17.492 | 25.073 | 13.145 | 0 | 0 | 60.227 | 57.402 | 46.746 | 21.843 | 0 | 0 | 58.5 | 35.359 | [5 empty] | 0 | 1.614 | 44 | 2.7686 | 2.5565 | 1.3053 | 1.1321 | 1.4244 | 51.4484
2005-10-31 | 20:12 | 0 | 20.904 | 0 | 2 | 0 | 27.696 | 29.553 | 26.757 | 26.733 | 17.195 | 25.048 | 13.168 | 0 | 0 | 60.136 | 57.357 | 46.746 | 21.843 | 0 | 0 | 58.477 | 35.335 | [5 empty] | 0 | 0.963 | 45 | 2.7619 | 2.5501 | 1.305 | 1.1321 | 1.418 | 51.3427
2005-10-31 | 20:13 | 0 | 20.904 | 1 | 3 | 0 | 27.336 | 28.54 | 26.711 | 26.566 | 16.652 | 25.048 | 13.243 | 0 | 0 | 60.093 | 57.334 | 46.792 | 21.819 | 0 | 0 | 58.5 | 35.263 | [5 empty] | 0 | 0.77 | 46 | 2.74 | 2.5293 | 1.3041 | 1.1321 | 1.3973 | 50.9943
2005-10-31 | 20:14 | 0 | 20.929 | 0 | 2 | 0 | 27.191 | 27.986 | 26.662 | 26.517 | 16.529 | 25.119 | 13.193 | 0 | 0 | 60.002 | 57.334 | 46.676 | 21.819 | 0 | 0 | 58.5 | 35.242 | [5 empty] | 0 | 0.674 | 47 | 2.7546 | 2.5432 | 1.3047 | 1.1321 | 1.4111 | 51.2271
2005-10-31 | 20:15 | 0 | 20.934 | 0 | 2 | 0 | 27.076 | 27.726 | 26.762 | 26.451 | 16.509 | 25.078 | 13.198 | 0 | 0 | 59.963 | 57.318 | 46.704 | 21.848 | 0 | 0 | 58.438 | 35.222 | [5 empty] | 0 | 0.625 | 48 | 2.7531 | 2.5418 | 1.3046 | 1.1321 | 1.4097 | 51.204
2005-10-31 | 20:16 | 0 | 20.958 | 0 | 3 | 0 | 34.493 | 27.51 | 27.172 | 26.595 | 23.126 | 25.078 | 13.273 | 0 | 0 | 59.874 | 57.295 | 46.589 | 21.848 | 0 | 0 | 58.416 | 35.153 | [5 empty] | 0 | 7.898 | 49 | 2.7313 | 2.521 | 1.3038 | 1.1321 | 1.389 | 50.8533
2005-10-31 | 20:17 | 0 | 20.929 | 0 | 2 | 0 | 45.644 | 29.962 | 27.481 | 26.855 | 25.095 | 25.048 | 13.341 | 0 | 0 | 59.778 | 57.245 | 46.769 | 21.917 | 0 | 0 | 58.343 | 35.146 | [5 empty] | 0 | 18.789 | 50 | 2.7115 | 2.5022 | 1.303 | 1.1321 | 1.3701 | 50.5305
2005-10-31 | 20:18 | 1 | 20.909 | 0 | 3 | 0 | 47.049 | 43.563 | 27.655 | 27.39 | 25.872 | 25.053 | 13.421 | 0 | 0 | 59.739 | 57.249 | 46.659 | 21.848 | 0 | 0 | 58.327 | 35.129 | [5 empty] | 20.909 | 19.659 | 51 | 2.6882 | 2.4801 | 1.302 | 1.1321 | 1.348 | 50.1447
2005-10-31 | 20:19 | 0 | 20.909 | 0 | 2 | 1 | 47.6 | 46.865 | 27.704 | 27.581 | 25.943 | 25.029 | 13.421 | 0 | 0 | 59.693 | 57.227 | 46.683 | 21.848 | 0 | 0 | 58.327 | 35.081 | [5 empty] | 0 | 20.019 | 52 | 2.6882 | 2.4801 | 1.302 | 1.1321 | 1.348 | 50.1447
2005-10-31 | 20:20 | 0 | 20.904 | 0 | 3 | 0 | 47.892 | 47.549 | 27.625 | 27.721 | 25.602 | 24.975 | 13.366 | 2 | 0 | 59.598 | 57.156 | 46.585 | 21.843 | 0 | 0 | 58.299 | 35.029 | [5 empty] | 0 | 20.171 | 0 | 2.7042 | 2.4953 | 1.3027 | 1.1321 | 1.3632 | 50.4107
2005-10-31 | 20:21 | 0 | 20.929 | 0 | 2 | 0 | 47.777 | 47.892 | 27.65 | 27.53 | 25.119 | 25.048 | 13.341 | 1 | 0 | 59.577 | 57.179 | 46.494 | 21.819 | 0 | 0 | 58.276 | 35.029 | [5 empty] | 0 | 20.247 | 1 | 2.7115 | 2.5022 | 3.1709 | 3 | -0.49779 | -18.3584
2005-10-31 | 20:22 | 0 | 20.904 | 0 | 2 | 0 | 48.006 | 48.121 | 27.674 | 27.481 | 24.759 | 25.073 | 13.464 | 2 | 0 | 59.531 | 57.179 | 46.517 | 21.843 | 0 | 0 | 58.208 | 35.005 | [5 empty] | 0 | 20.525 | 2 | 2.6757 | 2.4682 | 3.1694 | 3 | -0.53184 | -19.8766
2005-10-31 | 20:23 | 1 | 20.88 | 1 | 2 | 0 | 48.076 | 48.167 | 27.674 | 27.481 | 24.83 | 24.999 | 13.416 | 1 | 0 | 59.509 | 57.179 | 46.585 | 21.797 | 0 | 0 | 58.254 | 34.935 | [5 empty] | 20.88 | 20.595 | 3 | 2.6897 | 2.4815 | 3.17 | 3 | -0.51855 | -19.2793
2005-10-31 | 20:24 | 0 | 20.88 | 0 | 3 | 0 | 48.006 | 48.235 | 27.745 | 27.505 | 24.663 | 25.168 | 13.366 | 1 | 0 | 59.531 | 57.179 | 46.585 | 21.797 | 0 | 0 | 58.231 | 34.935 | [5 empty] | 0 | 20.501 | 4 | 2.7042 | 2.4953 | 3.1706 | 3 | -0.50471 | -18.6637
2005-10-31 | 20:25 | 0 | 20.88 | 0 | 2 | 0 | 48.053 | 48.258 | 27.841 | 27.552 | 24.759 | 25.024 | 13.442 | 2 | 0 | 59.531 | 57.222 | 46.655 | 21.942 | 0 | 0 | 58.208 | 34.959 | [5 empty] | 0 | 20.501 | 5 | 2.6821 | 2.4743 | 3.1697 | 3 | -0.52575 | -19.6021
2005-10-31 | 20:26 | 0 | 20.855 | 0 | 2 | 0 | 47.777 | 48.373 | 28.229 | 27.696 | 24.663 | 25.193 | 13.442 | 1 | 0 | 59.486 | 57.179 | 46.631 | 21.819 | 0 | 0 | 58.187 | 34.912 | [5 empty] | 0 | 20.081 | 6 | 2.6821 | 2.4743 | 3.1697 | 3 | -0.52575 | -19.6021
2005-10-31 | 20:27 | 0 | 20.88 | 0 | 2 | 0 | 47.642 | 48.237 | 28.373 | 27.89 | 24.639 | 25.097 | 13.366 | 1 | 0 | 59.534 | 57.202 | 46.748 | 21.843 | 0 | 0 | 58.187 | 34.914 | [5 empty] | 0 | 19.752 | 7 | 2.7042 | 2.4953 | 3.1706 | 3 | -0.50471 | -18.6637
2005-10-31 | 20:28 | 1 | 20.858 | 0 | 2 | 0 | 47.504 | 48.055 | 28.758 | 28.155 | 24.879 | 25.144 | 13.391 | 2 | 0 | 59.511 | 57.202 | 46.655 | 21.868 | 0 | 0 | 58.187 | 34.89 | [5 empty] | 20.858 | 19.349 | 8 | 2.6969 | 2.4884 | 3.1703 | 3 | -0.51163 | -18.9707
2005-10-31 | 20:29 | 0 | 20.848 | 0 | 2 | 0 | 47.518 | 47.908 | 29.04 | 28.486 | 24.801 | 25.186 | 13.283 | 1 | 0 | 59.504 | 57.195 | 46.601 | 21.836 | 0 | 0 | 58.114 | 34.883 | [5 empty] | 0 | 19.032 | 9 | 2.7284 | 2.5183 | 3.1716 | 3 | -0.48173 | -17.6564
2005-10-31 | 20:30 | 0 | 20.88 | 0 | 2 | 0 | 47.572 | 47.985 | 29.359 | 28.878 | 24.928 | 25.193 | 13.391 | 1 | 0 | 59.534 | 57.202 | 46.792 | 21.821 | 0 | 0 | 58.121 | 34.866 | [5 empty] | 0 | 18.694 | 10 | 2.6969 | 2.4884 | 3.1703 | 3 | -0.51163 | -18.9707
2005-10-31 | 20:31 | 0 | 20.88 | 0 | 2 | 0 | 47.801 | 47.962 | 29.602 | 29.312 | 24.879 | 25.193 | 13.439 | 1 | 0 | 59.511 | 57.179 | 46.701 | 21.843 | 0 | 0 | 58.121 | 34.842 | [5 empty] | 0 | 18.489 | 11 | 2.683 | 2.4751 | 3.1697 | 3 | -0.52492 | -19.5648
2005-10-31 | 20:32 | 0 | 20.88 | 0 | 2 | 0 | 48.055 | 48.1 | 29.866 | 29.383 | 24.953 | 25.217 | 13.464 | 2 | 0 | 59.557 | 57.202 | 46.678 | 21.843 | 0 | 0 | 58.121 | 34.818 | [5 empty] | 0 | 18.672 | 12 | 2.6757 | 2.4682 | 3.1694 | 3 | -0.53184 | -19.8766
2005-10-31 | 20:33 | 1 | 20.858 | 1 | 2 | 0 | 48.237 | 48.214 | 30.058 | 29.697 | 25.119 | 25.338 | 13.489 | 1 | 0 | 59.557 | 57.224 | 46.792 | 21.893 | 0 | 0 | 58.076 | 34.842 | [5 empty] | 20.858 | 18.54 | 13 | 2.6684 | 2.4612 | 3.1691 | 3 | -0.53876 | -20.1902
2005-10-31 | 20:34 | 0 | 20.88 | 0 | 2 | 0 | 48.856 | 48.352 | 30.421 | 29.891 | 25.362 | 25.362 | 13.514 | 1 | 0 | 59.557 | 57.224 | 46.701 | 21.868 | 0 | 0 | 58.032 | 34.773 | [5 empty] | 0 | 18.965 | 14 | 2.6611 | 2.4543 | 3.1688 | 3 | -0.54568 | -20.5054
2005-10-31 | 20:35 | 0 | 20.848 | 0 | 2 | 0 | 49.353 | 48.781 | 30.629 | 30.148 | 25.521 | 25.306 | 13.406 | 1 | 0 | 59.504 | 57.172 | 46.718 | 21.812 | 0 | 0 | 58.002 | 34.763 | [5 empty] | 0 | 19.205 | 15 | 2.6926 | 2.4842 | 3.1701 | 3 | -0.51578 | -19.1557
2005-10-31 | 20:36 | 0 | 20.848 | 0 | 2 | 0 | 49.95 | 49.239 | 30.749 | 30.484 | 25.666 | 25.281 | 13.333 | 1 | 0 | 59.458 | 57.149 | 46.785 | 21.836 | 0 | 0 | 58.023 | 34.763 | [5 empty] | 0 | 19.466 | 16 | 2.7138 | 2.5044 | 3.171 | 3 | -0.49557 | -18.2611
2005-10-31 | 20:37 | 0 | 20.904 | 0 | 2 | 0 | 50.599 | 49.82 | 31.191 | 30.661 | 26.036 | 25.362 | 13.439 | 2 | 0 | 59.511 | 57.202 | 46.839 | 21.893 | 0 | 0 | 58.053 | 34.773 | [5 empty] | 0 | 19.938 | 17 | 2.683 | 2.4751 | 3.1697 | 3 | -0.52492 | -19.5648
2005-10-31 | 20:38 | 0 | 20.873 | 0 | 1 | 0 | 51.143 | 50.27 | 31.208 | 30.943 | 24.703 | 25.21 | 13.457 | 1 | 0 | 59.481 | 57.172 | 46.762 | 21.836 | 0 | 0 | 58.023 | 34.742 | [5 empty] | 0 | 20.2 | 18 | 2.6777 | 2.4701 | 3.1695 | 3 | -0.5299 | -19.7891
2005-10-31 | 20:39 | 0 | 20.873 | 0 | 2 | 1 | 42.143 | 50.912 | 31.399 | 31.134 | 21.307 | 25.232 | 13.507 | 0 | 0 | 59.481 | 57.149 | 46.832 | 21.836 | 0 | 0 | 58.023 | 34.763 | [5 empty] | 0 | 11.009 | 19 | 2.6632 | 2.4563 | 3.1689 | 3 | -0.54374 | -20.417
2005-10-31 | 20:40 | 0 | 20.848 | 0 | 2 | 0 | 35.868 | 49.995 | 31.472 | 31.183 | 20.561 | 25.257 | 13.482 | 1 | 0 | 59.458 | 57.195 | 46.785 | 21.836 | 0 | 0 | 58.091 | 34.787 | [5 empty] | 0 | 4.685 | 0 | 2.6704 | 2.4632 | 3.1692 | 3 | -0.53682 | -20.1022
2005-10-31 | 20:41 | 0 | 20.88 | 0 | 2 | 0 | 34.019 | 41.54 | 31.794 | 31.384 | 19.515 | 25.482 | 13.514 | 0 | 0 | 59.511 | 57.179 | 46.839 | 21.843 | 0 | 0 | 58.053 | 34.866 | [5 empty] | 0 | 2.635 | 1 | 2.6611 | 2.4543 | 1.0919 | 0.92308 | 1.5312 | 57.5414
2005-10-31 | 20:42 | 0 | 20.858 | 0 | 1 | 0 | 33.338 | 36.629 | 31.84 | 31.48 | 19.294 | 25.433 | 13.489 | 0 | 0 | 59.534 | 57.179 | 46.907 | 21.843 | 0 | 0 | 58.098 | 34.773 | [5 empty] | 0 | 1.858 | 2 | 2.6684 | 2.4612 | 1.0922 | 0.92308 | 1.5382 | 57.6438
2005-10-31 | 20:43 | 0 | 20.826 | 1 | 2 | 0 | 33.072 | 34.742 | 31.737 | 31.568 | 18.99 | 25.377 | 13.482 | 0 | 0 | 59.458 | 57.149 | 46.97 | 21.836 | 0 | 0 | 58.002 | 34.742 | [5 empty] | 0 | 1.504 | 3 | 2.6704 | 2.4632 | 1.0923 | 0.92308 | 1.5401 | 57.6723
2005-10-31 | 20:44 | 0 | 20.848 | 0 | 2 | 0 | 32.862 | 33.964 | 31.762 | 31.664 | 18.397 | 25.426 | 13.406 | 0 | 0 | 59.481 | 57.128 | 46.853 | 21.836 | 0 | 0 | 58.002 | 34.694 | [5 empty] | 0 | 1.198 | 4 | 2.6926 | 2.4842 | 1.0932 | 0.92308 | 1.5611 | 57.9796
2005-10-31 | 20:45 | 0 | 20.873 | 0 | 1 | 0 | 32.766 | 33.589 | 31.688 | 31.786 | 18.371 | 25.306 | 13.482 | 0 | 0 | 59.436 | 57.128 | 46.877 | 21.836 | 0 | 0 | 57.934 | 34.694 | [5 empty] | 0 | 0.98 | 5 | 2.6704 | 2.4632 | 1.0923 | 0.92308 | 1.5401 | 57.6723
2005-10-31 | 20:46 | 0 | 20.848 | 0 | 2 | 0 | 32.625 | 33.402 | 31.544 | 31.713 | 18.15 | 25.33 | 13.605 | 0 | 0 | 59.436 | 57.106 | 46.877 | 21.836 | 0 | 0 | 57.934 | 34.646 | [5 empty] | 0 | 0.912 | 6 | 2.6346 | 2.4291 | 1.0908 | 0.92308 | 1.5061 | 57.1641
2005-10-31 | 20:47 | 0 | 20.784 | 0 | 2 | 0 | 32.539 | 33.125 | 31.48 | 31.575 | 18.057 | 25.433 | 13.514 | 1 | 0 | 59.397 | 57.044 | 46.816 | 21.77 | 0 | 0 | 57.852 | 34.584 | [5 empty] | 0 | 0.964 | 7 | 2.6611 | 2.4543 | 1.0919 | 0.92308 | 1.5312 | 57.5414
2005-10-31 | 20:48 | 0 | 20.789 | 0 | 2 | 0 | 32.424 | 33.012 | 31.34 | 31.485 | 25.629 | 25.318 | 13.618 | 0 | 0 | 59.358 | 57.071 | 46.958 | 21.799 | 0 | 0 | 57.923 | 34.613 | [5 empty] | 0 | 0.939 | 8 | 2.6308 | 2.4255 | 1.0907 | 0.92308 | 1.5025 | 57.1096
2005-10-31 | 20:49 | 1 | 20.806 | 0 | 1 | 0 | 48.648 | 32.821 | 31.166 | 31.335 | 24.59 | 25.289 | 13.638 | 0 | 0 | 59.285 | 57.021 | 46.907 | 21.794 | 0 | 0 | 57.872 | 34.677 | [5 empty] | 20.806 | 17.313 | 9 | 2.625 | 2.42 | 1.0904 | 0.92308 | 1.4969 | 57.0254
2005-10-31 | 20:50 | 0 | 20.784 | 0 | 2 | 0 | 40.152 | 36.344 | 30.926 | 31.07 | 21.12 | 25.313 | 13.562 | 0 | 0 | 59.285 | 57.021 | 46.837 | 21.819 | 0 | 0 | 57.895 | 34.56 | [5 empty] | 0 | 9.082 | 10 | 2.6471 | 2.441 | 1.0913 | 0.92308 | 1.518 | 57.3433
2005-10-31 | 20:51 | 0 | 20.814 | 0 | 2 | 0 | 34.447 | 45.903 | 30.641 | 31.1 | 19.593 | 25.269 | 13.545 | 1 | 0 | 59.292 | 57.026 | 46.982 | 21.848 | 0 | 0 | 57.856 | 34.565 | [5 empty] | 0 | 3.347 | 11 | 2.6521 | 2.4457 | 1.0915 | 0.92308 | 1.5227 | 57.4137
2005-10-31 | 20:52 | 0 | 20.806 | 0 | 2 | 0 | 32.704 | 38.248 | 30.492 | 30.707 | 18.057 | 25.433 | 13.612 | 0 | 0 | 59.219 | 56.998 | 46.837 | 21.819 | 0 | 0 | 57.895 | 34.536 | [5 empty] | 0 | 1.997 | 12 | 2.6326 | 2.4272 | 1.0908 | 0.92308 | 1.5041 | 57.1348
2005-10-31 | 20:53 | 0 | 20.836 | 0 | 2 | 0 | 31.99 | 34.376 | 30.207 | 30.521 | 17.964 | 25.269 | 13.519 | 0 | 0 | 59.223 | 56.982 | 47.026 | 21.824 | 0 | 0 | 57.879 | 34.565 | [5 empty] | 0 | 1.469 | 13 | 2.6597 | 2.4529 | 1.0919 | 0.92308 | 1.5299 | 57.5209
2005-10-31 | 20:54 | 0 | 20.784 | 0 | 1 | 0 | 31.48 | 33.007 | 30.009 | 30.129 | 17.735 | 25.19 | 13.562 | 0 | 0 | 59.196 | 56.955 | 46.792 | 21.819 | 0 | 0 | 57.806 | 34.512 | [5 empty] | 0 | 1.351 | 14 | 2.6471 | 2.441 | 1.0913 | 0.92308 | 1.518 | 57.3433
2005-10-31 | 20:55 | 0 | 20.784 | 1 | 2 | 0 | 31.141 | 32.345 | 29.962 | 30.009 | 17.59 | 25.215 | 13.612 | 0 | 0 | 59.15 | 56.955 | 46.907 | 21.794 | 0 | 0 | 57.783 | 34.512 | [5 empty] | 0 | 1.132 | 15 | 2.6326 | 2.4272 | 1.0908 | 0.92308 | 1.5041 | 57.1348
2005-10-31 | 20:56 | 0 | 20.784 | 0 | 2 | 0 | 30.803 | 31.84 | 29.817 | 29.842 | 17.464 | 25.215 | 13.537 | 0 | 0 | 59.15 | 56.955 | 46.884 | 21.819 | 0 | 0 | 57.829 | 34.512 | [5 empty] | 0 | 0.961 | 16 | 2.6544 | 2.448 | 1.0916 | 0.92308 | 1.5249 | 57.4468
2005-10-31 | 20:57 | 0 | 20.831 | 0 | 2 | 0 | 30.587 | 31.431 | 29.768 | 29.697 | 17.786 | 25.335 | 13.562 | 0 | 0 | 59.173 | 56.932 | 46.816 | 21.794 | 0 | 0 | 57.872 | 34.512 | [5 empty] | 0 | 0.89 | 17 | 2.6471 | 2.441 | 1.0913 | 0.92308 | 1.518 | 57.3433
2005-10-31 | 20:58 | 0 | 20.784 | 0 | 1 | 0 | 30.394 | 31.117 | 29.528 | 29.624 | 17.514 | 25.19 | 13.587 | 0 | 0 | 59.13 | 56.932 | 46.954 | 21.794 | 0 | 0 | 57.829 | 34.488 | [5 empty] | 0 | 0.77 | 18 | 2.6399 | 2.4341 | 1.0911 | 0.92308 | 1.511 | 57.2393
2005-10-31 | 20:59 | 0 | 20.806 | 0 | 2 | 0 | 30.178 | 30.901 | 29.383 | 29.455 | 21.77 | 25.335 | 13.638 | 0 | 0 | 59.15 | 56.932 | 46.816 | 21.794 | 0 | 0 | 57.806 | 34.464 | [5 empty] | 0 | 0.723 | 19 | 2.625 | 2.42 | 1.0904 | 0.92308 | 1.4969 | 57.0254
2005-10-31 | 21:00 | 0 | 20.806 | 0 | 2 | 0 | 45.829 | 30.707 | 29.31 | 29.334 | 23.987 | 25.264 | 13.638 | 0 | 0 | 59.107 | 56.909 | 46.837 | 21.819 | 0 | 0 | 57.761 | 34.488 | [5 empty] | 0 | 16.495 | 20 | 2.625 | 2.42 | 1.0904 | 0.92308 | 1.4969 | 57.0254
2005-10-31 | 21:01 | 0 | 20.784 | 0 | 2 | 0 | 39.753 | 32.515 | 29.263 | 29.263 | 21.096 | 25.313 | 13.587 | 1 | 0 | 59.061 | 56.864 | 46.86 | 21.819 | 0 | 0 | 57.672 | 34.488 | [5 empty] | 0 | 10.49 | 21 | 2.6399 | 2.4341 | 1.0911 | 0.92308 | 1.511 | 57.2393
2005-10-31 | 21:02 | 0 | 20.806 | 0 | 2 | 0 | 32.866 | 44.405 | 29.045 | 29.263 | 18.575 | 25.215 | 13.685 | 0 | 0 | 59.039 | 56.843 | 46.884 | 21.819 | 0 | 0 | 57.649 | 34.464 | [5 empty] | 0 | 3.603 | 22 | 2.6113 | 2.407 | 1.0899 | 0.92308 | 1.4839 | 56.8261
2005-10-31 | 21:03 | 0 | 20.75 | 0 | 2 | 0 | 30.818 | 37.251 | 28.964 | 29.035 | 17.28 | 25.301 | 13.65 | 0 | 0 | 59.029 | 56.811 | 46.804 | 21.76 | 0 | 0 | 57.64 | 34.431 | [5 empty] | 0 | 1.783 | 23 | 2.6215 | 2.4167 | 1.0903 | 0.92308 | 1.4936 | 56.9747
2005-10-31 | 21:04 | 0 | 20.784 | 0 | 1 | 0 | 30.153 | 32.704 | 28.998 | 28.925 | 17.268 | 25.19 | 13.66 | 1 | 0 | 59.016 | 56.843 | 46.93 | 21.794 | 0 | 0 | 57.672 | 34.512 | [5 empty] | 0 | 1.228 | 24 | 2.6186 | 2.4139 | 1.0902 | 0.92308 | 1.4908 | 56.9324
2005-10-31 | 21:05 | 0 | 20.806 | 0 | 2 | 0 | 29.768 | 31.191 | 28.925 | 28.805 | 16.996 | 25.19 | 13.612 | 0 | 0 | 58.995 | 56.843 | 46.816 | 21.819 | 0 | 0 | 57.672 | 34.464 | [5 empty] | 0 | 0.963 | 25 | 2.6326 | 2.4272 | 1.0908 | 0.92308 | 1.5041 | 57.1348
2005-10-31 | 21:06 | 0 | 20.806 | 0 | 2 | 0 | 29.624 | 30.563 | 28.878 | 28.925 | 17.069 | 25.215 | 13.612 | 0 | 0 | 58.995 | 56.82 | 46.86 | 21.819 | 0 | 0 | 57.649 | 34.443 | [5 empty] | 0 | 0.699 | 26 | 2.6326 | 2.4272 | 1.0908 | 0.92308 | 1.5041 | 57.1348
2005-10-31 | 21:07 | 0 | 20.772 | 1 | 2 | 0 | 29.445 | 30.193 | 28.77 | 28.891 | 16.715 | 25.085 | 13.65 | 0 | 0 | 58.938 | 56.741 | 46.828 | 21.785 | 0 | 0 | 57.66 | 34.407 | [5 empty] | 0 | 0.554 | 27 | 2.6215 | 2.4167 | 1.0903 | 0.92308 | 1.4936 | 56.9747
2005-10-31 | 21:08 | 0 | 20.784 | 0 | 2 | 0 | 29.312 | 30.011 | 28.663 | 28.783 | 16.775 | 25.024 | 13.59 | 0 | 0 | 58.927 | 56.686 | 46.86 | 21.723 | 0 | 0 | 57.649 | 34.349 | [5 empty] | 0 | 0.529 | 28 | 2.639 | 2.4333 | 1.091 | 0.92308 | 1.5102 | 57.2268
2005-10-31 | 21:09 | 0 | 20.784 | 0 | 1 | 0 | 29.239 | 29.746 | 28.758 | 28.685 | 16.974 | 25.144 | 13.688 | 0 | 0 | 58.904 | 56.709 | 46.792 | 21.748 | 0 | 0 | 57.603 | 34.395 | [5 empty] | 0 | 0.554 | 29 | 2.6105 | 2.4062 | 1.0899 | 0.92308 | 1.4831 | 56.8133
2005-10-31 | 21:10 | 0 | 20.76 | 0 | 2 | 0 | 29.119 | 29.626 | 28.709 | 28.613 | 18.95 | 25.073 | 13.713 | 0 | 0 | 58.95 | 56.729 | 46.722 | 21.748 | 0 | 0 | 57.603 | 34.395 | [5 empty] | 0 | 0.506 | 30 | 2.6032 | 2.3992 | 1.0896 | 0.92308 | 1.4762 | 56.7063
2005-10-31 | 21:11 | 0 | 20.738 | 0 | 2 | 0 | 42.291 | 29.481 | 28.638 | 28.663 | 23.484 | 25.122 | 13.688 | 0 | 0 | 58.927 | 56.709 | 46.722 | 21.748 | 0 | 0 | 57.583 | 34.395 | [5 empty] | 0 | 13.628 | 31 | 2.6105 | 2.4062 | 1.0899 | 0.92308 | 1.4831 | 56.8133
2005-10-31 | 21:12 | 0 | 20.738 | 0 | 2 | 0 | 40.504 | 30.59 | 28.589 | 28.589 | 20.544 | 25.193 | 13.638 | 1 | 0 | 58.904 | 56.709 | 46.746 | 21.748 | 0 | 0 | 57.603 | 34.395 | [5 empty] | 0 | 11.915 | 32 | 2.625 | 2.42 | 1.0904 | 0.92308 | 1.4969 | 57.0254
2005-10-31 | 21:13 | 0 | 20.76 | 0 | 2 | 0 | 32.468 | 43.606 | 28.444 | 28.638 | 18.776 | 25.048 | 13.688 | 0 | 0 | 58.881 | 56.686 | 46.792 | 21.772 | 0 | 0 | 57.603 | 34.419 | [5 empty] | 0 | 3.83 | 33 | 2.6105 | 2.4062 | 1.0899 | 0.92308 | 1.4831 | 56.8133
2005-10-31 | 21:14 | 0 | 20.76 | 0 | 2 | 0 | 30.202 | 36.957 | 28.542 | 28.589 | 18.085 | 25.048 | 13.59 | 0 | 0 | 58.861 | 56.686 | 46.816 | 21.797 | 0 | 0 | 57.626 | 34.443 | [5 empty] | 0 | 1.613 | 34 | 2.639 | 2.4333 | 1.091 | 0.92308 | 1.5102 | 57.2268
2005-10-31 | 21:15 | 0 | 20.784 | 0 | 2 | 0 | 29.481 | 31.96 | 28.589 | 28.42 | 17.69 | 25.144 | 13.615 | 0 | 0 | 58.838 | 56.709 | 46.769 | 21.748 | 0 | 0 | 57.603 | 34.419 | [5 empty] | 0 | 1.061 | 35 | 2.6317 | 2.4264 | 1.0907 | 0.92308 | 1.5033 | 57.1222
2005-10-31 | 21:16 | 0 | 20.784 | 0 | 1 | 0 | 29.168 | 30.467 | 28.42 | 28.3 | 17.416 | 24.999 | 13.688 | 0 | 0 | 58.861 | 56.686 | 46.769 | 21.748 | 0 | 0 | 57.491 | 34.371 | [5 empty] | 0 | 0.868 | 36 | 2.6105 | 2.4062 | 1.0899 | 0.92308 | 1.4831 | 56.8133
2005-10-31 | 21:17 | 0 | 20.784 | 0 | 2 | 0 | 28.974 | 29.817 | 28.398 | 28.398 | 17.145 | 24.977 | 13.763 | 0 | 0 | 58.838 | 56.686 | 46.816 | 21.748 | 0 | 0 | 57.537 | 34.371 | [5 empty] | 0 | 0.576 | 37 | 2.5886 | 2.3854 | 1.089 | 0.92308 | 1.4623 | 56.4906
2005-10-31 | 21:18 | 0 | 20.784 | 0 | 2 | 0 | 28.878 | 29.504 | 28.373 | 28.275 | 16.996 | 25.024 | 13.909 | 1 | 0 | 58.881 | 56.686 | 46.792 | 21.772 | 0 | 0 | 57.537 | 34.349 | [5 empty] | 0 | 0.603 | 38 | 2.5461 | 2.345 | 1.0873 | 0.92308 | 1.4219 | 55.8467
2005-10-31 | 21:19 | 0 | 20.784 | 1 | 2 | 0 | 28.734 | 29.337 | 28.253 | 28.229 | 17.072 | 24.904 | 14.01 | 0 | 0 | 58.861 | 56.663 | 46.769 | 21.772 | 0 | 0 | 57.537 | 34.371 | [5 empty] | 0 | 0.505 | 39 | 2.5167 | 2.317 | 1.0861 | 0.92308 | 1.394 | 55.3885
2005-10-31 | 21:20 | 0 | 20.809 | 0 | 2 | 0 | 28.709 | 29.143 | 28.179 | 28.229 | 17.22 | 24.904 | 14.01 | 0 | 0 | 58.792 | 56.663 | 46.816 | 21.797 | 0 | 0 | 57.514 | 34.395 | [5 empty] | 0 | 0.48 | 40 | 2.5167 | 2.317 | 1.0861 | 0.92308 | 1.394 | 55.3885
2005-10-31 | 21:21 | 0 | 20.809 | 0 | 2 | 0 | 28.589 | 29.047 | 28.229 | 28.108 | 17.021 | 24.904 | 14.057 | 0 | 0 | 58.815 | 56.64 | 46.769 | 21.772 | 0 | 0 | 57.514 | 34.395 | [5 empty] | 0 | 0.481 | 41 | 2.503 | 2.304 | 1.0855 | 0.92308 | 1.3809 | 55.1716
2005-10-31 | 21:22 | 0 | 20.76 | 0 | 2 | 0 | 38.107 | 28.927 | 28.035 | 28.059 | 23.53 | 24.783 | 14.035 | 0 | 0 | 58.769 | 56.617 | 46.816 | 21.748 | 0 | 0 | 57.448 | 34.349 | [5 empty] | 0 | 10.048 | 42 | 2.5094 | 2.3101 | 1.0858 | 0.92308 | 1.387 | 55.2734
2005-10-31 | 21:23 | 0 | 20.738 | 0 | 2 | 0 | 40.975 | 29.626 | 28.035 | 28.084 | 19.96 | 24.759 | 14.108 | 0 | 0 | 58.746 | 56.594 | 46.86 | 21.748 | 0 | 0 | 57.471 | 34.325 | [5 empty] | 0 | 12.891 | 43 | 2.4882 | 2.2899 | 1.0849 | 0.92308 | 1.3668 | 54.9335
2005-10-31 | 21:24 | 0 | 20.784 | 0 | 2 | 0 | 32.059 | 42.855 | 28.01 | 27.915 | 18.233 | 24.808 | 14.206 | 1 | 0 | 58.769 | 56.594 | 46.769 | 21.748 | 0 | 0 | 57.471 | 34.325 | [5 empty] | 0 | 4.144 | 44 | 2.4596 | 2.2628 | 1.0837 | 0.92308 | 1.3397 | 54.468
2005-10-31 | 21:25 | 0 | 20.752 | 0 | 2 | 0 | 29.594 | 36.079 | 28.027 | 27.883 | 17.68 | 24.776 | 14.125 | 0 | 0 | 58.717 | 56.565 | 46.785 | 21.716 | 0 | 0 | 57.395 | 34.318 | [5 empty] | 0 | 1.711 | 45 | 2.4832 | 2.2852 | 1.0847 | 0.92308 | 1.3621 | 54.8535
2005-10-31 | 21:26 | 0 | 20.728 | 0 | 2 | 0 | 28.846 | 31.159 | 27.932 | 27.812 | 17.089 | 24.801 | 14.15 | 0 | 0 | 58.717 | 56.565 | 46.877 | 21.741 | 0 | 0 | 57.373 | 34.318 | [5 empty] | 0 | 1.034 | 46 | 2.4759 | 2.2783 | 1.0844 | 0.92308 | 1.3552 | 54.7353
2005-10-31 | 21:27 | 0 | 20.728 | 0 | 2 | 0 | 28.557 | 29.641 | 27.956 | 27.787 | 17.064 | 24.825 | 14.249 | 0 | 0 | 58.742 | 56.567 | 46.741 | 21.741 | 0 | 0 | 57.375 | 34.318 | [5 empty] | 0 | 0.77 | 47 | 2.4471 | 2.2509 | 1.0832 | 0.92308 | 1.3278 | 54.2603
2005-10-31 | 21:28 | 0 | 20.728 | 0 | 2 | 0 | 28.412 | 29.16 | 27.787 | 27.787 | 17.434 | 24.752 | 14.249 | 0 | 0 | 58.719 | 56.521 | 46.9 | 21.716 | 0 | 0 | 57.352 | 34.342 | [5 empty] | 0 | 0.625 | 48 | 2.4471 | 2.2509 | 1.0832 | 0.92308 | 1.3278 | 54.2603
2005-10-31 | 21:29 | 0 | 20.752 | 0 | 2 | 0 | 28.317 | 28.846 | 27.763 | 27.858 | 17.187 | 24.68 | 14.223 | 0 | 0 | 58.696 | 56.501 | 46.785 | 21.716 | 0 | 0 | 57.375 | 34.318 | [5 empty] | 0 | 0.459 | 49 | 2.4547 | 2.2581 | 1.0835 | 0.92308 | 1.335 | 54.3862
2005-10-31 | 21:30 | 0 | 20.735 | 1 | 2 | 0 | 28.202 | 28.707 | 27.792 | 27.743 | 17.019 | 24.71 | 14.279 | 0 | 0 | 58.724 | 56.528 | 46.837 | 21.77 | 0 | 0 | 57.379 | 34.323 | [5 empty] | 0 | 0.459 | 50 | 2.4384 | 2.2426 | 1.0829 | 0.92308 | 1.3195 | 54.1142
2005-10-31 | 21:31 | 0 | 20.728 | 0 | 2 | 0 | 28.123 | 28.535 | 27.618 | 27.738 | 17.137 | 24.656 | 14.274 | 1 | 0 | 58.676 | 56.478 | 46.762 | 21.741 | 0 | 0 | 57.375 | 34.294 | [5 empty] | 0 | 0.385 | 51 | 2.4398 | 2.244 | 1.0829 | 0.92308 | 1.3209 | 54.1386
2005-10-31 | 21:32 | 0 | 20.706 | 0 | 2 | 0 | 27.981 | 28.412 | 27.692 | 27.547 | 16.619 | 24.752 | 14.347 | 0 | 0 | 58.696 | 56.478 | 46.762 | 21.716 | 0 | 0 | 57.418 | 34.247 | [5 empty] | 0 | 0.434 | 52 | 2.4186 | 2.2238 | 1.0821 | 0.92308 | 1.3007 | 53.779
2005-10-31 | 21:33 | 1 | 20.728 | 0 | 2 | 0 | 33.354 | 28.366 | 27.571 | 27.522 | 23.548 | 24.68 | 14.347 | 0 | 0 | 58.653 | 56.478 | 46.9 | 21.716 | 0 | 0 | 57.375 | 34.225 | [5 empty] | 20.728 | 5.832 | 53 | 2.4186 | 2.2238 | 1.0821 | 0.92308 | 1.3007 | 53.779
2005-10-31 | 21:34 | 0 | 20.706 | 0 | 2 | 0 | 45.868 | 28.726 | 27.571 | 27.473 | 24.102 | 24.607 | 14.296 | 0 | 0 | 58.653 | 56.478 | 46.879 | 21.741 | 0 | 0 | 57.329 | 34.247 | [5 empty] | 0 | 18.395 | 54 | 2.4334 | 2.2379 | 1.0827 | 0.92308 | 1.3148 | 54.0309
2005-10-31 | 21:35 | 0 | 20.706 | 0 | 2 | 0 | 47.404 | 42.52 | 27.449 | 27.473 | 25.137 | 24.68 | 14.274 | 2 | 0 | 58.653 | 56.478 | 46.9 | 21.741 | 0 | 0 | 57.329 | 34.247 | [5 empty] | 0 | 19.931 | 55 | 2.4398 | 2.244 | 1.0829 | 0.92308 | 1.3209 | 54.1386
2005-10-31 | 21:36 | 0 | 20.728 | 0 | 3 | 0 | 47.383 | 46.489 | 27.498 | 27.378 | 25.161 | 24.656 | 14.347 | 1 | 0 | 58.653 | 56.455 | 46.762 | 21.716 | 0 | 0 | 57.375 | 34.27 | [5 empty] | 0 | 20.005 | 56 | 2.4186 | 2.2238 | 1.0821 | 0.92308 | 1.3007 | 53.779
2005-10-31 | 21:37 | 0 | 20.728 | 0 | 2 | 0 | 47.451 | 47.313 | 27.571 | 27.427 | 24.68 | 24.801 | 14.296 | 2 | 0 | 58.653 | 56.455 | 46.762 | 21.741 | 0 | 0 | 57.329 | 34.225 | [5 empty] | 0 | 20.024 | 57 | 2.4334 | 2.2379 | 1.0827 | 0.92308 | 1.3148 | 54.0309
2005-10-31 | 21:38 | 1 | 20.752 | 0 | 2 | 0 | 47.612 | 47.451 | 27.618 | 27.473 | 24.367 | 24.68 | 14.397 | 1 | 0 | 58.653 | 56.432 | 46.879 | 21.741 | 0 | 0 | 57.306 | 34.247 | [5 empty] | 20.752 | 20.139 | 58 | 2.404 | 2.2099 | 1.0815 | 0.92308 | 1.2868 | 53.529
2005-10-31 | 21:39 | 0 | 20.728 | 0 | 2 | 0 | 47.679 | 47.649 | 27.586 | 27.466 | 24.261 | 24.649 | 14.314 | 1 | 0 | 58.623 | 56.403 | 46.849 | 21.684 | 0 | 0 | 57.277 | 34.215 | [5 empty] | 0 | 20.213 | 59 | 2.4282 | 2.2329 | 1.0825 | 0.92308 | 1.3098 | 53.9423
2005-10-31 | 21:40 | 0 | 20.696 | 1 | 2 | 0 | 47.535 | 47.628 | 27.755 | 27.441 | 24.094 | 24.671 | 14.364 | 1 | 0 | 58.646 | 56.426 | 46.825 | 21.733 | 0 | 0 | 57.277 | 34.263 | [5 empty] | 0 | 20.094 | 60 | 2.4136 | 2.219 | 1.0819 | 0.92308 | 1.296 | 53.6943
2005-10-31 | 21:41 | 0 | 20.706 | 0 | 2 | 0 | 47.451 | 47.794 | 27.907 | 27.571 | 24.077 | 24.703 | 14.372 | 2 | 0 | 58.676 | 56.478 | 46.879 | 21.741 | 0 | 0 | 57.329 | 34.27 | [5 empty] | 0 | 19.88 | 61 | 2.4113 | 2.2168 | 1.0818 | 0.92308 | 1.2938 | 53.6544
2005-10-31 | 21:42 | 0 | 20.706 | 0 | 2 | 0 | 47.038 | 47.749 | 27.883 | 27.593 | 24.246 | 24.752 | 14.445 | 1 | 0 | 58.676 | 56.478 | 46.879 | 21.716 | 0 | 0 | 57.263 | 34.247 | [5 empty] | 0 | 19.445 | 62 | 2.39 | 2.1966 | 1.0809 | 0.92308 | 1.2735 | 53.2861
2005-10-31 | 21:43 | 1 | 20.696 | 0 | 2 | 0 | 46.594 | 47.649 | 27.611 | 27.706 | 24.455 | 24.815 | 14.56 | 1 | 0 | 58.735 | 56.537 | 46.87 | 21.829 | 0 | 0 | 57.254 | 34.215 | [5 empty] | 20.696 | 18.888 | 63 | 2.3565 | 2.1648 | 1.0796 | 0.92308 | 1.2417 | 52.6926
2005-10-31 | 21:44 | 0 | 20.706 | 0 | 2 | 1 | 46.396 | 47.175 | 27.402 | 27.427 | 25.016 | 24.752 | 14.47 | 2 | 0 | 58.765 | 56.521 | 46.947 | 21.716 | 0 | 0 | 57.306 | 34.247 | [5 empty] | 0 | 18.969 | 64 | 2.3827 | 2.1897 | 1.0806 | 0.92308 | 1.2666 | 53.1585
2005-10-31 | 21:45 | 0 | 20.728 | 0 | 2 | 0 | 46.809 | 46.718 | 27.353 | 27.184 | 25.546 | 24.776 | 14.495 | 1 | 0 | 58.787 | 56.478 | 46.856 | 21.716 | 0 | 0 | 57.352 | 34.247 | [5 empty] | 0 | 19.625 | 0 | 2.3755 | 2.1828 | 1.0803 | 0.92308 | 1.2597 | 53.0301
2005-10-31 | 21:46 | 0 | 20.728 | 0 | 3 | 0 | 46.832 | 47.061 | 27.353 | 27.088 | 25.691 | 24.921 | 14.445 | 2 | 0 | 58.81 | 56.478 | 46.9 | 21.741 | 0 | 0 | 57.306 | 34.247 | [5 empty] | 0 | 19.744 | 1 | 2.39 | 2.1966 | 3.3157 | 3.1579 | -0.96127 | -40.2203
2005-10-31 | 21:47 | 0 | 20.696 | 0 | 2 | 0 | 46.963 | 47.238 | 27.446 | 27.012 | 25.737 | 24.749 | 14.492 | 1 | 0 | 58.826 | 56.496 | 46.851 | 21.738 | 0 | 0 | 57.281 | 34.196 | [5 empty] | 0 | 19.951 | 2 | 2.3763 | 2.1836 | 3.3152 | 3.1579 | -0.97428 | -40.9994
2005-10-31 | 21:48 | 1 | 20.74 | 0 | 3 | 0 | 47.094 | 47.392 | 27.701 | 27.098 | 25.968 | 24.81 | 14.482 | 1 | 0 | 58.774 | 56.464 | 46.888 | 21.704 | 0 | 0 | 57.227 | 34.211 | [5 empty] | 20.74 | 19.996 | 3 | 2.3792 | 2.1864 | 3.3153 | 3.1579 | -0.97151 | -40.8329
2005-10-31 | 21:49 | 0 | 20.716 | 1 | 2 | 0 | 47.117 | 47.369 | 28.111 | 27.461 | 25.823 | 24.786 | 14.482 | 2 | 0 | 58.817 | 56.464 | 46.979 | 21.704 | 0 | 0 | 57.204 | 34.235 | [5 empty] | 0 | 19.656 | 4 | 2.3792 | 2.1864 | 3.3153 | 3.1579 | -0.97151 | -40.8329
2005-10-31 | 21:50 | 0 | 20.716 | 0 | 2 | 0 | 47.024 | 47.53 | 28.859 | 27.775 | 25.87 | 24.884 | 14.507 | 1 | 0 | 58.84 | 56.464 | 46.888 | 21.704 | 0 | 0 | 57.27 | 34.235 | [5 empty] | 0 | 19.249 | 5 | 2.372 | 2.1795 | 3.315 | 3.1579 | -0.97843 | -41.2499
2005-10-31 | 21:51 | 0 | 20.716 | 0 | 3 | 0 | 46.842 | 47.574 | 29.678 | 28.616 | 25.605 | 25.029 | 14.482 | 2 | 0 | 58.863 | 56.464 | 46.842 | 21.728 | 0 | 0 | 57.293 | 34.211 | [5 empty] | 0 | 18.226 | 6 | 2.3792 | 2.1864 | 3.3153 | 3.1579 | -0.97151 | -40.8329
2005-10-31 | 21:52 | 0 | 20.74 | 0 | 2 | 0 | 46.428 | 47.369 | 30.399 | 29.508 | 25.583 | 24.884 | 14.555 | 1 | 0 | 58.817 | 56.487 | 46.979 | 21.728 | 0 | 0 | 57.227 | 34.187 | [5 empty] | 0 | 16.92 | 7 | 2.358 | 2.1662 | 3.3144 | 3.1579 | -0.99172 | -42.0579
2005-10-31 | 21:53 | 1 | 20.74 | 0 | 3 | 0 | 46.657 | 46.909 | 31.002 | 30.423 | 25.678 | 24.931 | 14.555 | 2 | 0 | 58.84 | 56.464 | 46.956 | 21.753 | 0 | 0 | 57.249 | 34.211 | [5 empty] | 20.74 | 16.234 | 8 | 2.358 | 2.1662 | 3.3144 | 3.1579 | -0.99172 | -42.0579
2005-10-31 | 21:54 | 0 | 20.74 | 0 | 2 | 0 | 46.771 | 47.117 | 31.605 | 31.073 | 25.87 | 25.029 | 14.555 | 1 | 0 | 58.886 | 56.487 | 46.842 | 21.753 | 0 | 0 | 57.227 | 34.163 | [5 empty] | 0 | 15.698 | 9 | 2.358 | 2.1662 | 3.3144 | 3.1579 | -0.99172 | -42.0579
2005-10-31 | 21:55 | 0 | 20.765 | 0 | 2 | 0 | 47.299 | 47.185 | 31.87 | 31.725 | 26.098 | 25.038 | 14.616 | 1 | 0 | 58.872 | 56.474 | 46.989 | 21.763 | 0 | 0 | 57.19 | 34.22 | [5 empty] | 0 | 15.574 | 10 | 2.3402 | 2.1493 | 3.3137 | 3.1579 | -1.0086 | -43.0986
2005-10-31 | 21:56 | 0 | 20.765 | 0 | 3 | 0 | 47.53 | 47.507 | 32.085 | 32.061 | 26.233 | 24.98 | 14.606 | 1 | 0 | 58.84 | 56.442 | 46.956 | 21.728 | 0 | 0 | 57.158 | 34.187 | [5 empty] | 0 | 15.469 | 11 | 2.3431 | 2.1521 | 3.3138 | 3.1579 | -1.0058 | -42.927
2005-10-31 | 21:57 | 0 | 20.799 | 0 | 2 | 0 | 47.791 | 47.815 | 32.24 | 32.336 | 26.603 | 24.965 | 14.616 | 1 | 0 | 58.895 | 56.496 | 47.126 | 21.738 | 0 | 0 | 57.147 | 34.268 | [5 empty] | 0 | 15.455 | 12 | 2.3402 | 2.1493 | 3.3137 | 3.1579 | -1.0086 | -43.0986
2005-10-31 | 21:58 | 0 | 20.765 | 0 | 3 | 0 | 47.896 | 48.011 | 32.424 | 32.399 | 26.811 | 25.029 | 14.555 | 1 | 0 | 58.863 | 56.464 | 47.047 | 21.728 | 0 | 0 | 57.115 | 34.258 | [5 empty] | 0 | 15.497 | 13 | 2.358 | 2.1662 | 3.3144 | 3.1579 | -0.99172 | -42.0579
2005-10-31 | 21:59 | 1 | 20.814 | 1 | 2 | 0 | 48.468 | 48.31 | 32.685 | 32.613 | 27.196 | 25.051 | 14.58 | 2 | 0 | 58.886 | 56.442 | 47.117 | 21.728 | 0 | 0 | 57.138 | 34.235 | [5 empty] | 20.814 | 15.855 | 14 | 2.3507 | 2.1593 | 3.3142 | 3.1579 | -0.99864 | -42.4825
2005-10-31 | 22:00 | 0 | 20.789 | 0 | 2 | 0 | 48.905 | 48.492 | 32.685 | 32.802 | 27.221 | 25.004 | 14.555 | 1 | 0 | 58.84 | 56.464 | 47.161 | 21.728 | 0 | 0 | 57.115 | 34.235 | [5 empty] | 0 | 16.103 | 15 | 2.358 | 2.1662 | 3.3144 | 3.1579 | -0.99172 | -42.0579
2005-10-31 | 22:01 | 0 | 20.789 | 0 | 3 | 0 | 48.858 | 49.18 | 32.637 | 32.754 | 27.341 | 25.1 | 14.53 | 1 | 0 | 58.84 | 56.442 | 47.094 | 21.704 | 0 | 0 | 57.204 | 34.235 | [5 empty] | 0 | 16.104 | 16 | 2.3653 | 2.1731 | 3.3147 | 3.1579 | -0.9848 | -41.6359
2005-10-31 | 22:02 | 0 | 20.823 | 0 | 2 | 0 | 49.028 | 49.213 | 32.67 | 32.787 | 27.422 | 25.183 | 14.442 | 1 | 0 | 58.872 | 56.474 | 47.15 | 21.763 | 0 | 0 | 57.19 | 34.316 | [5 empty] | 0 | 16.241 | 17 | 2.3909 | 2.1975 | 3.3158 | 3.1579 | -0.96044 | -40.1708
2005-10-31 | 22:03 | 0 | 20.765 | 0 | 2 | 1 | 49.227 | 49.248 | 32.802 | 32.847 | 27.557 | 25.124 | 14.384 | 2 | 0 | 58.84 | 56.419 | 47.07 | 21.704 | 0 | 0 | 57.158 | 34.258 | [5 empty] | 0 | 16.38 | 18 | 2.4078 | 2.2135 | 3.3165 | 3.1579 | -0.94439 | -39.2223
2005-10-31 | 22:04 | 1 | 20.765 | 0 | 2 | 0 | 49.456 | 49.456 | 32.871 | 32.919 | 27.581 | 25.34 | 14.359 | 1 | 0 | 58.886 | 56.419 | 47.117 | 21.704 | 0 | 0 | 57.181 | 34.282 | [5 empty] | 20.765 | 16.537 | 0 | 2.4151 | 2.2204 | 3.3168 | 3.1579 | -0.93747 | -38.8175
2005-10-31 | 22:05 | 0 | 20.765 | 0 | 3 | 0 | 49.684 | 49.731 | 32.943 | 32.964 | 27.726 | 25.195 | 14.482 | 1 | 0 | 58.863 | 56.442 | 47.231 | 21.728 | 0 | 0 | 57.204 | 34.304 | [5 empty] | 0 | 16.72 | 1 | 2.3792 | 2.1864 | 1.6959 | 1.5385 | 0.64792 | 27.2322
2005-10-31 | 22:06 | 0 | 20.789 | 0 | 2 | 0 | 50.006 | 49.96 | 33.06 | 33.084 | 27.846 | 25.244 | 14.482 | 1 | 0 | 58.908 | 56.419 | 47.14 | 21.728 | 0 | 0 | 57.204 | 34.304 | [5 empty] | 0 | 16.922 | 2 | 2.3792 | 2.1864 | 1.6959 | 1.5385 | 0.64792 | 27.2322
2005-10-31 | 22:07 | 0 | 20.789 | 0 | 2 | 0 | 50.258 | 50.312 | 33.235 | 33.187 | 28.074 | 25.303 | 14.52 | 1 | 0 | 58.892 | 56.428 | 47.171 | 21.741 | 0 | 0 | 57.167 | 34.268 | [5 empty] | 0 | 17.071 | 3 | 2.3682 | 2.1759 | 1.6954 | 1.5385 | 0.6374 | 26.9153
2005-10-31 | 22:08 | 0 | 20.777 | 1 | 2 | 0 | 50.473 | 50.473 | 33.163 | 33.28 | 28.121 | 25.232 | 14.495 | 2 | 0 | 58.87 | 56.382 | 47.147 | 21.691 | 0 | 0 | 57.188 | 34.268 | [5 empty] | 0 | 17.193 | 4 | 2.3755 | 2.1828 | 1.6957 | 1.5385 | 0.64432 | 27.1242
2005-10-31 | 22:09 | 0 | 20.752 | 0 | 2 | 0 | 50.609 | 50.655 | 33.445 | 33.421 | 27.76 | 25.352 | 14.543 | 1 | 0 | 58.87 | 56.382 | 47.147 | 21.691 | 0 | 0 | 57.099 | 34.244 | [5 empty] | 0 | 17.188 | 5 | 2.3615 | 2.1695 | 1.6952 | 1.5385 | 0.63104 | 26.7221
2005-10-31 | 22:10 | 0 | 20.728 | 0 | 2 | 0 | 41.434 | 50.884 | 33.538 | 33.517 | 24.364 | 25.377 | 14.568 | 0 | 0 | 58.87 | 56.405 | 47.171 | 21.738 | 0 | 0 | 57.076 | 34.22 | [5 empty] | 0 | 7.917 | 6 | 2.3542 | 2.1626 | 1.6949 | 1.5385 | 0.62412 | 26.5108
2005-10-31 | 22:11 | 0 | 20.752 | 0 | 3 | 0 | 36.923 | 46.505 | 33.538 | 33.61 | 22.172 | 25.232 | 14.618 | 0 | 0 | 58.847 | 56.382 | 47.194 | 21.716 | 0 | 0 | 57.099 | 34.22 | [5 empty] | 0 | 3.313 | 7 | 2.3396 | 2.1487 | 1.6943 | 1.5385 | 0.61028 | 26.0842
2005-10-31 | 22:12 | 0 | 20.809 | 0 | 2 | 0 | 35.615 | 39.375 | 33.782 | 33.665 | 21 | 25.36 | 14.676 | 1 | 0 | 58.945 | 56.412 | 47.248 | 21.77 | 0 | 0 | 57.083 | 34.275 | [5 empty] | 0 | 1.95 | 8 | 2.3227 | 2.1327 | 1.6936 | 1.5385 | 0.59422 | 25.5827
2005-10-31 | 22:13 | 0 | 20.799 | 0 | 2 | 0 | 35.091 | 36.83 | 33.845 | 33.797 | 20.777 | 25.328 | 14.618 | 0 | 0 | 58.87 | 56.426 | 47.171 | 21.738 | 0 | 0 | 57.01 | 34.22 | [5 empty] | 0 | 1.294 | 9 | 2.3396 | 2.1487 | 1.6943 | 1.5385 | 0.61028 | 26.0842
2005-10-31 | 22:14 | 0 | 20.777 | 0 | 2 | 0 | 34.833 | 35.89 | 34.058 | 34.01 | 20.247 | 25.472 | 14.618 | 0 | 0 | 58.892 | 56.382 | 47.171 | 21.716 | 0 | 0 | 57.01 | 34.244 | [5 empty] | 0 | 0.823 | 10 | 2.3396 | 2.1487 | 1.6943 | 1.5385 | 0.61028 | 26.0842
2005-10-31 | 22:15 | 0 | 20.777 | 0 | 2 | 0 | 34.785 | 35.443 | 33.562 | 34.316 | 20.296 | 25.401 | 14.593 | 0 | 0 | 58.824 | 56.359 | 47.241 | 21.738 | 0 | 0 | 57.01 | 34.268 | [5 empty] | 0 | 0.469 | 11 | 2.3469 | 2.1557 | 1.6946 | 1.5385 | 0.6172 | 26.2981
2005-10-31 | 22:16 | 0 | 20.752 | 0 | 3 | 0 | 34.691 | 35.301 | 33.118 | 33.869 | 19.877 | 25.448 | 14.568 | 0 | 0 | 58.824 | 56.359 | 47.171 | 21.738 | 0 | 0 | 56.987 | 34.268 | [5 empty] | 0 | 0.822 | 12 | 2.3542 | 2.1626 | 1.6949 | 1.5385 | 0.62412 | 26.5108
2005-10-31 | 22:17 | 0 | 20.777 | 0 | 2 | 0 | 34.596 | 35.115 | 32.787 | 33.469 | 19.704 | 25.401 | 14.668 | 0 | 0 | 58.803 | 56.337 | 47.241 | 21.738 | 0 | 0 | 56.987 | 34.292 | [5 empty] | 0 | 1.127 | 13 | 2.3251 | 2.1349 | 1.6937 | 1.5385 | 0.59644 | 25.6523
2005-10-31 | 22:18 | 0 | 20.799 | 0 | 2 | 0 | 34.151 | 34.995 | 32.553 | 33.139 | 19.309 | 25.448 | 14.618 | 0 | 0 | 58.781 | 56.337 | 47.262 | 21.716 | 0 | 0 | 57.01 | 34.244 | [5 empty] | 0 | 1.012 | 14 | 2.3396 | 2.1487 | 1.6943 | 1.5385 | 0.61028 | 26.0842
2005-10-31 | 22:19 | 0 | 20.799 | 0 | 3 | 0 | 33.658 | 34.62 | 32.36 | 32.694 | 27.231 | 25.472 | 14.668 | 0 | 0 | 58.781 | 56.314 | 47.171 | 21.716 | 0 | 0 | 57.01 | 34.268 | [5 empty] | 0 | 0.964 | 15 | 2.3251 | 2.1349 | 1.6937 | 1.5385 | 0.59644 | 25.6523
2005-10-31 | 22:20 | 1 | 20.777 | 1 | 2 | 0 | 46.048 | 34.127 | 32.193 | 32.577 | 26.316 | 25.544 | 14.643 | 1 | 0 | 58.758 | 56.291 | 47.171 | 21.738 | 0 | 0 | 56.987 | 34.268 | [5 empty] | 20.777 | 13.471 | 16 | 2.3324 | 2.1418 | 1.694 | 1.5385 | 0.60336 | 25.8689
2005-10-31 | 22:21 | 0 | 20.777 | 0 | 3 | 0 | 48.226 | 43.597 | 31.975 | 32.385 | 26.485 | 25.423 | 14.691 | 1 | 0 | 58.669 | 56.248 | 47.147 | 21.738 | 0 | 0 | 56.987 | 34.268 | [5 empty] | 0 | 15.841 | 17 | 2.3184 | 2.1285 | 1.6934 | 1.5385 | 0.59007 | 25.4518
2005-10-31 | 22:22 | 0 | 20.784 | 0 | 2 | 0 | 48.669 | 47.889 | 31.838 | 32.247 | 26.539 | 25.48 | 14.749 | 1 | 0 | 58.698 | 56.3 | 47.178 | 21.748 | 0 | 0 | 57.017 | 34.299 | [5 empty] | 0 | 16.422 | 18 | 2.3015 | 2.1125 | 1.6927 | 1.5385 | 0.57402 | 24.941
2005-10-31 | 22:23 | 0 | 20.784 | 0 | 2 | 0 | 48.347 | 48.692 | 31.477 | 31.887 | 26.613 | 25.769 | 14.774 | 1 | 0 | 58.721 | 56.3 | 47.154 | 21.77 | 0 | 0 | 56.994 | 34.323 | [5 empty] | 0 | 16.46 | 19 | 2.2942 | 2.1056 | 1.6924 | 1.5385 | 0.5671 | 24.7185
2005-10-31 | 22:24 | 0 | 20.784 | 0 | 2 | 0 | 48.233 | 48.508 | 31.428 | 31.718 | 26.492 | 25.48 | 14.749 | 1 | 0 | 58.676 | 56.277 | 47.224 | 21.748 | 0 | 0 | 56.994 | 34.323 | [5 empty] | 0 | 16.515 | 20 | 2.3015 | 2.1125 | 1.6927 | 1.5385 | 0.57402 | 24.941
2005-10-31 | 22:25 | 1 | 20.777 | 0 | 3 | 0 | 48.478 | 48.478 | 31.446 | 31.446 | 26.556 | 25.472 | 14.716 | 1 | 0 | 58.6 | 56.248 | 47.194 | 21.738 | 0 | 0 | 57.01 | 34.268 | [5 empty] | 20.777 | 17.032 | 21 | 2.3111 | 2.1216 | 1.6931 | 1.5385 | 0.58315 | 25.2325
2005-10-31 | 22:26 | 0 | 20.777 | 0 | 2 | 0 | 49.096 | 48.545 | 31.639 | 31.396 | 26.772 | 25.666 | 14.716 | 2 | 0 | 58.623 | 56.225 | 47.217 | 21.716 | 0 | 0 | 56.921 | 34.22 | [5 empty] | 0 | 17.7 | 22 | 2.3111 | 2.1216 | 1.6931 | 1.5385 | 0.58315 | 25.2325
2005-10-31 | 22:27 | 0 | 20.809 | 0 | 2 | 0 | 49.493 | 49.059 | 31.573 | 31.492 | 26.865 | 25.615 | 14.754 | 1 | 0 | 58.664 | 56.286 | 47.21 | 21.777 | 0 | 0 | 56.96 | 34.306 | [5 empty] | 0 | 18.001 | 23 | 2.3 | 2.1111 | 1.6927 | 1.5385 | 0.57263 | 24.8966
2005-10-31 | 22:28 | 0 | 20.838 | 0 | 2 | 0 | 49.915 | 49.572 | 31.701 | 31.75 | 26.907 | 25.487 | 14.779 | 1 | 0 | 58.664 | 56.243 | 47.234 | 21.777 | 0 | 0 | 56.96 | 34.306 | [5 empty] | 0 | 18.165 | 24 | 2.2928 | 2.1042 | 1.6924 | 1.5385 | 0.56571 | 24.6739
2005-10-31 | 22:29 | 0 | 20.814 | 1 | 2 | 0 | 50.076 | 50.053 | 31.919 | 31.75 | 26.931 | 25.558 | 14.704 | 1 | 0 | 58.73 | 56.266 | 47.21 | 21.777 | 0 | 0 | 56.96 | 34.282 | [5 empty] | 0 | 18.326 | 25 | 2.3146 | 2.1249 | 1.6933 | 1.5385 | 0.58647 | 25.338
2005-10-31 | 22:30 | 0 | 20.806 | 0 | 2 | 0 | 50.251 | 50.298 | 32.321 | 31.911 | 27.069 | 25.526 | 14.648 | 1 | 0 | 58.657 | 56.236 | 47.271 | 21.745 | 0 | 0 | 56.907 | 34.275 | [5 empty] | 0 | 18.34 | 26 | 2.3309 | 2.1404 | 1.6939 | 1.5385 | 0.60197 | 25.8257
2005-10-31 | 22:31 | 0 | 20.863 | 0 | 2 | 0 | 44.848 | 50.443 | 32.615 | 32.375 | 25.124 | 25.534 | 14.804 | 1 | 0 | 58.753 | 56.332 | 47.257 | 21.802 | 0 | 0 | 56.937 | 34.33 | [5 empty] | 0 | 12.473 | 27 | 2.2855 | 2.0973 | 1.6921 | 1.5385 | 0.55879 | 24.4497
2005-10-31 | 22:32 | 0 | 20.838 | 0 | 2 | 0 | 37.055 | 49.801 | 32.943 | 32.567 | 22.812 | 25.583 | 14.681 | 1 | 0 | 58.687 | 56.243 | 47.234 | 21.777 | 0 | 0 | 56.893 | 34.33 | [5 empty] | 0 | 4.488 | 28 | 2.3213 | 2.1313 | 1.6935 | 1.5385 | 0.59284 | 25.5391
2005-10-31 | 22:33 | 0 | 20.814 | 0 | 2 | 0 | 34.895 | 41.286 | 32.991 | 32.778 | 21.682 | 25.607 | 14.681 | 0 | 0 | 58.708 | 56.243 | 47.187 | 21.777 | 0 | 0 | 56.871 | 34.306 | [5 empty] | 0 | 2.117 | 29 | 2.3213 | 2.1313 | 1.6935 | 1.5385 | 0.59284 | 25.5391
2005-10-31 | 22:34 | 0 | 20.806 | 0 | 2 | 0 | 34.275 | 36.603 | 33.359 | 33.007 | 20.492 | 25.551 | 14.648 | 0 | 0 | 58.657 | 56.191 | 47.203 | 21.745 | 0 | 0 | 56.841 | 34.251 | [5 empty] | 0 | 1.268 | 30 | 2.3309 | 2.1404 | 1.6939 | 1.5385 | 0.60197 | 25.8257
2005-10-31 | 22:35 | 0 | 20.838 | 0 | 2 | 0 | 34.072 | 35.294 | 33.366 | 33.318 | 20.311 | 25.558 | 14.681 | 0 | 0 | 58.687 | 56.197 | 47.301 | 21.777 | 0 | 0 | 56.825 | 34.282 | [5 empty] | 0 | 0.754 | 31 | 2.3213 | 2.1313 | 1.6935 | 1.5385 | 0.59284 | 25.5391
2005-10-31 | 22:36 | 0 | 20.814 | 0 | 2 | 0 | 34.024 | 34.754 | 33.156 | 33.366 | 20.016 | 25.512 | 14.656 | 0 | 0 | 58.708 | 56.197 | 47.325 | 21.753 | 0 | 0 | 56.871 | 34.258 | [5 empty] | 0 | 0.658 | 32 | 2.3286 | 2.1382 | 1.6938 | 1.5385 | 0.59976 | 25.7564
2005-10-31 | 22:37 | 0 | 20.782 | 0 | 2 | 0 | 33.969 | 34.51 | 32.725 | 33.335 | 19.734 | 25.455 | 14.648 | 0 | 0 | 58.635 | 56.168 | 47.227 | 21.721 | 0 | 0 | 56.864 | 34.275 | [5 empty] | 0 | 0.634 | 33 | 2.3309 | 2.1404 | 1.6939 | 1.5385 | 0.60197 | 25.8257
2005-10-31 | 22:38 | 0 | 20.814 | 0 | 2 | 0 | 34.048 | 34.4 | 32.448 | 33.108 | 19.644 | 25.438 | 14.704 | 0 | 0 | 58.664 | 56.175 | 47.21 | 21.728 | 0 | 0 | 56.893 | 34.282 | [5 empty] | 0 | 0.94 | 34 | 2.3146 | 2.1249 | 1.6933 | 1.5385 | 0.58647 | 25.338
2005-10-31 | 22:39 | 0 | 20.814 | 0 | 3 | 0 | 33.718 | 34.447 | 32.208 | 32.591 | 19.744 | 25.512 | 14.729 | 0 | 0 | 58.708 | 56.197 | 47.21 | 21.753 | 0 | 0 | 56.848 | 34.306 | [5 empty] | 0 | 1.127 | 35 | 2.3073 | 2.118 | 1.693 | 1.5385 | 0.57955 | 25.118
2005-10-31 | 22:40 | 0 | 20.733 | 0 | 2 | 0 | 33.287 | 34.182 | 32.007 | 32.367 | 19.488 | 25.382 | 14.696 | 0 | 0 | 58.589 | 56.145 | 47.18 | 21.696 | 0 | 0 | 56.841 | 34.299 | [5 empty] | 0 | 0.92 | 36 | 2.3169 | 2.1271 | 1.6933 | 1.5385 | 0.58869 | 25.4081
2005-10-31 | 22:41 | 1 | 20.789 | 1 | 2 | 0 | 43.87 | 33.79 | 31.943 | 32.328 | 25.943 | 25.414 | 14.704 | 1 | 0 | 58.596 | 56.131 | 47.21 | 21.753 | 0 | 0 | 56.871 | 34.282 | [5 empty] | 20.789 | 11.542 | 37 | 2.3146 | 2.1249 | 1.6933 | 1.5385 | 0.58647 | 25.338
2005-10-31 | 22:42 | 0 | 20.814 | 0 | 3 | 1 | 48.013 | 37.244 | 32.039 | 32.159 | 26.041 | 25.463 | 14.779 | 0 | 0 | 58.596 | 56.131 | 47.187 | 21.728 | 0 | 0 | 56.848 | 34.258 | [5 empty] | 0 | 15.854 | 38 | 2.2928 | 2.1042 | 1.6924 | 1.5385 | 0.56571 | 24.6739
2005-10-31 | 22:43 | 0 | 20.757 | 0 | 2 | 0 | 48.165 | 47.019 | 31.767 | 32.032 | 26.056 | 25.406 | 14.696 | 2 | 0 | 58.5 | 56.077 | 47.133 | 21.696 | 0 | 0 | 56.841 | 34.251 | [5 empty] | 0 | 16.133 | 0 | 2.3169 | 2.1271 | 1.6933 | 1.5385 | 0.58869 | 25.4081
2005-10-31 | 22:44 | 0 | 20.789 | 0 | 2 | 0 | 48.38 | 48.219 | 31.629 | 31.99 | 26.257 | 25.342 | 14.852 | 1 | 0 | 58.507 | 56.107 | 47.21 | 21.777 | 0 | 0 | 56.825 | 34.306 | [5 empty] | 0 | 16.39 | 1 | 2.2715 | 2.084 | 2.2959 | 2.1429 | -0.058891 | -2.5926
2005-10-31 | 22:45 | 0 | 20.789 | 0 | 2 | 0 | 48.541 | 48.333 | 31.605 | 31.774 | 26.257 | 25.487 | 14.779 | 1 | 0 | 58.507 | 56.084 | 47.14 | 21.728 | 0 | 0 | 56.802 | 34.306 | [5 empty] | 0 | 16.767 | 2 | 2.2928 | 2.1042 | 2.2968 | 2.1429 | -0.038684 | -1.6872
2005-10-31 | 22:46 | 1 | 20.814 | 0 | 2 | 0 | 48.746 | 48.678 | 31.411 | 31.534 | 26.331 | 25.389 | 14.829 | 1 | 0 | 58.484 | 56.084 | 47.278 | 21.777 | 0 | 0 | 56.759 | 34.354 | [5 empty] | 20.814 | 17.212 | 3 | 2.2782 | 2.0903 | 2.2962 | 2.1429 | -0.052524 | -2.3055
2005-10-31 | 22:47 | 0 | 20.782 | 0 | 3 | 0 | 49.197 | 48.786 | 31.404 | 31.487 | 26.551 | 25.345 | 14.882 | 1 | 0 | 58.463 | 56.133 | 47.122 | 21.733 | 0 | 0 | 56.761 | 34.309 | [5 empty] | 0 | 17.71 | 4 | 2.2628 | 2.0757 | 2.2955 | 2.1429 | -0.067195 | -2.9696
2005-10-31 | 22:48 | 0 | 20.777 | 0 | 2 | 0 | 49.652 | 49.192 | 31.399 | 31.448 | 26.824 | 25.377 | 14.842 | 1 | 0 | 58.493 | 56.07 | 47.152 | 21.716 | 0 | 0 | 56.768 | 34.388 | [5 empty] | 0 | 18.204 | 5 | 2.2744 | 2.0867 | 2.296 | 2.1429 | -0.056123 | -2.4676
2005-10-31 | 22:49 | 0 | 20.777 | 0 | 2 | 0 | 49.948 | 49.673 | 31.593 | 31.519 | 26.873 | 25.281 | 14.842 | 1 | 0 | 58.47 | 56.047 | 47.22 | 21.741 | 0 | 0 | 56.722 | 34.364 | [5 empty] | 0 | 18.429 | 6 | 2.2744 | 2.0867 | 2.296 | 2.1429 | -0.056123 | -2.4676
2005-10-31 | 22:50 | 0 | 20.801 | 0 | 2 | 0 | 50.062 | 50.018 | 31.762 | 31.664 | 26.39 | 25.377 | 14.94 | 2 | 0 | 58.47 | 56.07 | 47.243 | 21.716 | 0 | 0 | 56.745 | 34.388 | [5 empty] | 0 | 18.398 | 7 | 2.2459 | 2.0596 | 2.2949 | 2.1429 | -0.083249 | -3.7068
2005-10-31 | 22:51 | 0 | 20.745 | 1 | 2 | 0 | 39.715 | 50.378 | 31.777 | 31.632 | 23.83 | 25.369 | 14.784 | 0 | 0 | 58.486 | 56.016 | 47.259 | 21.709 | 0 | 0 | 56.715 | 34.38 | [5 empty] | 0 | 8.083 | 8 | 2.2913 | 2.1028 | 2.2967 | 2.1429 | -0.040068 | -1.7487
2005-10-31 | 22:52 | 0 | 20.801 | 0 | 2 | 0 | 35.139 | 46.006 | 32.218 | 31.808 | 22.464 | 25.45 | 14.817 | 0 | 0 | 58.562 | 56.026 | 47.175 | 21.716 | 0 | 0 | 56.791 | 34.364 | [5 empty] | 0 | 3.331 | 9 | 2.2817 | 2.0937 | 2.2963 | 2.1429 | -0.049203 | -2.1564
2005-10-31 | 22:53 | 0 | 20.77 | 0 | 2 | 0 | 33.771 | 38.093 | 32.451 | 32.019 | 21.395 | 25.249 | 14.784 | 1 | 0 | 58.509 | 55.995 | 47.145 | 21.709 | 0 | 0 | 56.738 | 34.309 | [5 empty] | 0 | 1.752 | 10 | 2.2913 | 2.1028 | 2.2967 | 2.1429 | -0.040068 | -1.7487
2005-10-31 | 22:54 | 0 | 20.745 | 0 | 2 | 0 | 33.323 | 35.132 | 32.759 | 32.331 | 21.059 | 25.394 | 14.809 | 0 | 0 | 58.486 | 56.016 | 47.189 | 21.733 | 0 | 0 | 56.738 | 34.357 | [5 empty] | 0 | 0.992 | 11 | 2.284 | 2.0959 | 2.2964 | 2.1429 | -0.046988 | -2.0573
2005-10-31 | 22:55 | 0 | 20.777 | 0 | 2 | 0 | 33.261 | 34.201 | 32.955 | 32.673 | 20.728 | 25.45 | 14.842 | 0 | 0 | 58.562 | 56.026 | 47.199 | 21.861 | 0 | 0 | 56.699 | 34.459 | [5 empty] | 0 | 0.588 | 12 | 2.2744 | 2.0867 | 2.296 | 2.1429 | -0.056123 | -2.4676
2005-10-31 | 22:56 | 0 | 20.777 | 0 | 2 | 0 | 33.306 | 33.847 | 32.531 | 32.979 | 20.37 | 25.257 | 14.864 | 0 | 0 | 58.539 | 56.026 | 47.313 | 21.741 | 0 | 0 | 56.679 | 34.388 | [5 empty] | 0 | 0.327 | 13 | 2.268 | 2.0806 | 2.2958 | 2.1429 | -0.062212 | -2.743
2005-10-31 | 22:57 | 0 | 20.72 | 0 | 2 | 0 | 33.371 | 33.651 | 32.019 | 32.807 | 20.217 | 25.249 | 14.809 | 0 | 0 | 58.463 | 55.949 | 47.145 | 21.709 | 0 | 0 | 56.67 | 34.309 | [5 empty] | 0 | 0.564 | 14 | 2.284 | 2.0959 | 2.2964 | 2.1429 | -0.046988 | -2.0573
2005-10-31 | 22:58 | 0 | 20.752 | 0 | 2 | 0 | 33.354 | 33.823 | 31.786 | 32.363 | 19.953 | 25.521 | 14.965 | 0 | 0 | 58.493 | 56.002 | 47.199 | 21.765 | 0 | 0 | 56.722 | 34.34 | [5 empty] | 0 | 1.383 | 15 | 2.284 | 2.0959 | 2.2964 | 2.1429 | -0.046988 | -2.0573
2005-10-31 | 22:59 | 0 | 20.696 | 0 | 2 | 0 | 32.948 | 33.723 | 31.441 | 31.897 | 19.92 | 25.345 | 14.832 | 0 | 0 | 58.486 | 55.925 | 47.122 | 21.709 | 0 | 0 | 56.715 | 34.309 | [5 empty] | 20.777 | 14.644 | 16 | 2.2604 | 2.0734 | 2.2955 | 2.1429 | -0.069409 | -3.0706
2005-10-31 | 23:00 | 0 | 20.72 | 0 | 3 | 0 | 32.993 | 33.464 | 31.487 | 31.61 | 27.755 | 25.345 | 14.809 | 0 | 0 | 58.463 | 55.925 | 47.075 | 21.709 | 0 | 0 | 56.715 | 34.357 | [5 empty] | 0 | 16.241 | 17 | 2.2817 | 2.0937 | 2.2963 | 2.1429 | -0.049203 | -2.1564
2005-10-31 | 23:01 | 1 | 20.777 | 0 | 2 | 0 | 46.188 | 33.12 | 31.497 | 31.544 | 26.605 | 25.281 | 14.89 | 0 | 0 | 58.45 | 55.956 | 47.105 | 21.741 | 0 | 0 | 56.699 | 34.34 | [5 empty] | 0 | 16.363 | 18 | 2.2817 | 2.0937 | 2.2963 | 2.1429 | -0.049203 | -2.1564
2005-10-31 | 23:02 | 0 | 20.752 | 1 | 2 | 0 | 47.978 | 43.53 | 31.448 | 31.737 | 26.485 | 25.186 | 14.817 | 1 | 0 | 58.404 | 55.909 | 47.129 | 21.741 | 0 | 0 | 56.699 | 34.318 | [5 empty] | 0 | 16.6 | 19 | 2.2965 | 2.1078 | 2.2969 | 2.1429 | -0.035086 | -1.5278
2005-10-31 | 23:03 | 0 | 20.777 | 0 | 3 | 0 | 47.931 | 47.609 | 31.352 | 31.568 | 26.414 | 25.232 | 14.817 | 2 | 0 | 58.404 | 55.932 | 47.105 | 21.814 | 0 | 0 | 56.679 | 34.34 | [5 empty] | 0 | 16.861 | 20 | 2.284 | 2.0959 | 2.2964 | 2.1429 | -0.046988 | -2.0573
2005-10-31 | 23:04 | 0 | 20.752 | 0 | 2 | 0 | 47.999 | 47.931 | 31.088 | 31.399 | 26.463 | 25.257 | 14.766 | 1 | 0 | 58.381 | 55.909 | 47.129 | 21.716 | 0 | 0 | 56.61 | 34.34 | [5 empty] | 0 | 17.326 | 21 | 2.289 | 2.1006 | 2.2966 | 2.1429 | -0.042283 | -1.8472
2005-10-31 | 23:05 | 0 | 20.745 | 0 | 2 | 0 | 48.083 | 48.039 | 30.911 | 31.222 | 26.287 | 25.178 | 14.809 | 1 | 0 | 58.306 | 55.834 | 47.122 | 21.709 | 0 | 0 | 56.558 | 34.309 | [5 empty] | 20.752 | 17.762 | 22 | 2.268 | 2.0806 | 2.2958 | 2.1429 | -0.062212 | -2.743
2005-10-31 | 23:06 | 0 | 20.777 | 0 | 2 | 0 | 48.436 | 48.23 | 31.014 | 31.11 | 26.534 | 25.257 | 14.792 | 1 | 0 | 58.336 | 56.026 | 47.152 | 21.836 | 0 | 0 | 56.61 | 34.34 | [5 empty] | 0 | 18.178 | 23 | 2.268 | 2.0806 | 2.2958 | 2.1429 | -0.062212 | -2.743
2005-10-31 | 23:07 | 1 | 20.752 | 0 | 2 | 0 | 48.872 | 48.368 | 31.038 | 31.11 | 26.534 | 25.33 | 14.864 | 1 | 0 | 58.381 | 55.888 | 47.129 | 21.716 | 0 | 0 | 56.565 | 34.294 | [5 empty] | 0 | 18.54 | 24 | 2.2532 | 2.0665 | 2.2952 | 2.1429 | -0.076329 | -3.3877
2005-10-31 | 23:08 | 0 | 20.777 | 0 | 2 | 0 | 49.192 | 48.849 | 31.038 | 31.014 | 26.63 | 25.306 | 14.864 | 2 | 0 | 58.336 | 55.888 | 47.152 | 21.741 | 0 | 0 | 56.565 | 34.34 | [5 empty] | 0 | 18.696 | 25 | 2.268 | 2.0806 | 2.2958 | 2.1429 | -0.062212 | -2.743
2005-10-31 | 23:09 | 0 | 20.752 | 0 | 2 | 0 | 49.628 | 49.169 | 31.183 | 31.088 | 26.75 | 25.33 | 14.915 | 1 | 0 | 58.381 | 55.888 | 47.129 | 21.716 | 0 | 0 | 56.588 | 34.34 | [5 empty] | 0 | 18.596 | 26 | 2.2555 | 2.0687 | 2.2953 | 2.1429 | -0.074115 | -3.286
2005-10-31 | 23:10 | 0 | 20.752 | 0 | 2 | 0 | 49.904 | 49.605 | 31.377 | 31.208 | 26.799 | 25.377 | 14.864 | 1 | 0 | 58.358 | 55.888 | 47.152 | 21.741 | 0 | 0 | 56.61 | 34.34 | [5 empty] | 20.674 | 18.476 | 27 | 2.2628 | 2.0757 | 2.2955 | 2.1429 | -0.067195 | -2.9696
2005-10-31 | 23:11 | 0 | 20.696 | 0 | 2 | 0 | 49.988 | 50.011 | 31.441 | 31.392 | 26.841 | 25.178 | 14.907 | 1 | 0 | 58.329 | 55.879 | 47.075 | 21.709 | 0 | 0 | 56.535 | 34.357 | [5 empty] | 0 | 13.9 | 0 | 2.2409 | 2.0549 | 2.2947 | 2.1429 | -0.087955 | -3.9249
2005-10-31 | 23:12 | 1 | 20.674 | 1 | 2 | 1 | 49.988 | 50.149 | 31.754 | 31.512 | 26.887 | 25.394 | 14.882 | 2 | 0 | 58.374 | 55.811 | 47.122 | 21.709 | 0 | 0 | 56.558 | 34.287 | [5 empty] | 0 | 5.09 | 1 | 2.2121 | 2.0275 | 2.2935 | 2.1429 | -0.11536 | -5.2149
2005-10-31 | 23:13 | 0 | 20.72 | 0 | 2 | 0 | 45.63 | 50.216 | 32.115 | 31.73 | 24.744 | 25.394 | 14.957 | 1 | 0 | 58.397 | 55.811 | 47.122 | 21.733 | 0 | 0 | 56.535 | 34.333 | [5 empty] | 0 | 2.259 | 2 | 2.2246 | 2.0394 | 2.294 | 2.1429 | -0.10346 | -4.6505
2005-10-31 | 23:14 | 0 | 20.72 | 0 | 3 | 0 | 37.06 | 49.941 | 32.211 | 31.97 | 22.841 | 25.298 | 15.056 | 0 | 0 | 58.441 | 55.902 | 47.259 | 21.758 | 0 | 0 | 56.469 | 34.333 | [5 empty] | 0 | 1.412 | 3 | 2.2342 | 2.0485 | 2.2944 | 2.1429 | -0.094321 | -4.2217
2005-10-31 | 23:15 | 0 | 20.752 | 0 | 2 | 0 | 34.622 | 41.32 | 32.412 | 32.363 | 21.716 | 25.281 | 15.013 | 0 | 0 | 58.427 | 55.841 | 47.243 | 21.765 | 0 | 0 | 56.521 | 34.34 | [5 empty] | 0 | 0.938 | 4 | 2.2386 | 2.0527 | 2.2946 | 2.1429 | -0.090169 | -4.0279
2005-10-31 | 23:16 | 0 | 20.72 | 0 | 2 | 0 | 33.816 | 36.308 | 32.735 | 32.404 | 21.034 | 25.394 | 14.98 | 0 | 0 | 58.374 | 55.834 | 47.145 | 21.733 | 0 | 0 | 56.515 | 34.333 | [5 empty] | 0 | 0.636 | 5 | 2.268 | 2.0806 | 2.2958 | 2.1429 | -0.062212 | -2.743
2005-10-31 | 23:17 | 0 | 20.728 | 0 | 2 | 0 | 33.541 | 34.811 | 32.742 | 32.603 | 20.752 | 25.257 | 14.965 | 0 | 0 | 58.404 | 55.841 | 47.152 | 21.765 | 0 | 0 | 56.588 | 34.34 | [5 empty] | 0 | 0.634 | 6 | 2.2913 | 2.1028 | 2.2967 | 2.1429 | -0.040068 | -1.7487
2005-10-31 | 23:18 | 0 | 20.728 | 0 | 2 | 0 | 33.402 | 34.247 | 32.649 | 32.766 | 20.443 | 25.355 | 14.864 | 1 | 0 | 58.404 | 55.841 | 47.152 | 21.765 | 0 | 0 | 56.565 | 34.364 | [5 empty] | 0 | 0.872 | 7 | 2.3059 | 2.1166 | 2.2973 | 2.1429 | -0.026228 | -1.1375
2005-10-31 | 23:19 | 0 | 20.745 | 0 | 2 | 0 | 33.393 | 33.933 | 32.186 | 32.759 | 20.6 | 25.298 | 14.784 | 0 | 0 | 58.374 | 55.811 | 47.098 | 21.758 | 0 | 0 | 56.535 | 34.357 | [5 empty] | 0 | 1.046 | 8 | 2.3207 | 2.1307 | 2.2979 | 2.1429 | -0.012112 | -0.52189
2005-10-31 | 23:20 | 0 | 20.696 | 0 | 3 | 0 | 33.323 | 33.792 | 31.73 | 32.451 | 20.166 | 25.274 | 14.734 | 0 | 0 | 58.352 | 55.764 | 47.145 | 21.733 | 0 | 0 | 56.469 | 34.38 | [5 empty] | 0 | 0.72 | 9 | 2.2773 | 2.0895 | 2.2961 | 2.1429 | -0.053355 | -2.3429
2005-10-31 | 23:21 | 0 | 20.696 | 0 | 2 | 0 | 33.065 | 33.723 | 31.561 | 32.019 | 19.945 | 25.225 | 14.683 | 0 | 0 | 58.352 | 55.764 | 47.236 | 21.733 | 0 | 0 | 56.423 | 34.38 | [5 empty] | 0 | 10.285 | 10 | 2.284 | 2.0959 | 2.2964 | 2.1429 | -0.046988 | -2.0573
2005-10-31 | 23:22 | 0 | 20.72 | 0 | 3 | 0 | 32.641 | 33.464 | 31.487 | 31.921 | 19.772 | 25.2 | 14.832 | 0 | 0 | 58.352 | 55.788 | 47.098 | 21.733 | 0 | 0 | 56.446 | 34.38 | [5 empty] | 0 | 15.211 | 11 | 2.2604 | 2.0734 | 2.2955 | 2.1429 | -0.069409 | -3.0706
2005-10-31 | 23:23 | 0 | 20.696 | 0 | 2 | 0 | 42.111 | 33.041 | 31.441 | 31.826 | 26.767 | 25.2 | 14.809 | 0 | 0 | 58.285 | 55.764 | 47.189 | 21.758 | 0 | 0 | 56.401 | 34.38 | [5 empty] | 0 | 16.047 | 12 | 2.2773 | 2.0895 | 2.2961 | 2.1429 | -0.053355 | -2.3429
2005-10-31 | 23:24 | 0 | 20.728 | 1 | 3 | 0 | 46.853 | 37.959 | 31.352 | 31.642 | 27.569 | 25.401 | 14.89 | 1 | 0 | 58.336 | 55.774 | 47.105 | 21.765 | 0 | 0 | 56.499 | 34.34 | [5 empty] | 0 | 16.101 | 13 | 2.2773 | 2.0895 | 2.2961 | 2.1429 | -0.053355 | -2.3429
2005-10-31 | 23:25 | 0 | 20.72 | 0 | 2 | 0 | 47.488 | 46.389 | 30.982 | 31.441 | 27.128 | 25.225 | 14.832 | 1 | 0 | 58.306 | 55.72 | 47.075 | 21.758 | 0 | 0 | 56.558 | 34.333 | [5 empty] | 20.752 | 16.206 | 14 | 2.2744 | 2.0867 | 2.296 | 2.1429 | -0.056123 | -2.4676
2005-10-31 | 23:26 | 0 | 20.745 | 0 | 3 | 0 | 47.397 | 47.488 | 30.766 | 31.296 | 27.056 | 25.225 | 14.832 | 1 | 0 | 58.24 | 55.697 | 47.213 | 21.733 | 0 | 0 | 56.492 | 34.333 | [5 empty] | 0 | 16.409 | 15 | 2.3024 | 2.1133 | 2.2972 | 2.1429 | -0.02955 | -1.2835
2005-10-31 | 23:27 | 1 | 20.752 | 0 | 2 | 0 | 47.22 | 47.588 | 30.654 | 31.014 | 26.824 | 25.33 | 14.842 | 1 | 0 | 58.29 | 55.725 | 47.082 | 21.836 | 0 | 0 | 56.542 | 34.34 | [5 empty] | 0 | 16.547 | 16 | 2.3009 | 2.1119 | 2.2971 | 2.1429 | -0.030934 | -1.3444
2005-10-31 | 23:28 | 0 | 20.708 | 0 | 3 | 0 | 47.04 | 47.453 | 30.56 | 30.631 | 26.779 | 25.333 | 14.746 | 2 | 0 | 58.249 | 55.683 | 47.063 | 21.721 | 0 | 0 | 56.478 | 34.273 | [5 empty] | 0 | 16.688 | 17 | 2.2936 | 2.105 | 2.2968 | 2.1429 | -0.037854 | -1.6504
2005-10-31 | 23:29 | 0 | 20.738 | 0 | 2 | 0 | 47.112 | 47.343 | 30.519 | 30.565 | 26.689 | 25.242 | 14.751 | 1 | 0 | 58.231 | 55.734 | 47.182 | 21.775 | 0 | 0 | 56.505 | 34.325 | [5 empty] | 0 | 16.57 | 18 | 2.2665 | 2.0793 | 2.2957 | 2.1429 | -0.063596 | -2.8059
2005-10-31 | 23:30 | 0 | 20.713 | 0 | 3 | 0 | 47.229 | 47.32 | 30.59 | 30.541 | 26.615 | 25.242 | 14.776 | 1 | 0 | 58.231 | 55.802 | 47.159 | 21.821 | 0 | 0 | 56.483 | 34.397 | [5 empty] | 0 | 16.287 | 19 | 2.2665 | 2.0793 | 2.2957 | 2.1429 | -0.063596 | -2.8059
2005-10-31 | 23:31 | 0 | 20.662 | 0 | 2 | 0 | 47.201 | 47.497 | 30.73 | 30.631 | 26.515 | 25.262 | 14.869 | 1 | 0 | 58.226 | 55.659 | 47.063 | 21.696 | 0 | 0 | 56.455 | 34.392 | [5 empty] | 20.662 | 16.166 | 20 | 2.259 | 2.0721 | 2.2954 | 2.1429 | -0.070793 | -3.1339
2005-10-31 | 23:32 | 0 | 20.662 | 0 | 2 | 0 | 47.063 | 47.497 | 30.801 | 30.776 | 26.635 | 25.333 | 14.869 | 1 | 0 | 58.183 | 55.659 | 47.084 | 21.721 | 0 | 0 | 56.455 | 34.438 | [5 empty] | 0 | 16.089 | 21 | 2.2304 | 2.0449 | 2.2942 | 2.1429 | -0.09792 | -4.3901
2005-10-31 | 23:33 | 1 | 20.662 | 1 | 3 | 0 | 47.04 | 47.43 | 30.994 | 30.874 | 26.779 | 25.262 | 14.895 | 2 | 0 | 58.226 | 55.659 | 47.178 | 21.721 | 0 | 0 | 56.432 | 34.414 | [5 empty] | 0 | 16.264 | 22 | 2.2377 | 2.0519 | 2.2945 | 2.1429 | -0.091 | -4.0666
2005-10-31 | 23:34 | 0 | 20.662 | 0 | 2 | 0 | 47.154 | 47.383 | 31.284 | 31.065 | 26.9 | 25.406 | 14.993 | 1 | 0 | 58.249 | 55.659 | 47.084 | 21.721 | 0 | 0 | 56.478 | 34.438 | [5 empty] | 0 | 15.996 | 23 | 2.2738 | 2.0862 | 2.296 | 2.1429 | -0.056676 | -2.4926
2005-10-31 | 23:35 | 0 | 20.662 | 0 | 2 | 0 | 47.474 | 47.453 | 31.428 | 31.21 | 27.164 | 25.357 | 14.968 | 1 | 0 | 58.226 | 55.683 | 47.222 | 21.745 | 0 | 0 | 56.432 | 34.438 | [5 empty] | 0 | 16.175 | 24 | 2.2802 | 2.0923 | 2.2963 | 2.1429 | -0.050587 | -2.2185
2005-10-31 | 23:36 | 0 | 20.662 | 0 | 3 | 0 | 47.591 | 47.773 | 31.524 | 31.595 | 27.38 | 25.382 | 14.844 | 1 | 0 | 58.226 | 55.638 | 47.154 | 21.745 | 0 | 0 | 56.432 | 34.462 | [5 empty] | 20.662 | 16.025 | 25 | 2.2951 | 2.1064 | 2.2969 | 2.1429 | -0.03647 | -1.589
2005-10-31 | 23:37 | 0 | 20.662 | 0 | 2 | 0 | 47.819 | 47.887 | 31.764 | 31.644 | 27.623 | 25.453 | 14.822 | 1 | 0 | 58.249 | 55.659 | 47.201 | 21.721 | 0 | 0 | 56.455 | 34.438 | [5 empty] | 0 | 16.02 | 26 | 2.3024 | 2.1133 | 2.2972 | 2.1429 | -0.02955 | -1.2835
2005-10-31 | 23:38 | 1 | 20.662 | 0 | 2 | 0 | 47.934 | 48.048 | 31.958 | 31.909 | 27.598 | 25.526 | 14.771 | 2 | 0 | 58.226 | 55.638 | 47.201 | 21.866 | 0 | 0 | 56.501 | 34.51 | [5 empty] | 0 | 16.193 | 27 | 2.3236 | 2.1335 | 2.298 | 2.1429 | -0.0093435 | -0.40211
2005-10-31 | 23:39 | 0 | 20.662 | 0 | 3 | 0 | 48.025 | 48.254 | 32.103 | 32.005 | 27.814 | 25.477 | 14.746 | 1 | 0 | 58.315 | 55.659 | 47.131 | 21.721 | 0 | 0 | 56.478 | 34.414 | [5 empty] | 0 | 15.998 | 0 | 2.3309 | 2.1404 | 2.2983 | 2.1429 | -0.0024235 | -0.10397
2005-10-31 | 23:40 | 0 | 20.662 | 0 | 2 | 1 | 48.391 | 48.347 | 32.269 | 32.198 | 27.959 | 25.526 | 14.673 | 1 | 0 | 58.249 | 55.638 | 47.084 | 21.721 | 0 | 0 | 56.455 | 34.438 | [5 empty] | 0 | 16.27 | 1 | 2.3329 | 2.1424 | 3.1555 | 3 | -0.85763 | -36.7617
2005-10-31 | 23:41 | 0 | 20.637 | 0 | 3 | 0 | 48.461 | 48.643 | 32.414 | 32.463 | 28.103 | 25.502 | 14.648 | 1 | 0 | 58.249 | 55.638 | 47.154 | 21.721 | 0 | 0 | 56.455 | 34.438 | [5 empty] | 0 | 16.218 | 2 | 2.3455 | 2.1543 | 3.156 | 3 | -0.84573 | -36.058
2005-10-31 | 23:42 | 0 | 20.63 | 1 | 2 | 0 | 48.821 | 48.73 | 32.622 | 32.551 | 28.432 | 25.519 | 14.641 | 1 | 0 | 58.196 | 55.585 | 47.147 | 21.689 | 0 | 0 | 56.426 | 34.431 | [5 empty] | 20.63 | 16.029 | 3 | 2.3551 | 2.1634 | 3.1564 | 3 | -0.83659 | -35.523
2005-10-31 | 23:43 | 0 | 20.637 | 0 | 2 | 0 | 48.965 | 48.942 | 32.84 | 32.747 | 28.464 | 25.647 | 14.598 | 2 | 0 | 58.249 | 55.615 | 47.201 | 21.745 | 0 | 0 | 56.412 | 34.486 | [5 empty] | 0 | 16.097 | 4 | 2.36 | 2.1681 | 3.1566 | 3 | -0.83189 | -35.2491
2005-10-31 | 23:44 | 1 | 20.63 | 0 | 3 | 0 | 49.003 | 49.278 | 32.809 | 32.974 | 28.481 | 25.495 | 14.565 | 1 | 0 | 58.219 | 55.585 | 47.238 | 21.714 | 0 | 0 | 56.426 | 34.455 | [5 empty] | 0 | 16.163 | 5 | 2.3667 | 2.1745 | 3.1569 | 3 | -0.82552 | -34.8803
2005-10-31 | 23:45 | 0 | 20.662 | 0 | 2 | 0 | 49.15 | 49.309 | 33.029 | 33.053 | 28.609 | 25.647 | 14.548 | 1 | 0 | 58.272 | 55.638 | 47.201 | 21.745 | 0 | 0 | 56.455 | 34.486 | [5 empty] | 0 | 16.297 | 6 | 2.3813 | 2.1883 | 3.1575 | 3 | -0.81168 | -34.0859
2005-10-31 | 23:46 | 0 | 20.684 | 0 | 3 | 0 | 49.309 | 49.493 | 33.098 | 33.146 | 28.633 | 25.671 | 14.525 | 1 | 0 | 58.295 | 55.615 | 47.154 | 21.77 | 0 | 0 | 56.501 | 34.486 | [5 empty] | 0 | 16.296 | 7 | 2.39 | 2.1966 | 3.1578 | 3 | -0.80338 | -33.6138
2005-10-31 | 23:47 | 0 | 20.637 | 0 | 2 | 0 | 49.584 | 49.584 | 33.17 | 33.287 | 28.658 | 25.791 | 14.475 | 2 | 0 | 58.274 | 55.615 | 47.178 | 21.745 | 0 | 0 | 56.48 | 34.462 | [5 empty] | 20.627 | 16.57 | 8 | 2.4063 | 2.2121 | 3.1585 | 3 | -0.78788 | -32.7419
2005-10-31 | 23:48 | 0 | 20.632 | 0 | 2 | 0 | 49.696 | 49.925 | 33.259 | 33.4 | 28.773 | 25.715 | 14.445 | 1 | 0 | 58.269 | 55.589 | 47.173 | 21.741 | 0 | 0 | 56.453 | 34.481 | [5 empty] | 0 | 10.575 | 9 | 2.4049 | 2.2107 | 3.1585 | 3 | -0.78926 | -32.8192
2005-10-31 | 23:49 | 1 | 20.627 | 0 | 3 | 0 | 50.058 | 49.988 | 33.443 | 33.488 | 28.842 | 25.661 | 14.389 | 1 | 0 | 58.242 | 55.561 | 47.168 | 21.736 | 0 | 0 | 56.403 | 34.476 | [5 empty] | 0 | 3.926 | 10 | 2.4049 | 2.2107 | 3.1585 | 3 | -0.78926 | -32.8192
2005-10-31 | 23:50 | 0 | 20.679 | 0 | 2 | 0 | 44.209 | 50.361 | 33.448 | 33.634 | 26.365 | 25.882 | 14.394 | 1 | 0 | 58.313 | 55.566 | 47.22 | 21.741 | 0 | 0 | 56.453 | 34.457 | [5 empty] | 0 | 2.046 | 11 | 2.399 | 2.2052 | 3.1582 | 3 | -0.7948 | -33.1297
2005-10-31 | 23:51 | 0 | 20.679 | 0 | 2 | 0 | 37.701 | 48.046 | 33.589 | 33.775 | 24.364 | 25.737 | 14.394 | 0 | 0 | 58.269 | 55.543 | 47.243 | 21.765 | 0 | 0 | 56.407 | 34.457 | [5 empty] | 0 | 1.318 | 12 | 2.4136 | 2.219 | 3.1588 | 3 | -0.78096 | -32.3564
2005-10-31 | 23:52 | 0 | 20.649 | 1 | 3 | 0 | 35.84 | 39.786 | 33.653 | 33.794 | 23.349 | 25.686 | 14.414 | 1 | 0 | 58.219 | 55.561 | 47.192 | 21.736 | 0 | 0 | 56.403 | 34.428 | [5 empty] | 0 | 0.823 | 13 | 2.4136 | 2.219 | 3.1588 | 3 | -0.78096 | -32.3564
2005-10-31 | 23:53 | 0 | 20.674 | 0 | 2 | 0 | 35.182 | 36.942 | 33.818 | 33.864 | 22.53 | 25.732 | 14.364 | 0 | 0 | 58.285 | 55.561 | 47.168 | 21.736 | 0 | 0 | 56.426 | 34.404 | [5 empty] | 0 | 0.636 | 14 | 2.3842 | 2.1911 | 3.1576 | 3 | -0.80891 | -33.9281
2005-10-31 | 23:54 | 0 | 20.627 | 0 | 3 | 0 | 34.876 | 35.933 | 33.912 | 34.053 | 21.927 | 25.686 | 14.364 | 0 | 0 | 58.219 | 55.538 | 47.215 | 21.736 | 0 | 0 | 56.314 | 34.428 | [5 empty] | 0 | 0.469 | 15 | 2.3769 | 2.1842 | 3.1573 | 3 | -0.81583 | -34.3232
2005-10-31 | 23:55 | 0 | 20.649 | 0 | 2 | 0 | 34.782 | 35.51 | 33.818 | 34.146 | 21.638 | 25.612 | 14.465 | 0 | 0 | 58.242 | 55.538 | 47.192 | 21.758 | 0 | 0 | 56.38 | 34.428 | [5 empty] | 0 | 0.846 | 16 | 2.3915 | 2.198 | 3.1579 | 3 | -0.80199 | -33.5355
2005-10-31 | 23:56 | 0 | 20.649 | 0 | 3 | 0 | 34.711 | 35.275 | 33.395 | 34.242 | 21.228 | 25.612 | 14.49 | 0 | 0 | 58.219 | 55.538 | 47.259 | 21.758 | 0 | 0 | 56.291 | 34.452 | [5 empty] | 0 | 10.74 | 17 | 2.3542 | 2.1626 | 3.1571 | 3 | -0.83742 | -35.5714
2005-10-31 | 23:57 | 0 | 20.649 | 0 | 2 | 0 | 34.593 | 35.11 | 33.184 | 33.747 | 21.302 | 25.732 | 14.44 | 0 | 0 | 58.219 | 55.515 | 47.145 | 21.782 | 0 | 0 | 56.291 | 34.428 | [5 empty] | 2360.9591 | 8.7029 | 18 | 2.2346 | 2.0489 | 3.1564 | 3 | -0.95108 | -42.5613
2005-10-31 | 23:58 | 0 | 20.649 | 0 | 3 | 0 | 34.287 | 35.017 | 32.972 | 33.371 | 21.277 | 25.612 | 14.512 | 0 | 0 | 58.174 | 55.491 | 47.145 | 21.736 | 0 | 0 | 56.291 | 34.5 | [5 empty] | 0 | 0 | 19 | 6.5964 | 6.195 | 3.1516 | 3 | 3.195 | 48.4355
2005-10-31 | 23:59 | 0 | 20.657 | 0 | 3 | 0 | 33.893 | 34.715 | 32.694 | 33.354 | 21.331 | 25.617 | 14.52 | 0 | 0 | 58.158 | 55.519 | 47.243 | 21.787 | 0 | 0 | 56.364 | 34.457
2005-11-01 | 0:00 | 0 | 20.657 | 0 | 2 | 0 | 43.834 | 34.316 | 32.483 | 33.094 | 28.533 | 25.521 | 14.568 | 0 | 0 | 58.158 | 55.519 | 47.287 | 21.765 | 0 | 0 | 56.364 | 34.457 | [5 empty] | #REF! | #VALUE! | 0 | #VALUE! | #VALUE! | 3.3283 | 3 | #VALUE! | #VALUE!
2005-10-31 | 1441 | 111 | 21.2699 | 1.29 | 2885 | 31 | 38.9561 |  |  | 30.2533 | 21.9375 | 25.0524 | 14.9786 | 687 | 2 |  |  |  | 22.1153 | 7 | 0 |  |  | 13.125 | 19:30 | 16.245 | 11:53 | 3.12 | #REF!
|  | 1 | [18 empty] | 0 | [10 empty] | #VALUE! | #VALUE! |  | 32 | #VALUE! | #VALUE!